## 0030Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 00:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2162
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 | 1240 | 1240 | -5 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1162 | 1240 | 1240 | -78 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1408 | 1517 | 1517 | -109 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1141 | 1240 | 1240 | -99 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1138 | 1240 | 1240 | -102 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1384 | 1517 | 1517 | -133 | 91 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1373 | 1517 | 1517 | -144 | 91 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1351 | 1517 | 1517 | -166 | 89 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1348 | 1517 | 1517 | -169 | 89 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1346 | 1517 | 1517 | -171 | 89 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1344 | 1517 | 1517 | -173 | 89 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1084 | 1240 | 1240 | -156 | 87 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 | 1517 | 1517 | -207 | 86 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 | 1517 | 1517 | -207 | 86 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1061 | 1240 | 1240 | -179 | 86 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1282 | 1517 | 1517 | -235 | 85 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1475 | 1760 | 1760 | -285 | 84 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 | 1517 | 1517 | -254 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1256 | 1517 | 1517 | -261 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1255 | 1517 | 1517 | -262 | 83 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1249 | 1517 | 1517 | -268 | 82 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1245 | 1517 | 1517 | -272 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1014 | 1240 | 1240 | -226 | 82 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1429 | 1760 | 1760 | -331 | 81 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1229 | 1517 | 1517 | -288 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1227 | 1517 | 1517 | -290 | 81 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1226 | 1517 | 1517 | -291 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1222 | 1517 | 1517 | -295 | 81 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1218 | 1517 | 1517 | -299 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1217 | 1517 | 1517 | -300 | 80 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1217 | 1517 | 1517 | -300 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1216 | 1517 | 1517 | -301 | 80 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1214 | 1517 | 1517 | -303 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 992 | 1240 | 1240 | -248 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1211 | 1517 | 1517 | -306 | 80 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 | 1517 | 1517 | -308 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 | 1517 | 1517 | -308 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1207 | 1517 | 1517 | -310 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -986 | 1240 | 1240 | -254 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1204 | 1517 | 1517 | -313 | 79 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1201 | 1517 | 1517 | -316 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1200 | 1517 | 1517 | -317 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 | 1240 | 1240 | -263 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 976 | 1240 | 1240 | -264 | 79 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1193 | 1517 | 1517 | -324 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 | 1240 | 1240 | -270 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 966 | 1240 | 1240 | -274 | 78 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -957 | 1240 | 1240 | -283 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 956 | 1240 | 1240 | -284 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 953 | 1240 | 1240 | -287 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 952 | 1240 | 1240 | -288 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 951 | 1240 | 1240 | -289 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 951 | 1240 | 1240 | -289 | 77 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 950 | 1240 | 1240 | -290 | 77 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 949 | 1240 | 1240 | -291 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 | 1240 | 1240 | -296 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 | 1240 | 1240 | -296 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 | 1240 | 1240 | -296 | 76 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 941 | 1240 | 1240 | -299 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 936 | 1240 | 1240 | -304 | 76 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1144 | 1517 | 1517 | -373 | 75 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1141 | 1517 | 1517 | -376 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 932 | 1240 | 1240 | -308 | 75 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 926 | 1240 | 1240 | -314 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 926 | 1240 | 1240 | -314 | 75 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 922 | 1240 | 1240 | -318 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 920 | 1240 | 1240 | -320 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1122 | 1517 | 1517 | -395 | 74 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 | 1517 | 1517 | -403 | 73 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1111 | 1517 | 1517 | -406 | 73 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 903 | 1240 | 1240 | -337 | 73 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1102 | 1517 | 1517 | -415 | 73 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 890 | 1240 | 1240 | -350 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -889 | 1240 | 1240 | -351 | 72 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS15_1:line | 1134 | 1600 | 1600 | -466 | 71 | []

## 0030Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 00:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2162
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 |  | 1240 | -5 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1162 |  | 1240 | -78 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1408 |  | 1517 | -109 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1141 |  | 1240 | -99 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1138 |  | 1240 | -102 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1384 |  | 1517 | -133 | 91 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1373 |  | 1517 | -144 | 91 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1351 |  | 1517 | -166 | 89 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1348 |  | 1517 | -169 | 89 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1346 |  | 1517 | -171 | 89 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1344 |  | 1517 | -173 | 89 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1084 |  | 1240 | -156 | 87 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 |  | 1517 | -207 | 86 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 |  | 1517 | -207 | 86 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1061 |  | 1240 | -179 | 86 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1282 |  | 1517 | -235 | 85 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1475 |  | 1760 | -285 | 84 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 |  | 1517 | -254 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1256 |  | 1517 | -261 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1255 |  | 1517 | -262 | 83 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1249 |  | 1517 | -268 | 82 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1245 |  | 1517 | -272 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1014 |  | 1240 | -226 | 82 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1429 |  | 1760 | -331 | 81 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1229 |  | 1517 | -288 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1227 |  | 1517 | -290 | 81 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1226 |  | 1517 | -291 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1222 |  | 1517 | -295 | 81 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1218 |  | 1517 | -299 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1217 |  | 1517 | -300 | 80 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1217 |  | 1517 | -300 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1216 |  | 1517 | -301 | 80 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1214 |  | 1517 | -303 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 992 |  | 1240 | -248 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1211 |  | 1517 | -306 | 80 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 |  | 1517 | -308 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 |  | 1517 | -308 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1207 |  | 1517 | -310 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -986 |  | 1240 | -254 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1204 |  | 1517 | -313 | 79 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1201 |  | 1517 | -316 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1200 |  | 1517 | -317 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 |  | 1240 | -263 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 976 |  | 1240 | -264 | 79 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1193 |  | 1517 | -324 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 |  | 1240 | -270 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 966 |  | 1240 | -274 | 78 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -957 |  | 1240 | -283 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 956 |  | 1240 | -284 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 953 |  | 1240 | -287 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 952 |  | 1240 | -288 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 951 |  | 1240 | -289 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 951 |  | 1240 | -289 | 77 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 950 |  | 1240 | -290 | 77 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 949 |  | 1240 | -291 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 |  | 1240 | -296 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 |  | 1240 | -296 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 |  | 1240 | -296 | 76 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 941 |  | 1240 | -299 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 936 |  | 1240 | -304 | 76 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1144 |  | 1517 | -373 | 75 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1141 |  | 1517 | -376 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 932 |  | 1240 | -308 | 75 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 926 |  | 1240 | -314 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 926 |  | 1240 | -314 | 75 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 922 |  | 1240 | -318 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 920 |  | 1240 | -320 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1122 |  | 1517 | -395 | 74 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 |  | 1517 | -403 | 73 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1111 |  | 1517 | -406 | 73 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 903 |  | 1240 | -337 | 73 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1102 |  | 1517 | -415 | 73 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 890 |  | 1240 | -350 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -889 |  | 1240 | -351 | 72 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS15_1:line | 1134 |  | 1600 | -466 | 71 | []

## 0130Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 01:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2115
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 | 1240 | 1240 | -2 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1445 | 1517 | 1517 | -72 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1424 | 1517 | 1517 | -93 | 94 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1419 | 1517 | 1517 | -98 | 94 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1407 | 1517 | 1517 | -110 | 93 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1405 | 1517 | 1517 | -112 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1142 | 1240 | 1240 | -98 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1136 | 1240 | 1240 | -104 | 92 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1385 | 1517 | 1517 | -132 | 91 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1384 | 1517 | 1517 | -133 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1124 | 1240 | 1240 | -116 | 91 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1359 | 1517 | 1517 | -158 | 90 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1359 | 1517 | 1517 | -158 | 90 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1334 | 1517 | 1517 | -183 | 88 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1315 | 1517 | 1517 | -202 | 87 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1302 | 1517 | 1517 | -215 | 86 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1301 | 1517 | 1517 | -216 | 86 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1301 | 1517 | 1517 | -216 | 86 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1056 | 1240 | 1240 | -184 | 85 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1289 | 1517 | 1517 | -228 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1052 | 1240 | 1240 | -188 | 85 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1278 | 1517 | 1517 | -239 | 84 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1276 | 1517 | 1517 | -241 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1273 | 1517 | 1517 | -244 | 84 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1268 | 1517 | 1517 | -249 | 84 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1268 | 1517 | 1517 | -249 | 84 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1266 | 1517 | 1517 | -251 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 | 1517 | 1517 | -253 | 83 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 | 1517 | 1517 | -254 | 83 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 | 1517 | 1517 | -254 | 83 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1260 | 1517 | 1517 | -257 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1259 | 1517 | 1517 | -258 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1254 | 1517 | 1517 | -263 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1253 | 1517 | 1517 | -264 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 | 1517 | 1517 | -265 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1250 | 1517 | 1517 | -267 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1247 | 1517 | 1517 | -270 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1242 | 1517 | 1517 | -275 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1004 | 1240 | 1240 | -236 | 81 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1424 | 1760 | 1760 | -336 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -991 | 1240 | 1240 | -249 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 988 | 1240 | 1240 | -252 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1204 | 1517 | 1517 | -313 | 79 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1384 | 1760 | 1760 | -376 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 971 | 1240 | 1240 | -269 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1188 | 1517 | 1517 | -329 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 965 | 1240 | 1240 | -275 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 964 | 1240 | 1240 | -276 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 957 | 1240 | 1240 | -283 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1168 | 1517 | 1517 | -349 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -953 | 1240 | 1240 | -287 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 | 1517 | 1517 | -352 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1164 | 1517 | 1517 | -353 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 949 | 1240 | 1240 | -291 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -949 | 1240 | 1240 | -291 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1159 | 1517 | 1517 | -358 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 946 | 1240 | 1240 | -294 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 | 1240 | 1240 | -296 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 | 1240 | 1240 | -296 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 | 1240 | 1240 | -298 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 | 1240 | 1240 | -298 | 76 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 939 | 1240 | 1240 | -301 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 938 | 1240 | 1240 | -302 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 936 | 1240 | 1240 | -304 | 76 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 934 | 1240 | 1240 | -306 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -934 | 1240 | 1240 | -306 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 927 | 1240 | 1240 | -313 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -918 | 1240 | 1240 | -322 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 918 | 1240 | 1240 | -322 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -911 | 1240 | 1240 | -329 | 73 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -899 | 1240 | 1240 | -341 | 73 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 894 | 1240 | 1240 | -346 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -877 | 1240 | 1240 | -363 | 71 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -871 | 1240 | 1240 | -369 | 70 | []

## 0130Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 01:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2115
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 |  | 1240 | -2 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1445 |  | 1517 | -72 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1424 |  | 1517 | -93 | 94 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1419 |  | 1517 | -98 | 94 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1407 |  | 1517 | -110 | 93 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1405 |  | 1517 | -112 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1142 |  | 1240 | -98 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1136 |  | 1240 | -104 | 92 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1385 |  | 1517 | -132 | 91 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1384 |  | 1517 | -133 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1124 |  | 1240 | -116 | 91 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1359 |  | 1517 | -158 | 90 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1359 |  | 1517 | -158 | 90 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1334 |  | 1517 | -183 | 88 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1315 |  | 1517 | -202 | 87 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1302 |  | 1517 | -215 | 86 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1301 |  | 1517 | -216 | 86 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1301 |  | 1517 | -216 | 86 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1056 |  | 1240 | -184 | 85 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1289 |  | 1517 | -228 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1052 |  | 1240 | -188 | 85 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1278 |  | 1517 | -239 | 84 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1276 |  | 1517 | -241 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1273 |  | 1517 | -244 | 84 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1268 |  | 1517 | -249 | 84 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1268 |  | 1517 | -249 | 84 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1266 |  | 1517 | -251 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 |  | 1517 | -253 | 83 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 |  | 1517 | -254 | 83 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 |  | 1517 | -254 | 83 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1260 |  | 1517 | -257 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1259 |  | 1517 | -258 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1254 |  | 1517 | -263 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1253 |  | 1517 | -264 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 |  | 1517 | -265 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1250 |  | 1517 | -267 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1247 |  | 1517 | -270 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1242 |  | 1517 | -275 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1004 |  | 1240 | -236 | 81 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1424 |  | 1760 | -336 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -991 |  | 1240 | -249 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 988 |  | 1240 | -252 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1204 |  | 1517 | -313 | 79 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1384 |  | 1760 | -376 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 971 |  | 1240 | -269 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1188 |  | 1517 | -329 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 965 |  | 1240 | -275 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 964 |  | 1240 | -276 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 957 |  | 1240 | -283 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1168 |  | 1517 | -349 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -953 |  | 1240 | -287 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 |  | 1517 | -352 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1164 |  | 1517 | -353 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 949 |  | 1240 | -291 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -949 |  | 1240 | -291 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1159 |  | 1517 | -358 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 946 |  | 1240 | -294 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 |  | 1240 | -296 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 |  | 1240 | -296 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 |  | 1240 | -298 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 |  | 1240 | -298 | 76 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 939 |  | 1240 | -301 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 938 |  | 1240 | -302 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 936 |  | 1240 | -304 | 76 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 934 |  | 1240 | -306 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -934 |  | 1240 | -306 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 927 |  | 1240 | -313 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -918 |  | 1240 | -322 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 918 |  | 1240 | -322 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -911 |  | 1240 | -329 | 73 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -899 |  | 1240 | -341 | 73 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 894 |  | 1240 | -346 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -877 |  | 1240 | -363 | 71 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -871 |  | 1240 | -369 | 70 | []

## 0230Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 02:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2112
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1239 | 1240 | 1240 | -1 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1441 | 1517 | 1517 | -76 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1421 | 1517 | 1517 | -96 | 94 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1415 | 1517 | 1517 | -102 | 93 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1400 | 1517 | 1517 | -117 | 92 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1398 | 1517 | 1517 | -119 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1137 | 1240 | 1240 | -103 | 92 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1136 | 1240 | 1240 | -104 | 92 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1388 | 1517 | 1517 | -129 | 91 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1383 | 1517 | 1517 | -134 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1120 | 1240 | 1240 | -120 | 90 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1360 | 1517 | 1517 | -157 | 90 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1359 | 1517 | 1517 | -158 | 90 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1330 | 1517 | 1517 | -187 | 88 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1313 | 1517 | 1517 | -204 | 87 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1305 | 1517 | 1517 | -212 | 86 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1301 | 1517 | 1517 | -216 | 86 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1300 | 1517 | 1517 | -217 | 86 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1057 | 1240 | 1240 | -183 | 85 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1290 | 1517 | 1517 | -227 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1052 | 1240 | 1240 | -188 | 85 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1278 | 1517 | 1517 | -239 | 84 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1276 | 1517 | 1517 | -241 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1273 | 1517 | 1517 | -244 | 84 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1269 | 1517 | 1517 | -248 | 84 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1269 | 1517 | 1517 | -248 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1267 | 1517 | 1517 | -250 | 84 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1266 | 1517 | 1517 | -251 | 83 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1265 | 1517 | 1517 | -252 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 | 1517 | 1517 | -253 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 | 1517 | 1517 | -254 | 83 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 | 1517 | 1517 | -256 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1254 | 1517 | 1517 | -263 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1253 | 1517 | 1517 | -264 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1253 | 1517 | 1517 | -264 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 | 1517 | 1517 | -265 | 83 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1247 | 1517 | 1517 | -270 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1242 | 1517 | 1517 | -275 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1003 | 1240 | 1240 | -237 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1223 | 1517 | 1517 | -294 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -992 | 1240 | 1240 | -248 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 988 | 1240 | 1240 | -252 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1196 | 1517 | 1517 | -321 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1188 | 1517 | 1517 | -329 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 | 1240 | 1240 | -270 | 78 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1374 | 1760 | 1760 | -386 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 964 | 1240 | 1240 | -276 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 959 | 1240 | 1240 | -281 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 954 | 1240 | 1240 | -286 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 | 1517 | 1517 | -352 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 | 1517 | 1517 | -352 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | -1164 | 1517 | 1517 | -353 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -951 | 1240 | 1240 | -289 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 949 | 1240 | 1240 | -291 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 945 | 1240 | 1240 | -295 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 | 1240 | 1240 | -296 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 | 1240 | 1240 | -296 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 | 1240 | 1240 | -296 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 | 1240 | 1240 | -298 | 76 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1336 | 1760 | 1760 | -424 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 941 | 1240 | 1240 | -299 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 938 | 1240 | 1240 | -302 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 937 | 1240 | 1240 | -303 | 76 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 937 | 1240 | 1240 | -303 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -935 | 1240 | 1240 | -305 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 935 | 1240 | 1240 | -305 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 927 | 1240 | 1240 | -313 | 75 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 920 | 1240 | 1240 | -320 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -919 | 1240 | 1240 | -321 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 912 | 1240 | 1240 | -328 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 898 | 1240 | 1240 | -342 | 72 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -894 | 1240 | 1240 | -346 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -874 | 1240 | 1240 | -366 | 70 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -870 | 1240 | 1240 | -370 | 70 | []

## 0230Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 02:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2112
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1239 |  | 1240 | -1 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1441 |  | 1517 | -76 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1421 |  | 1517 | -96 | 94 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1415 |  | 1517 | -102 | 93 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1400 |  | 1517 | -117 | 92 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1398 |  | 1517 | -119 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1137 |  | 1240 | -103 | 92 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1136 |  | 1240 | -104 | 92 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1388 |  | 1517 | -129 | 91 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1383 |  | 1517 | -134 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1120 |  | 1240 | -120 | 90 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1360 |  | 1517 | -157 | 90 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1359 |  | 1517 | -158 | 90 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1330 |  | 1517 | -187 | 88 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1313 |  | 1517 | -204 | 87 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1305 |  | 1517 | -212 | 86 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1301 |  | 1517 | -216 | 86 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1300 |  | 1517 | -217 | 86 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1057 |  | 1240 | -183 | 85 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1290 |  | 1517 | -227 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1052 |  | 1240 | -188 | 85 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1278 |  | 1517 | -239 | 84 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1276 |  | 1517 | -241 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1273 |  | 1517 | -244 | 84 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1269 |  | 1517 | -248 | 84 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1269 |  | 1517 | -248 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1267 |  | 1517 | -250 | 84 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1266 |  | 1517 | -251 | 83 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1265 |  | 1517 | -252 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 |  | 1517 | -253 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 |  | 1517 | -254 | 83 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 |  | 1517 | -256 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1254 |  | 1517 | -263 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1253 |  | 1517 | -264 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1253 |  | 1517 | -264 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 |  | 1517 | -265 | 83 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1247 |  | 1517 | -270 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1242 |  | 1517 | -275 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1003 |  | 1240 | -237 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1223 |  | 1517 | -294 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -992 |  | 1240 | -248 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 988 |  | 1240 | -252 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1196 |  | 1517 | -321 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1188 |  | 1517 | -329 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 |  | 1240 | -270 | 78 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1374 |  | 1760 | -386 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 964 |  | 1240 | -276 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 959 |  | 1240 | -281 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 954 |  | 1240 | -286 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 |  | 1517 | -352 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 |  | 1517 | -352 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | -1164 |  | 1517 | -353 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -951 |  | 1240 | -289 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 949 |  | 1240 | -291 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 945 |  | 1240 | -295 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 |  | 1240 | -296 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 |  | 1240 | -296 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 944 |  | 1240 | -296 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 |  | 1240 | -298 | 76 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1336 |  | 1760 | -424 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 941 |  | 1240 | -299 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 938 |  | 1240 | -302 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 937 |  | 1240 | -303 | 76 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 937 |  | 1240 | -303 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -935 |  | 1240 | -305 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 935 |  | 1240 | -305 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 927 |  | 1240 | -313 | 75 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 920 |  | 1240 | -320 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -919 |  | 1240 | -321 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 912 |  | 1240 | -328 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 898 |  | 1240 | -342 | 72 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -894 |  | 1240 | -346 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -874 |  | 1240 | -366 | 70 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -870 |  | 1240 | -370 | 70 | []

## 0330Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 03:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2110
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 | 1240 | 1240 | -5 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1435 | 1517 | 1517 | -82 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1417 | 1517 | 1517 | -100 | 93 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1411 | 1517 | 1517 | -106 | 93 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1397 | 1517 | 1517 | -120 | 92 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1395 | 1517 | 1517 | -122 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1133 | 1240 | 1240 | -107 | 91 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1131 | 1240 | 1240 | -109 | 91 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1382 | 1517 | 1517 | -135 | 91 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1378 | 1517 | 1517 | -139 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1115 | 1240 | 1240 | -125 | 90 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1355 | 1517 | 1517 | -162 | 89 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1355 | 1517 | 1517 | -162 | 89 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1329 | 1517 | 1517 | -188 | 88 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 | 1517 | 1517 | -207 | 86 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1301 | 1517 | 1517 | -216 | 86 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1299 | 1517 | 1517 | -218 | 86 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1298 | 1517 | 1517 | -219 | 86 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1054 | 1240 | 1240 | -186 | 85 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1287 | 1517 | 1517 | -230 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1048 | 1240 | 1240 | -192 | 85 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1275 | 1517 | 1517 | -242 | 84 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1273 | 1517 | 1517 | -244 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1269 | 1517 | 1517 | -248 | 84 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1266 | 1517 | 1517 | -251 | 83 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1265 | 1517 | 1517 | -252 | 83 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 | 1517 | 1517 | -254 | 83 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 | 1517 | 1517 | -254 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 | 1517 | 1517 | -256 | 83 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 | 1517 | 1517 | -256 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 | 1517 | 1517 | -256 | 83 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1259 | 1517 | 1517 | -258 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 | 1517 | 1517 | -265 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1250 | 1517 | 1517 | -267 | 82 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1250 | 1517 | 1517 | -267 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1247 | 1517 | 1517 | -270 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1244 | 1517 | 1517 | -273 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 | 1517 | 1517 | -277 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1012 | 1240 | 1240 | -228 | 82 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1220 | 1517 | 1517 | -297 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -993 | 1240 | 1240 | -247 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 987 | 1240 | 1240 | -253 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1194 | 1517 | 1517 | -323 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1186 | 1517 | 1517 | -331 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -968 | 1240 | 1240 | -272 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -961 | 1240 | 1240 | -279 | 78 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1363 | 1760 | 1760 | -397 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -957 | 1240 | 1240 | -283 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -954 | 1240 | 1240 | -286 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -951 | 1240 | 1240 | -289 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1163 | 1517 | 1517 | -354 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1161 | 1517 | 1517 | -356 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -947 | 1240 | 1240 | -293 | 76 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1158 | 1517 | 1517 | -359 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -944 | 1240 | 1240 | -296 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -943 | 1240 | 1240 | -297 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -942 | 1240 | 1240 | -298 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -942 | 1240 | 1240 | -298 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -941 | 1240 | 1240 | -299 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -940 | 1240 | 1240 | -300 | 76 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1329 | 1760 | 1760 | -431 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -936 | 1240 | 1240 | -304 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -935 | 1240 | 1240 | -305 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -935 | 1240 | 1240 | -305 | 75 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -933 | 1240 | 1240 | -307 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -933 | 1240 | 1240 | -307 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 926 | 1240 | 1240 | -314 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -917 | 1240 | 1240 | -323 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -917 | 1240 | 1240 | -323 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -910 | 1240 | 1240 | -330 | 73 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -894 | 1240 | 1240 | -346 | 72 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -888 | 1240 | 1240 | -352 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -874 | 1240 | 1240 | -366 | 71 | []

## 0330Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 03:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2110
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 |  | 1240 | -5 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1435 |  | 1517 | -82 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1417 |  | 1517 | -100 | 93 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1411 |  | 1517 | -106 | 93 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1397 |  | 1517 | -120 | 92 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1395 |  | 1517 | -122 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1133 |  | 1240 | -107 | 91 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1131 |  | 1240 | -109 | 91 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1382 |  | 1517 | -135 | 91 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1378 |  | 1517 | -139 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1115 |  | 1240 | -125 | 90 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1355 |  | 1517 | -162 | 89 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1355 |  | 1517 | -162 | 89 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1329 |  | 1517 | -188 | 88 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 |  | 1517 | -207 | 86 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1301 |  | 1517 | -216 | 86 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1299 |  | 1517 | -218 | 86 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1298 |  | 1517 | -219 | 86 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1054 |  | 1240 | -186 | 85 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1287 |  | 1517 | -230 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1048 |  | 1240 | -192 | 85 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1275 |  | 1517 | -242 | 84 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1273 |  | 1517 | -244 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1269 |  | 1517 | -248 | 84 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1266 |  | 1517 | -251 | 83 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1265 |  | 1517 | -252 | 83 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 |  | 1517 | -254 | 83 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 |  | 1517 | -254 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 |  | 1517 | -256 | 83 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 |  | 1517 | -256 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 |  | 1517 | -256 | 83 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1259 |  | 1517 | -258 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 |  | 1517 | -265 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1250 |  | 1517 | -267 | 82 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1250 |  | 1517 | -267 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1247 |  | 1517 | -270 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1244 |  | 1517 | -273 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 |  | 1517 | -277 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1012 |  | 1240 | -228 | 82 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1220 |  | 1517 | -297 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -993 |  | 1240 | -247 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 987 |  | 1240 | -253 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1194 |  | 1517 | -323 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1186 |  | 1517 | -331 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -968 |  | 1240 | -272 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -961 |  | 1240 | -279 | 78 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1363 |  | 1760 | -397 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -957 |  | 1240 | -283 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -954 |  | 1240 | -286 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -951 |  | 1240 | -289 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1163 |  | 1517 | -354 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1161 |  | 1517 | -356 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -947 |  | 1240 | -293 | 76 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1158 |  | 1517 | -359 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -944 |  | 1240 | -296 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -943 |  | 1240 | -297 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -942 |  | 1240 | -298 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -942 |  | 1240 | -298 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -941 |  | 1240 | -299 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -940 |  | 1240 | -300 | 76 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1329 |  | 1760 | -431 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -936 |  | 1240 | -304 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -935 |  | 1240 | -305 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -935 |  | 1240 | -305 | 75 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -933 |  | 1240 | -307 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -933 |  | 1240 | -307 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 926 |  | 1240 | -314 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -917 |  | 1240 | -323 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -917 |  | 1240 | -323 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -910 |  | 1240 | -330 | 73 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -894 |  | 1240 | -346 | 72 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -888 |  | 1240 | -352 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -874 |  | 1240 | -366 | 71 | []

## 0430Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 04:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2097
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 | 1240 | 1240 | -6 | 99 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1446 | 1517 | 1517 | -71 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1430 | 1517 | 1517 | -87 | 94 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1423 | 1517 | 1517 | -94 | 94 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1411 | 1517 | 1517 | -106 | 93 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1409 | 1517 | 1517 | -108 | 93 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1392 | 1517 | 1517 | -125 | 92 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1386 | 1517 | 1517 | -131 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1131 | 1240 | 1240 | -109 | 91 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1128 | 1240 | 1240 | -112 | 91 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1364 | 1517 | 1517 | -153 | 90 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1364 | 1517 | 1517 | -153 | 90 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1112 | 1240 | 1240 | -128 | 90 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1342 | 1517 | 1517 | -175 | 88 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1321 | 1517 | 1517 | -196 | 87 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1311 | 1517 | 1517 | -206 | 86 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 | 1517 | 1517 | -207 | 86 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1307 | 1517 | 1517 | -210 | 86 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1295 | 1517 | 1517 | -222 | 85 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1285 | 1517 | 1517 | -232 | 85 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1283 | 1517 | 1517 | -234 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1047 | 1240 | 1240 | -193 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1277 | 1517 | 1517 | -240 | 84 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1275 | 1517 | 1517 | -242 | 84 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1273 | 1517 | 1517 | -244 | 84 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1273 | 1517 | 1517 | -244 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1271 | 1517 | 1517 | -246 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1269 | 1517 | 1517 | -248 | 84 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1269 | 1517 | 1517 | -248 | 84 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1268 | 1517 | 1517 | -249 | 84 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1267 | 1517 | 1517 | -250 | 84 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1260 | 1517 | 1517 | -257 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1258 | 1517 | 1517 | -259 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1257 | 1517 | 1517 | -260 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1254 | 1517 | 1517 | -263 | 83 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1251 | 1517 | 1517 | -266 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1249 | 1517 | 1517 | -268 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1020 | 1240 | 1240 | -220 | 82 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1222 | 1517 | 1517 | -295 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -994 | 1240 | 1240 | -246 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 987 | 1240 | 1240 | -253 | 80 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1388 | 1760 | 1760 | -372 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1194 | 1517 | 1517 | -323 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1192 | 1517 | 1517 | -325 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -963 | 1240 | 1240 | -277 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1172 | 1517 | 1517 | -345 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1172 | 1517 | 1517 | -345 | 77 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -958 | 1240 | 1240 | -282 | 77 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1357 | 1760 | 1760 | -403 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -956 | 1240 | 1240 | -284 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -955 | 1240 | 1240 | -285 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1168 | 1517 | 1517 | -349 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -949 | 1240 | 1240 | -291 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -943 | 1240 | 1240 | -297 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -942 | 1240 | 1240 | -298 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -939 | 1240 | 1240 | -301 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 | 1240 | 1240 | -302 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 | 1240 | 1240 | -302 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 | 1240 | 1240 | -302 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -936 | 1240 | 1240 | -304 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -932 | 1240 | 1240 | -308 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -932 | 1240 | 1240 | -308 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -930 | 1240 | 1240 | -310 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -929 | 1240 | 1240 | -311 | 75 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -925 | 1240 | 1240 | -315 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 922 | 1240 | 1240 | -318 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -913 | 1240 | 1240 | -327 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -912 | 1240 | 1240 | -328 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -903 | 1240 | 1240 | -337 | 73 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -888 | 1240 | 1240 | -352 | 72 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 534 | 750 | 750 | -216 | 71 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -875 | 1240 | 1240 | -365 | 71 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1051 | 1500 | 1500 | -449 | 70 | []

## 0430Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 04:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2097
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 |  | 1240 | -6 | 99 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1446 |  | 1517 | -71 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1430 |  | 1517 | -87 | 94 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1423 |  | 1517 | -94 | 94 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1411 |  | 1517 | -106 | 93 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1409 |  | 1517 | -108 | 93 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1392 |  | 1517 | -125 | 92 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1386 |  | 1517 | -131 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1131 |  | 1240 | -109 | 91 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1128 |  | 1240 | -112 | 91 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1364 |  | 1517 | -153 | 90 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1364 |  | 1517 | -153 | 90 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1112 |  | 1240 | -128 | 90 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1342 |  | 1517 | -175 | 88 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1321 |  | 1517 | -196 | 87 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1311 |  | 1517 | -206 | 86 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 |  | 1517 | -207 | 86 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1307 |  | 1517 | -210 | 86 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1295 |  | 1517 | -222 | 85 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1285 |  | 1517 | -232 | 85 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1283 |  | 1517 | -234 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1047 |  | 1240 | -193 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1277 |  | 1517 | -240 | 84 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1275 |  | 1517 | -242 | 84 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1273 |  | 1517 | -244 | 84 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1273 |  | 1517 | -244 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1271 |  | 1517 | -246 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1269 |  | 1517 | -248 | 84 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1269 |  | 1517 | -248 | 84 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1268 |  | 1517 | -249 | 84 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1267 |  | 1517 | -250 | 84 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1260 |  | 1517 | -257 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1258 |  | 1517 | -259 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1257 |  | 1517 | -260 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1254 |  | 1517 | -263 | 83 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1251 |  | 1517 | -266 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1249 |  | 1517 | -268 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1020 |  | 1240 | -220 | 82 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1222 |  | 1517 | -295 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -994 |  | 1240 | -246 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 987 |  | 1240 | -253 | 80 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1388 |  | 1760 | -372 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1194 |  | 1517 | -323 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1192 |  | 1517 | -325 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -963 |  | 1240 | -277 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1172 |  | 1517 | -345 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1172 |  | 1517 | -345 | 77 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -958 |  | 1240 | -282 | 77 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1357 |  | 1760 | -403 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -956 |  | 1240 | -284 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -955 |  | 1240 | -285 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1168 |  | 1517 | -349 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -949 |  | 1240 | -291 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -943 |  | 1240 | -297 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -942 |  | 1240 | -298 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -939 |  | 1240 | -301 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 |  | 1240 | -302 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 |  | 1240 | -302 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 |  | 1240 | -302 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -936 |  | 1240 | -304 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -932 |  | 1240 | -308 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -932 |  | 1240 | -308 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -930 |  | 1240 | -310 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -929 |  | 1240 | -311 | 75 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -925 |  | 1240 | -315 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 922 |  | 1240 | -318 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -913 |  | 1240 | -327 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -912 |  | 1240 | -328 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -903 |  | 1240 | -337 | 73 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -888 |  | 1240 | -352 | 72 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 534 |  | 750 | -216 | 71 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -875 |  | 1240 | -365 | 71 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1051 |  | 1500 | -449 | 70 | []

## 0530Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 05:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2132
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 | 1240 | 1240 | -3 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1448 | 1517 | 1517 | -69 | 95 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1428 | 1517 | 1517 | -89 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1428 | 1517 | 1517 | -89 | 94 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1407 | 1517 | 1517 | -110 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1148 | 1240 | 1240 | -92 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1137 | 1240 | 1240 | -103 | 92 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1388 | 1517 | 1517 | -129 | 91 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1387 | 1517 | 1517 | -130 | 91 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1384 | 1517 | 1517 | -133 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1128 | 1240 | 1240 | -112 | 91 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1362 | 1517 | 1517 | -155 | 90 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1357 | 1517 | 1517 | -160 | 89 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1357 | 1517 | 1517 | -160 | 89 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1314 | 1517 | 1517 | -203 | 87 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 | 1517 | 1517 | -207 | 86 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1307 | 1517 | 1517 | -210 | 86 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1298 | 1517 | 1517 | -219 | 86 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1289 | 1517 | 1517 | -228 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1051 | 1240 | 1240 | -189 | 85 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1280 | 1517 | 1517 | -237 | 84 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1274 | 1517 | 1517 | -243 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1267 | 1517 | 1517 | -250 | 84 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1267 | 1517 | 1517 | -250 | 84 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1265 | 1517 | 1517 | -252 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1265 | 1517 | 1517 | -252 | 83 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1467 | 1760 | 1760 | -293 | 83 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 | 1517 | 1517 | -253 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 | 1517 | 1517 | -254 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1032 | 1240 | 1240 | -208 | 83 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 | 1517 | 1517 | -256 | 83 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 | 1517 | 1517 | -256 | 83 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 | 1517 | 1517 | -256 | 83 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [OPP] [RO] | RLAC212 _RFILE22 _1:line | 572 | 690 | 690 | -118 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1253 | 1517 | 1517 | -264 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 | 1517 | 1517 | -265 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 | 1517 | 1517 | -265 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1246 | 1517 | 1517 | -271 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1246 | 1517 | 1517 | -271 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1242 | 1517 | 1517 | -275 | 82 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1425 | 1760 | 1760 | -335 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1225 | 1517 | 1517 | -292 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1000 | 1240 | 1240 | -240 | 81 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 992 | 1240 | 1240 | -248 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1202 | 1517 | 1517 | -315 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -972 | 1240 | 1240 | -268 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1186 | 1517 | 1517 | -331 | 78 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -968 | 1240 | 1240 | -272 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -967 | 1240 | 1240 | -273 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -956 | 1240 | 1240 | -284 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1169 | 1517 | 1517 | -348 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -955 | 1240 | 1240 | -285 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1167 | 1517 | 1517 | -350 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -951 | 1240 | 1240 | -289 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -951 | 1240 | 1240 | -289 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -948 | 1240 | 1240 | -292 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -948 | 1240 | 1240 | -292 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1159 | 1517 | 1517 | -358 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -947 | 1240 | 1240 | -293 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -945 | 1240 | 1240 | -295 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -944 | 1240 | 1240 | -296 | 76 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -939 | 1240 | 1240 | -301 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -939 | 1240 | 1240 | -301 | 76 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 | 1240 | 1240 | -302 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 | 1240 | 1240 | -302 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 934 | 1240 | 1240 | -306 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -925 | 1240 | 1240 | -315 | 75 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -925 | 1240 | 1240 | -315 | 75 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -916 | 1240 | 1240 | -324 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 881 | 1240 | 1240 | -359 | 71 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 526 | 750 | 750 | -224 | 70 | []

## 0530Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 05:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2132
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 |  | 1240 | -3 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1448 |  | 1517 | -69 | 95 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1428 |  | 1517 | -89 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1428 |  | 1517 | -89 | 94 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1407 |  | 1517 | -110 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1148 |  | 1240 | -92 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1137 |  | 1240 | -103 | 92 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1388 |  | 1517 | -129 | 91 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1387 |  | 1517 | -130 | 91 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1384 |  | 1517 | -133 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1128 |  | 1240 | -112 | 91 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1362 |  | 1517 | -155 | 90 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1357 |  | 1517 | -160 | 89 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1357 |  | 1517 | -160 | 89 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1314 |  | 1517 | -203 | 87 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 |  | 1517 | -207 | 86 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1307 |  | 1517 | -210 | 86 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1298 |  | 1517 | -219 | 86 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1289 |  | 1517 | -228 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1051 |  | 1240 | -189 | 85 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1280 |  | 1517 | -237 | 84 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1274 |  | 1517 | -243 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1267 |  | 1517 | -250 | 84 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1267 |  | 1517 | -250 | 84 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1265 |  | 1517 | -252 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1265 |  | 1517 | -252 | 83 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1467 |  | 1760 | -293 | 83 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 |  | 1517 | -253 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 |  | 1517 | -254 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1032 |  | 1240 | -208 | 83 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 |  | 1517 | -256 | 83 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 |  | 1517 | -256 | 83 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 |  | 1517 | -256 | 83 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [OPP] [RO] | RLAC212 _RFILE22 _1:line | 572 |  | 690 | -118 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1253 |  | 1517 | -264 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 |  | 1517 | -265 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 |  | 1517 | -265 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1246 |  | 1517 | -271 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1246 |  | 1517 | -271 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1242 |  | 1517 | -275 | 82 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1425 |  | 1760 | -335 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1225 |  | 1517 | -292 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1000 |  | 1240 | -240 | 81 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 992 |  | 1240 | -248 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1202 |  | 1517 | -315 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -972 |  | 1240 | -268 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1186 |  | 1517 | -331 | 78 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -968 |  | 1240 | -272 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -967 |  | 1240 | -273 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -956 |  | 1240 | -284 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1169 |  | 1517 | -348 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -955 |  | 1240 | -285 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1167 |  | 1517 | -350 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -951 |  | 1240 | -289 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -951 |  | 1240 | -289 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -948 |  | 1240 | -292 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -948 |  | 1240 | -292 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1159 |  | 1517 | -358 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -947 |  | 1240 | -293 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -945 |  | 1240 | -295 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -944 |  | 1240 | -296 | 76 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -939 |  | 1240 | -301 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -939 |  | 1240 | -301 | 76 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 |  | 1240 | -302 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 |  | 1240 | -302 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 934 |  | 1240 | -306 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -925 |  | 1240 | -315 | 75 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -925 |  | 1240 | -315 | 75 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -916 |  | 1240 | -324 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 881 |  | 1240 | -359 | 71 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 526 |  | 750 | -224 | 70 | []

## 0630Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 06:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2230
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 | 1240 | 1240 | -6 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [OPP] [RO] | RLAC212 _RFILE22 _1:line | 654 | 690 | 690 | -36 | 95 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1425 | 1517 | 1517 | -92 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1403 | 1517 | 1517 | -114 | 92 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1144 | 1240 | 1240 | -96 | 92 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1399 | 1517 | 1517 | -118 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1134 | 1240 | 1240 | -106 | 91 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1382 | 1517 | 1517 | -135 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1126 | 1240 | 1240 | -114 | 91 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1361 | 1517 | 1517 | -156 | 90 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1360 | 1517 | 1517 | -157 | 90 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1352 | 1517 | 1517 | -165 | 89 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1336 | 1517 | 1517 | -181 | 88 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1334 | 1517 | 1517 | -183 | 88 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1333 | 1517 | 1517 | -184 | 88 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 648 | 750 | 750 | -102 | 86 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 587 | 690 | 690 | -103 | 85 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1288 | 1517 | 1517 | -229 | 85 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1286 | 1517 | 1517 | -231 | 85 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1285 | 1517 | 1517 | -232 | 85 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1271 | 1517 | 1517 | -246 | 84 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 | 1517 | 1517 | -253 | 83 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1032 | 1240 | 1240 | -208 | 83 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1255 | 1517 | 1517 | -262 | 83 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1249 | 1517 | 1517 | -268 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1245 | 1517 | 1517 | -272 | 82 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1244 | 1517 | 1517 | -273 | 82 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1243 | 1517 | 1517 | -274 | 82 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1243 | 1517 | 1517 | -274 | 82 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 | 1517 | 1517 | -277 | 82 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 | 1517 | 1517 | -277 | 82 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 | 1517 | 1517 | -277 | 82 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1239 | 1517 | 1517 | -278 | 82 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1239 | 1517 | 1517 | -278 | 82 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1237 | 1517 | 1517 | -280 | 82 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 | 1517 | 1517 | -282 | 81 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 | 1517 | 1517 | -282 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1232 | 1517 | 1517 | -285 | 81 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1425 | 1760 | 1760 | -335 | 81 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1229 | 1517 | 1517 | -288 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 | 1517 | 1517 | -296 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -994 | 1240 | 1240 | -246 | 80 | []
RO_CO_00031 | N-1 Resita-Timisoara c2 | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 598 | 750 | 750 | -152 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1197 | 1517 | 1517 | -320 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -978 | 1240 | 1240 | -262 | 79 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1380 | 1760 | 1760 | -380 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 971 | 1240 | 1240 | -269 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -967 | 1240 | 1240 | -273 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -963 | 1240 | 1240 | -277 | 78 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -959 | 1240 | 1240 | -281 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1171 | 1517 | 1517 | -346 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -952 | 1240 | 1240 | -288 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -952 | 1240 | 1240 | -288 | 77 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1164 | 1517 | 1517 | -353 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -946 | 1240 | 1240 | -294 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -946 | 1240 | 1240 | -294 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -944 | 1240 | 1240 | -296 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -943 | 1240 | 1240 | -297 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -943 | 1240 | 1240 | -297 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -942 | 1240 | 1240 | -298 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -940 | 1240 | 1240 | -300 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 | 1240 | 1240 | -302 | 76 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1145 | 1517 | 1517 | -372 | 76 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1144 | 1517 | 1517 | -373 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -934 | 1240 | 1240 | -306 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -934 | 1240 | 1240 | -306 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -933 | 1240 | 1240 | -307 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 933 | 1240 | 1240 | -307 | 75 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -933 | 1240 | 1240 | -307 | 75 | []
RO_CO_00004 | N-1 Sibiu Sud-Tantareni | [RO-RO] Baru Mare - Hasdat [DIR] [RO] | RBARU22 _RHAS122 _1:line | 558 | 750 | 750 | -192 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1128 | 1517 | 1517 | -389 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -921 | 1240 | 1240 | -319 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -921 | 1240 | 1240 | -319 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 879 | 1240 | 1240 | -361 | 71 | []

## 0630Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 06:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2230
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 |  | 1240 | -6 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [OPP] [RO] | RLAC212 _RFILE22 _1:line | 654 |  | 690 | -36 | 95 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1425 |  | 1517 | -92 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1403 |  | 1517 | -114 | 92 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1144 |  | 1240 | -96 | 92 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1399 |  | 1517 | -118 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1134 |  | 1240 | -106 | 91 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1382 |  | 1517 | -135 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1126 |  | 1240 | -114 | 91 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1361 |  | 1517 | -156 | 90 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1360 |  | 1517 | -157 | 90 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1352 |  | 1517 | -165 | 89 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1336 |  | 1517 | -181 | 88 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1334 |  | 1517 | -183 | 88 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1333 |  | 1517 | -184 | 88 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 648 |  | 750 | -102 | 86 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 587 |  | 690 | -103 | 85 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1288 |  | 1517 | -229 | 85 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1286 |  | 1517 | -231 | 85 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1285 |  | 1517 | -232 | 85 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1271 |  | 1517 | -246 | 84 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 |  | 1517 | -253 | 83 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1032 |  | 1240 | -208 | 83 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1255 |  | 1517 | -262 | 83 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1249 |  | 1517 | -268 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1245 |  | 1517 | -272 | 82 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1244 |  | 1517 | -273 | 82 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1243 |  | 1517 | -274 | 82 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1243 |  | 1517 | -274 | 82 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 |  | 1517 | -277 | 82 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 |  | 1517 | -277 | 82 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 |  | 1517 | -277 | 82 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1239 |  | 1517 | -278 | 82 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1239 |  | 1517 | -278 | 82 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1237 |  | 1517 | -280 | 82 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 |  | 1517 | -282 | 81 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 |  | 1517 | -282 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1232 |  | 1517 | -285 | 81 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1425 |  | 1760 | -335 | 81 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1229 |  | 1517 | -288 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 |  | 1517 | -296 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -994 |  | 1240 | -246 | 80 | []
RO_CO_00031 | N-1 Resita-Timisoara c2 | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 598 |  | 750 | -152 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1197 |  | 1517 | -320 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -978 |  | 1240 | -262 | 79 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1380 |  | 1760 | -380 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 971 |  | 1240 | -269 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -967 |  | 1240 | -273 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -963 |  | 1240 | -277 | 78 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -959 |  | 1240 | -281 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1171 |  | 1517 | -346 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -952 |  | 1240 | -288 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -952 |  | 1240 | -288 | 77 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1164 |  | 1517 | -353 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -946 |  | 1240 | -294 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -946 |  | 1240 | -294 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -944 |  | 1240 | -296 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -943 |  | 1240 | -297 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -943 |  | 1240 | -297 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -942 |  | 1240 | -298 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -940 |  | 1240 | -300 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -938 |  | 1240 | -302 | 76 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1145 |  | 1517 | -372 | 76 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1144 |  | 1517 | -373 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -934 |  | 1240 | -306 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -934 |  | 1240 | -306 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -933 |  | 1240 | -307 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 933 |  | 1240 | -307 | 75 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -933 |  | 1240 | -307 | 75 | []
RO_CO_00004 | N-1 Sibiu Sud-Tantareni | [RO-RO] Baru Mare - Hasdat [DIR] [RO] | RBARU22 _RHAS122 _1:line | 558 |  | 750 | -192 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1128 |  | 1517 | -389 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -921 |  | 1240 | -319 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -921 |  | 1240 | -319 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 879 |  | 1240 | -361 | 71 | []

## 0730Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 07:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 103
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 685 | 690 | 690 | -5 | 99 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 620 | 690 | 690 | -70 | 90 | []
RO_CO_00031 | N-1 Resita-Timisoara c2 | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 614 | 750 | 750 | -136 | 82 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 573 | 750 | 750 | -177 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Filesti - Barbosi [DIR] [RO] | RBARB22 _RFILE22 _1:line | -502 | -690 | -690 | -188 | 73 | []
RO_CO_00004 | N-1 Sibiu Sud-Tantareni | [RO-RO] Baru Mare - Hasdat [DIR] [RO] | RBARU22 _RHAS122 _1:line | 533 | 750 | 750 | -217 | 71 | []

## 0730Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 07:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 103
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 685 |  | 690 | -5 | 99 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 620 |  | 690 | -70 | 90 | []
RO_CO_00031 | N-1 Resita-Timisoara c2 | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 614 |  | 750 | -136 | 82 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 573 |  | 750 | -177 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Filesti - Barbosi [DIR] [RO] | RBARB22 _RFILE22 _1:line | -502 |  | -690 | -188 | 73 | []
RO_CO_00004 | N-1 Sibiu Sud-Tantareni | [RO-RO] Baru Mare - Hasdat [DIR] [RO] | RBARU22 _RHAS122 _1:line | 533 |  | 750 | -217 | 71 | []

## 0830Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 08:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]:
Fallback applied
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs

## 0830Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 08:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]:
Fallback applied
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs

## 0930Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 09:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 13
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 681 | 690 | 690 | -9 | 99 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 613 | 690 | 690 | -77 | 89 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 589 | 750 | 750 | -161 | 79 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -641 | 824 | 824 | -183 | 78 | []

## 0930Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 09:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 13
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 681 |  | 690 | -9 | 99 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 613 |  | 690 | -77 | 89 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 589 |  | 750 | -161 | 79 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -641 |  | 824 | -183 | 78 | []

## 1030Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 10:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 653
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -822 | 824 | 824 | -2 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 622 | 690 | 690 | -68 | 90 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 | 1517 | 1517 | -296 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 528 | 690 | 690 | -162 | 77 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1394 | 1888 | 1888 | -494 | 74 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 536 | 750 | 750 | -214 | 71 | []

## 1030Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 10:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 653
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -822 |  | 824 | -2 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 622 |  | 690 | -68 | 90 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 |  | 1517 | -296 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 528 |  | 690 | -162 | 77 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1394 |  | 1888 | -494 | 74 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 536 |  | 750 | -214 | 71 | []

## 1130Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 11:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 250
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -823 | 824 | 824 | -1 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 650 | 690 | 690 | -40 | 94 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 566 | 690 | 690 | -124 | 82 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1115 | 1517 | 1517 | -402 | 74 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 550 | 750 | 750 | -200 | 73 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1346 | 1888 | 1888 | -542 | 71 | []

## 1130Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 11:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 250
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -823 |  | 824 | -1 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 650 |  | 690 | -40 | 94 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 566 |  | 690 | -124 | 82 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1115 |  | 1517 | -402 | 74 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 550 |  | 750 | -200 | 73 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1346 |  | 1888 | -542 | 71 | []

## 1230Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1269
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -823 | 824 | 824 | -1 | 100 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1488 | 1517 | 1517 | -29 | 98 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [OPP] [RO] | RLAC212 _RFILE22 _1:line | 635 | 690 | 690 | -55 | 92 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1648 | 1888 | 1888 | -240 | 87 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1280 | 1517 | 1517 | -237 | 84 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1274 | 1517 | 1517 | -243 | 84 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 | 1517 | 1517 | -253 | 83 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 | 1517 | 1517 | -277 | 82 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1226 | 1517 | 1517 | -291 | 81 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1225 | 1517 | 1517 | -292 | 81 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1217 | 1517 | 1517 | -300 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 550 | 690 | 690 | -140 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1196 | 1517 | 1517 | -321 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1186 | 1517 | 1517 | -331 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1180 | 1517 | 1517 | -337 | 78 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1177 | 1517 | 1517 | -340 | 78 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1177 | 1517 | 1517 | -340 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 | 1517 | 1517 | -352 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Filesti - Barbosi [DIR] [RO] | RBARB22 _RFILE22 _1:line | -527 | -690 | -690 | -163 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1151 | 1517 | 1517 | -366 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1144 | 1517 | 1517 | -373 | 75 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1140 | 1517 | 1517 | -377 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1138 | 1517 | 1517 | -379 | 75 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1135 | 1517 | 1517 | -382 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1135 | 1517 | 1517 | -382 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1133 | 1517 | 1517 | -384 | 75 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1133 | 1517 | 1517 | -384 | 75 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1131 | 1517 | 1517 | -386 | 75 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1129 | 1517 | 1517 | -388 | 74 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1128 | 1517 | 1517 | -389 | 74 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1127 | 1517 | 1517 | -390 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1118 | 1517 | 1517 | -399 | 74 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1117 | 1517 | 1517 | -400 | 74 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1117 | 1517 | 1517 | -400 | 74 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1104 | 1517 | 1517 | -413 | 73 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1102 | 1517 | 1517 | -415 | 73 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1095 | 1517 | 1517 | -422 | 72 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1092 | 1517 | 1517 | -425 | 72 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 530 | 750 | 750 | -220 | 71 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1072 | 1517 | 1517 | -445 | 71 | []

## 1230Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1269
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -823 |  | 824 | -1 | 100 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1488 |  | 1517 | -29 | 98 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [OPP] [RO] | RLAC212 _RFILE22 _1:line | 635 |  | 690 | -55 | 92 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1648 |  | 1888 | -240 | 87 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1280 |  | 1517 | -237 | 84 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1274 |  | 1517 | -243 | 84 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 |  | 1517 | -253 | 83 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 |  | 1517 | -277 | 82 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1226 |  | 1517 | -291 | 81 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1225 |  | 1517 | -292 | 81 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1217 |  | 1517 | -300 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 550 |  | 690 | -140 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1196 |  | 1517 | -321 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1186 |  | 1517 | -331 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1180 |  | 1517 | -337 | 78 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1177 |  | 1517 | -340 | 78 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1177 |  | 1517 | -340 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 |  | 1517 | -352 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Filesti - Barbosi [DIR] [RO] | RBARB22 _RFILE22 _1:line | -527 |  | -690 | -163 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1151 |  | 1517 | -366 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1144 |  | 1517 | -373 | 75 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1140 |  | 1517 | -377 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1138 |  | 1517 | -379 | 75 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1135 |  | 1517 | -382 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1135 |  | 1517 | -382 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1133 |  | 1517 | -384 | 75 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1133 |  | 1517 | -384 | 75 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1131 |  | 1517 | -386 | 75 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1129 |  | 1517 | -388 | 74 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1128 |  | 1517 | -389 | 74 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1127 |  | 1517 | -390 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1118 |  | 1517 | -399 | 74 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1117 |  | 1517 | -400 | 74 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1117 |  | 1517 | -400 | 74 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1104 |  | 1517 | -413 | 73 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1102 |  | 1517 | -415 | 73 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1095 |  | 1517 | -422 | 72 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1092 |  | 1517 | -425 | 72 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 530 |  | 750 | -220 | 71 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1072 |  | 1517 | -445 | 71 | []

## 1330Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1365
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1516 | 1517 | 1517 | -1 | 100 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -814 | 824 | 824 | -10 | 99 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 637 | 690 | 690 | -53 | 92 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1653 | 1888 | 1888 | -235 | 88 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1312 | 1517 | 1517 | -205 | 86 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1309 | 1517 | 1517 | -208 | 86 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1301 | 1517 | 1517 | -216 | 86 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1275 | 1517 | 1517 | -242 | 84 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1258 | 1517 | 1517 | -259 | 83 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1257 | 1517 | 1517 | -260 | 83 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1250 | 1517 | 1517 | -267 | 82 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1227 | 1517 | 1517 | -290 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1217 | 1517 | 1517 | -300 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 553 | 690 | 690 | -137 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1211 | 1517 | 1517 | -306 | 80 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1211 | 1517 | 1517 | -306 | 80 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1210 | 1517 | 1517 | -307 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1195 | 1517 | 1517 | -322 | 79 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1181 | 1517 | 1517 | -336 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1173 | 1517 | 1517 | -344 | 77 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1173 | 1517 | 1517 | -344 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1168 | 1517 | 1517 | -349 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 | 1517 | 1517 | -352 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 | 1517 | 1517 | -352 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1163 | 1517 | 1517 | -354 | 77 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1163 | 1517 | 1517 | -354 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Filesti - Barbosi [DIR] [RO] | RBARB22 _RFILE22 _1:line | -529 | -690 | -690 | -161 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1161 | 1517 | 1517 | -356 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1159 | 1517 | 1517 | -358 | 76 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1158 | 1517 | 1517 | -359 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1158 | 1517 | 1517 | -359 | 76 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1149 | 1517 | 1517 | -368 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1147 | 1517 | 1517 | -370 | 76 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1146 | 1517 | 1517 | -371 | 76 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1136 | 1517 | 1517 | -381 | 75 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1133 | 1517 | 1517 | -384 | 75 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1125 | 1517 | 1517 | -392 | 74 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1124 | 1517 | 1517 | -393 | 74 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 546 | 750 | 750 | -204 | 73 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1103 | 1517 | 1517 | -414 | 73 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1088 | 1517 | 1517 | -429 | 72 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1087 | 1517 | 1517 | -430 | 72 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1062 | 1517 | 1517 | -455 | 70 | []

## 1330Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1365
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1516 |  | 1517 | -1 | 100 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -814 |  | 824 | -10 | 99 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 637 |  | 690 | -53 | 92 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1653 |  | 1888 | -235 | 88 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1312 |  | 1517 | -205 | 86 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1309 |  | 1517 | -208 | 86 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1301 |  | 1517 | -216 | 86 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1275 |  | 1517 | -242 | 84 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1258 |  | 1517 | -259 | 83 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1257 |  | 1517 | -260 | 83 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1250 |  | 1517 | -267 | 82 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1227 |  | 1517 | -290 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1217 |  | 1517 | -300 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 553 |  | 690 | -137 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1211 |  | 1517 | -306 | 80 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1211 |  | 1517 | -306 | 80 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1210 |  | 1517 | -307 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1195 |  | 1517 | -322 | 79 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1181 |  | 1517 | -336 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1173 |  | 1517 | -344 | 77 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1173 |  | 1517 | -344 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1168 |  | 1517 | -349 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 |  | 1517 | -352 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1165 |  | 1517 | -352 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1163 |  | 1517 | -354 | 77 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1163 |  | 1517 | -354 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Filesti - Barbosi [DIR] [RO] | RBARB22 _RFILE22 _1:line | -529 |  | -690 | -161 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1161 |  | 1517 | -356 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1159 |  | 1517 | -358 | 76 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1158 |  | 1517 | -359 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1158 |  | 1517 | -359 | 76 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1149 |  | 1517 | -368 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1147 |  | 1517 | -370 | 76 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1146 |  | 1517 | -371 | 76 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1136 |  | 1517 | -381 | 75 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1133 |  | 1517 | -384 | 75 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1125 |  | 1517 | -392 | 74 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1124 |  | 1517 | -393 | 74 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 546 |  | 750 | -204 | 73 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1103 |  | 1517 | -414 | 73 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1088 |  | 1517 | -429 | 72 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1087 |  | 1517 | -430 | 72 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1062 |  | 1517 | -455 | 70 | []

## 1430Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 245
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 674 | 690 | 690 | -16 | 98 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 602 | 690 | 690 | -88 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Filesti - Barbosi [DIR] [RO] | RBARB22 _RFILE22 _1:line | -557 | -690 | -690 | -133 | 81 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 584 | 750 | 750 | -166 | 78 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 529 | 690 | 690 | -161 | 77 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -604 | 824 | 824 | -220 | 73 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [OPP] [RO] | RGUTI41 _RSMIR41 _1:line | -1051 | -1500 | -1500 | -449 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 245
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 674 |  | 690 | -16 | 98 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 602 |  | 690 | -88 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Filesti - Barbosi [DIR] [RO] | RBARB22 _RFILE22 _1:line | -557 |  | -690 | -133 | 81 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 584 |  | 750 | -166 | 78 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 529 |  | 690 | -161 | 77 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -604 |  | 824 | -220 | 73 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [OPP] [RO] | RGUTI41 _RSMIR41 _1:line | -1051 |  | -1500 | -449 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 944
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -823 | 824 | 824 | -1 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 619 | 690 | 690 | -71 | 90 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1354 | 1517 | 1517 | -163 | 89 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1544 | 1888 | 1888 | -344 | 82 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 584 | 750 | 750 | -166 | 78 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 533 | 690 | 690 | -157 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1138 | 1517 | 1517 | -379 | 75 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1130 | 1517 | 1517 | -387 | 75 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1121 | 1517 | 1517 | -396 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1094 | 1517 | 1517 | -423 | 72 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1094 | 1517 | 1517 | -423 | 72 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1092 | 1517 | 1517 | -425 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1081 | 1517 | 1517 | -436 | 71 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1074 | 1517 | 1517 | -443 | 71 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1062 | 1517 | 1517 | -455 | 70 | []

## 1530Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 944
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -823 |  | 824 | -1 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 619 |  | 690 | -71 | 90 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1354 |  | 1517 | -163 | 89 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1544 |  | 1888 | -344 | 82 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 584 |  | 750 | -166 | 78 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 533 |  | 690 | -157 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1138 |  | 1517 | -379 | 75 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1130 |  | 1517 | -387 | 75 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1121 |  | 1517 | -396 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1094 |  | 1517 | -423 | 72 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1094 |  | 1517 | -423 | 72 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1092 |  | 1517 | -425 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1081 |  | 1517 | -436 | 71 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1074 |  | 1517 | -443 | 71 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1062 |  | 1517 | -455 | 70 | []

## 1630Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2221
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1514 | 1517 | 1517 | -3 | 100 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1208 | 1240 | 1240 | -32 | 97 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1387 | 1517 | 1517 | -130 | 91 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1375 | 1517 | 1517 | -142 | 91 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1121 | 1240 | 1240 | -119 | 90 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1119 | 1240 | 1240 | -121 | 90 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1367 | 1517 | 1517 | -150 | 90 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1347 | 1517 | 1517 | -170 | 89 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1092 | 1240 | 1240 | -148 | 88 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1076 | 1240 | 1240 | -164 | 87 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1303 | 1517 | 1517 | -214 | 86 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1302 | 1517 | 1517 | -215 | 86 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1302 | 1517 | 1517 | -215 | 86 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1294 | 1517 | 1517 | -223 | 85 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1294 | 1517 | 1517 | -223 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1038 | 1240 | 1240 | -202 | 84 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1266 | 1517 | 1517 | -251 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1266 | 1517 | 1517 | -251 | 83 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 | 1517 | 1517 | -253 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1029 | 1240 | 1240 | -211 | 83 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1563 | 1888 | 1888 | -325 | 83 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 | 1517 | 1517 | -277 | 82 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1237 | 1517 | 1517 | -280 | 82 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1233 | 1517 | 1517 | -284 | 81 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1230 | 1517 | 1517 | -287 | 81 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1228 | 1517 | 1517 | -289 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1226 | 1517 | 1517 | -291 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1222 | 1517 | 1517 | -295 | 81 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 | 1517 | 1517 | -296 | 80 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 996 | 1240 | 1240 | -244 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1218 | 1517 | 1517 | -299 | 80 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1217 | 1517 | 1517 | -300 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1216 | 1517 | 1517 | -301 | 80 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1215 | 1517 | 1517 | -302 | 80 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1213 | 1517 | 1517 | -304 | 80 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1213 | 1517 | 1517 | -304 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1213 | 1517 | 1517 | -304 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1211 | 1517 | 1517 | -306 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1210 | 1517 | 1517 | -307 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 550 | 690 | 690 | -140 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 | 1517 | 1517 | -308 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 987 | 1240 | 1240 | -253 | 80 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1192 | 1517 | 1517 | -325 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 963 | 1240 | 1240 | -277 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1176 | 1517 | 1517 | -341 | 77 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 960 | 1240 | 1240 | -280 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 955 | 1240 | 1240 | -285 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 954 | 1240 | 1240 | -286 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 950 | 1240 | 1240 | -290 | 77 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 950 | 1240 | 1240 | -290 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 948 | 1240 | 1240 | -292 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 947 | 1240 | 1240 | -293 | 76 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1153 | 1517 | 1517 | -364 | 76 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 | 1240 | 1240 | -298 | 76 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 570 | 750 | 750 | -180 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 | 1240 | 1240 | -298 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 | 1240 | 1240 | -298 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 | 1240 | 1240 | -298 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 941 | 1240 | 1240 | -299 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 939 | 1240 | 1240 | -301 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 937 | 1240 | 1240 | -303 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 932 | 1240 | 1240 | -308 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 931 | 1240 | 1240 | -309 | 75 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1138 | 1517 | 1517 | -379 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1137 | 1517 | 1517 | -380 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 929 | 1240 | 1240 | -311 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 926 | 1240 | 1240 | -314 | 75 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 926 | 1240 | 1240 | -314 | 75 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 922 | 1240 | 1240 | -318 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 911 | 1240 | 1240 | -329 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1111 | 1517 | 1517 | -406 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 906 | 1240 | 1240 | -334 | 73 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1107 | 1517 | 1517 | -410 | 73 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -591 | 824 | 824 | -233 | 72 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 882 | 1240 | 1240 | -358 | 71 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -869 | 1240 | 1240 | -371 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2221
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1514 |  | 1517 | -3 | 100 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1208 |  | 1240 | -32 | 97 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1387 |  | 1517 | -130 | 91 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1375 |  | 1517 | -142 | 91 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1121 |  | 1240 | -119 | 90 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1119 |  | 1240 | -121 | 90 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1367 |  | 1517 | -150 | 90 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1347 |  | 1517 | -170 | 89 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1092 |  | 1240 | -148 | 88 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1076 |  | 1240 | -164 | 87 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1303 |  | 1517 | -214 | 86 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1302 |  | 1517 | -215 | 86 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1302 |  | 1517 | -215 | 86 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1294 |  | 1517 | -223 | 85 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1294 |  | 1517 | -223 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1038 |  | 1240 | -202 | 84 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1266 |  | 1517 | -251 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1266 |  | 1517 | -251 | 83 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1264 |  | 1517 | -253 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1029 |  | 1240 | -211 | 83 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1563 |  | 1888 | -325 | 83 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 |  | 1517 | -277 | 82 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1237 |  | 1517 | -280 | 82 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1233 |  | 1517 | -284 | 81 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1230 |  | 1517 | -287 | 81 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1228 |  | 1517 | -289 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1226 |  | 1517 | -291 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1222 |  | 1517 | -295 | 81 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 |  | 1517 | -296 | 80 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 996 |  | 1240 | -244 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1218 |  | 1517 | -299 | 80 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1217 |  | 1517 | -300 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1216 |  | 1517 | -301 | 80 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1215 |  | 1517 | -302 | 80 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1213 |  | 1517 | -304 | 80 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1213 |  | 1517 | -304 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1213 |  | 1517 | -304 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1211 |  | 1517 | -306 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1210 |  | 1517 | -307 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 550 |  | 690 | -140 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 |  | 1517 | -308 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 987 |  | 1240 | -253 | 80 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1192 |  | 1517 | -325 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 963 |  | 1240 | -277 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1176 |  | 1517 | -341 | 77 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 960 |  | 1240 | -280 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 955 |  | 1240 | -285 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 954 |  | 1240 | -286 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 950 |  | 1240 | -290 | 77 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 950 |  | 1240 | -290 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 948 |  | 1240 | -292 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 947 |  | 1240 | -293 | 76 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1153 |  | 1517 | -364 | 76 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 |  | 1240 | -298 | 76 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 570 |  | 750 | -180 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 |  | 1240 | -298 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 |  | 1240 | -298 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 942 |  | 1240 | -298 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 941 |  | 1240 | -299 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 939 |  | 1240 | -301 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 937 |  | 1240 | -303 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 932 |  | 1240 | -308 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 931 |  | 1240 | -309 | 75 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1138 |  | 1517 | -379 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1137 |  | 1517 | -380 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 929 |  | 1240 | -311 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 926 |  | 1240 | -314 | 75 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 926 |  | 1240 | -314 | 75 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 922 |  | 1240 | -318 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 911 |  | 1240 | -329 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1111 |  | 1517 | -406 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 906 |  | 1240 | -334 | 73 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1107 |  | 1517 | -410 | 73 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -591 |  | 824 | -233 | 72 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 882 |  | 1240 | -358 | 71 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -869 |  | 1240 | -371 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2208
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 | 1240 | 1240 | -3 | 100 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1466 | 1517 | 1517 | -51 | 97 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1151 | 1240 | 1240 | -89 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1147 | 1240 | 1240 | -93 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1122 | 1240 | 1240 | -118 | 90 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1367 | 1517 | 1517 | -150 | 90 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1357 | 1517 | 1517 | -160 | 89 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1094 | 1240 | 1240 | -146 | 88 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1338 | 1517 | 1517 | -179 | 88 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1331 | 1517 | 1517 | -186 | 88 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1061 | 1240 | 1240 | -179 | 86 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1293 | 1517 | 1517 | -224 | 85 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1293 | 1517 | 1517 | -224 | 85 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1292 | 1517 | 1517 | -225 | 85 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1280 | 1517 | 1517 | -237 | 84 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1279 | 1517 | 1517 | -238 | 84 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1275 | 1517 | 1517 | -242 | 84 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 | 1517 | 1517 | -256 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 | 1517 | 1517 | -265 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1022 | 1240 | 1240 | -218 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1016 | 1240 | 1240 | -224 | 82 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1228 | 1517 | 1517 | -289 | 81 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 | 1517 | 1517 | -296 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 996 | 1240 | 1240 | -244 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 554 | 690 | 690 | -136 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1216 | 1517 | 1517 | -301 | 80 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1216 | 1517 | 1517 | -301 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1212 | 1517 | 1517 | -305 | 80 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1210 | 1517 | 1517 | -307 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 | 1517 | 1517 | -308 | 80 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1206 | 1517 | 1517 | -311 | 80 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1206 | 1517 | 1517 | -311 | 80 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 | 1240 | 1240 | -256 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1202 | 1517 | 1517 | -315 | 79 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1202 | 1517 | 1517 | -315 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1202 | 1517 | 1517 | -315 | 79 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1200 | 1517 | 1517 | -317 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 981 | 1240 | 1240 | -259 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1199 | 1517 | 1517 | -318 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1199 | 1517 | 1517 | -318 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 980 | 1240 | 1240 | -260 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1196 | 1517 | 1517 | -321 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1194 | 1517 | 1517 | -323 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -974 | 1240 | 1240 | -266 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 971 | 1240 | 1240 | -269 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 | 1240 | 1240 | -270 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 | 1240 | 1240 | -270 | 78 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1186 | 1517 | 1517 | -331 | 78 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 586 | 750 | 750 | -164 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 | 1240 | 1240 | -273 | 78 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 964 | 1240 | 1240 | -276 | 78 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1179 | 1517 | 1517 | -338 | 78 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -962 | 1240 | 1240 | -278 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 962 | 1240 | 1240 | -278 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 961 | 1240 | 1240 | -279 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 960 | 1240 | 1240 | -280 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 958 | 1240 | 1240 | -282 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1170 | 1517 | 1517 | -347 | 77 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 956 | 1240 | 1240 | -284 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -953 | 1240 | 1240 | -287 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 953 | 1240 | 1240 | -287 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -952 | 1240 | 1240 | -288 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 950 | 1240 | 1240 | -290 | 77 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1443 | 1888 | 1888 | -445 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 947 | 1240 | 1240 | -293 | 76 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 946 | 1240 | 1240 | -294 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 946 | 1240 | 1240 | -294 | 76 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1151 | 1517 | 1517 | -366 | 76 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1124 | 1517 | 1517 | -393 | 74 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1123 | 1517 | 1517 | -394 | 74 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -908 | 1240 | 1240 | -332 | 73 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 904 | 1240 | 1240 | -336 | 73 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1100 | 1517 | 1517 | -417 | 73 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1272 | 1760 | 1760 | -488 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1095 | 1517 | 1517 | -422 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -888 | 1240 | 1240 | -352 | 72 | []

## 1730Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2208
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 |  | 1240 | -3 | 100 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1466 |  | 1517 | -51 | 97 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1151 |  | 1240 | -89 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1147 |  | 1240 | -93 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1122 |  | 1240 | -118 | 90 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1367 |  | 1517 | -150 | 90 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1357 |  | 1517 | -160 | 89 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1094 |  | 1240 | -146 | 88 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1338 |  | 1517 | -179 | 88 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1331 |  | 1517 | -186 | 88 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1061 |  | 1240 | -179 | 86 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1293 |  | 1517 | -224 | 85 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1293 |  | 1517 | -224 | 85 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1292 |  | 1517 | -225 | 85 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1280 |  | 1517 | -237 | 84 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1279 |  | 1517 | -238 | 84 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1275 |  | 1517 | -242 | 84 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1261 |  | 1517 | -256 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1252 |  | 1517 | -265 | 83 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1022 |  | 1240 | -218 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1016 |  | 1240 | -224 | 82 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1228 |  | 1517 | -289 | 81 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 |  | 1517 | -296 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 996 |  | 1240 | -244 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [DIR] [RO] | RLAC212 _RFILE22 _1:line | 554 |  | 690 | -136 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1216 |  | 1517 | -301 | 80 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1216 |  | 1517 | -301 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1212 |  | 1517 | -305 | 80 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1210 |  | 1517 | -307 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 |  | 1517 | -308 | 80 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1206 |  | 1517 | -311 | 80 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1206 |  | 1517 | -311 | 80 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 |  | 1240 | -256 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1202 |  | 1517 | -315 | 79 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1202 |  | 1517 | -315 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1202 |  | 1517 | -315 | 79 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1200 |  | 1517 | -317 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 981 |  | 1240 | -259 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1199 |  | 1517 | -318 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1199 |  | 1517 | -318 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 980 |  | 1240 | -260 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1196 |  | 1517 | -321 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1194 |  | 1517 | -323 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -974 |  | 1240 | -266 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 971 |  | 1240 | -269 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 |  | 1240 | -270 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 |  | 1240 | -270 | 78 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1186 |  | 1517 | -331 | 78 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 586 |  | 750 | -164 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 |  | 1240 | -273 | 78 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 964 |  | 1240 | -276 | 78 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1179 |  | 1517 | -338 | 78 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -962 |  | 1240 | -278 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 962 |  | 1240 | -278 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 961 |  | 1240 | -279 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 960 |  | 1240 | -280 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 958 |  | 1240 | -282 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1170 |  | 1517 | -347 | 77 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 956 |  | 1240 | -284 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -953 |  | 1240 | -287 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 953 |  | 1240 | -287 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -952 |  | 1240 | -288 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 950 |  | 1240 | -290 | 77 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1443 |  | 1888 | -445 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 947 |  | 1240 | -293 | 76 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 946 |  | 1240 | -294 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 946 |  | 1240 | -294 | 76 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1151 |  | 1517 | -366 | 76 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1124 |  | 1517 | -393 | 74 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1123 |  | 1517 | -394 | 74 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -908 |  | 1240 | -332 | 73 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 904 |  | 1240 | -336 | 73 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1100 |  | 1517 | -417 | 73 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1272 |  | 1760 | -488 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1095 |  | 1517 | -422 | 72 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -888 |  | 1240 | -352 | 72 | []

## 1830Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2239
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 | 1240 | 1240 | 0 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1173 | 1240 | 1240 | -67 | 95 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [OPP] [RO] | RLAC212 _RFILE22 _1:line | 651 | 690 | 690 | -39 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1157 | 1240 | 1240 | -83 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1152 | 1240 | 1240 | -88 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1125 | 1240 | 1240 | -115 | 91 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1372 | 1517 | 1517 | -145 | 90 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1078 | 1240 | 1240 | -162 | 87 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 | 1517 | 1517 | -207 | 86 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1300 | 1517 | 1517 | -217 | 86 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1053 | 1240 | 1240 | -187 | 85 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1288 | 1517 | 1517 | -229 | 85 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1277 | 1517 | 1517 | -240 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1021 | 1240 | 1240 | -219 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 567 | 690 | 690 | -123 | 82 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1241 | 1517 | 1517 | -276 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1013 | 1240 | 1240 | -227 | 82 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 613 | 750 | 750 | -137 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1011 | 1240 | 1240 | -229 | 82 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 | 1517 | 1517 | -282 | 81 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 | 1517 | 1517 | -282 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 997 | 1240 | 1240 | -243 | 80 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 995 | 1240 | 1240 | -245 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1215 | 1517 | 1517 | -302 | 80 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1215 | 1517 | 1517 | -302 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1214 | 1517 | 1517 | -303 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 989 | 1240 | 1240 | -251 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 987 | 1240 | 1240 | -253 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 | 1240 | 1240 | -256 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 | 1240 | 1240 | -256 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 983 | 1240 | 1240 | -257 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -982 | 1240 | 1240 | -258 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1200 | 1517 | 1517 | -317 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 978 | 1240 | 1240 | -262 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 | 1240 | 1240 | -263 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 976 | 1240 | 1240 | -264 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 976 | 1240 | 1240 | -264 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1191 | 1517 | 1517 | -326 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 973 | 1240 | 1240 | -267 | 78 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 972 | 1240 | 1240 | -268 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 968 | 1240 | 1240 | -272 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 | 1240 | 1240 | -273 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 | 1240 | 1240 | -273 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 963 | 1240 | 1240 | -277 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 963 | 1240 | 1240 | -277 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 962 | 1240 | 1240 | -278 | 78 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 959 | 1240 | 1240 | -281 | 77 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1171 | 1517 | 1517 | -346 | 77 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1160 | 1517 | 1517 | -357 | 76 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1159 | 1517 | 1517 | -358 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1157 | 1517 | 1517 | -360 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1156 | 1517 | 1517 | -361 | 76 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1151 | 1517 | 1517 | -366 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1151 | 1517 | 1517 | -366 | 76 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1149 | 1517 | 1517 | -368 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1147 | 1517 | 1517 | -370 | 76 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1144 | 1517 | 1517 | -373 | 75 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1144 | 1517 | 1517 | -373 | 75 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1141 | 1517 | 1517 | -376 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1140 | 1517 | 1517 | -377 | 75 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1140 | 1517 | 1517 | -377 | 75 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1139 | 1517 | 1517 | -378 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 930 | 1240 | 1240 | -310 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1138 | 1517 | 1517 | -379 | 75 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1319 | 1760 | 1760 | -441 | 75 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1136 | 1517 | 1517 | -381 | 75 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1131 | 1517 | 1517 | -386 | 75 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 920 | 1240 | 1240 | -320 | 74 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1118 | 1517 | 1517 | -399 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 908 | 1240 | 1240 | -332 | 73 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1104 | 1517 | 1517 | -413 | 73 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1272 | 1760 | 1760 | -488 | 72 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1083 | 1517 | 1517 | -434 | 71 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1068 | 1517 | 1517 | -449 | 70 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1065 | 1517 | 1517 | -452 | 70 | []

## 1830Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2239
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 |  | 1240 | 0 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1173 |  | 1240 | -67 | 95 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Filesti [OPP] [RO] | RLAC212 _RFILE22 _1:line | 651 |  | 690 | -39 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1157 |  | 1240 | -83 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1152 |  | 1240 | -88 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1125 |  | 1240 | -115 | 91 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1372 |  | 1517 | -145 | 90 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1078 |  | 1240 | -162 | 87 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1310 |  | 1517 | -207 | 86 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1300 |  | 1517 | -217 | 86 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1053 |  | 1240 | -187 | 85 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1288 |  | 1517 | -229 | 85 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1277 |  | 1517 | -240 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1021 |  | 1240 | -219 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 567 |  | 690 | -123 | 82 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1241 |  | 1517 | -276 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1013 |  | 1240 | -227 | 82 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 613 |  | 750 | -137 | 82 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1011 |  | 1240 | -229 | 82 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 |  | 1517 | -282 | 81 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 |  | 1517 | -282 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 997 |  | 1240 | -243 | 80 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 995 |  | 1240 | -245 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1215 |  | 1517 | -302 | 80 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1215 |  | 1517 | -302 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1214 |  | 1517 | -303 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 989 |  | 1240 | -251 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 987 |  | 1240 | -253 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 |  | 1240 | -256 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 |  | 1240 | -256 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 983 |  | 1240 | -257 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -982 |  | 1240 | -258 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1200 |  | 1517 | -317 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 978 |  | 1240 | -262 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 |  | 1240 | -263 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 976 |  | 1240 | -264 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 976 |  | 1240 | -264 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1191 |  | 1517 | -326 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 973 |  | 1240 | -267 | 78 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 972 |  | 1240 | -268 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 968 |  | 1240 | -272 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 |  | 1240 | -273 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 |  | 1240 | -273 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 963 |  | 1240 | -277 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 963 |  | 1240 | -277 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 962 |  | 1240 | -278 | 78 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 959 |  | 1240 | -281 | 77 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1171 |  | 1517 | -346 | 77 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1160 |  | 1517 | -357 | 76 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1159 |  | 1517 | -358 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1157 |  | 1517 | -360 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1156 |  | 1517 | -361 | 76 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1151 |  | 1517 | -366 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1151 |  | 1517 | -366 | 76 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1149 |  | 1517 | -368 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1147 |  | 1517 | -370 | 76 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1144 |  | 1517 | -373 | 75 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1144 |  | 1517 | -373 | 75 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1141 |  | 1517 | -376 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1140 |  | 1517 | -377 | 75 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1140 |  | 1517 | -377 | 75 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1139 |  | 1517 | -378 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 930 |  | 1240 | -310 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1138 |  | 1517 | -379 | 75 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1319 |  | 1760 | -441 | 75 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1136 |  | 1517 | -381 | 75 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1131 |  | 1517 | -386 | 75 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 920 |  | 1240 | -320 | 74 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1118 |  | 1517 | -399 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 908 |  | 1240 | -332 | 73 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1104 |  | 1517 | -413 | 73 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1272 |  | 1760 | -488 | 72 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1083 |  | 1517 | -434 | 71 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1068 |  | 1517 | -449 | 70 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1065 |  | 1517 | -452 | 70 | []

## 1930Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2201
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1236 | 1240 | 1240 | -4 | 100 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1153 | 1240 | 1240 | -87 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1152 | 1240 | 1240 | -88 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1137 | 1240 | 1240 | -103 | 92 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1125 | 1240 | 1240 | -115 | 91 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1375 | 1517 | 1517 | -142 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1072 | 1240 | 1240 | -168 | 86 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1047 | 1240 | 1240 | -193 | 84 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1279 | 1517 | 1517 | -238 | 84 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 | 1517 | 1517 | -254 | 83 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1251 | 1517 | 1517 | -266 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1016 | 1240 | 1240 | -224 | 82 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1243 | 1517 | 1517 | -274 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1006 | 1240 | 1240 | -234 | 81 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1223 | 1517 | 1517 | -294 | 81 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 | 1517 | 1517 | -296 | 81 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 | 1517 | 1517 | -296 | 80 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 994 | 1240 | 1240 | -246 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -994 | 1240 | 1240 | -246 | 80 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 993 | 1240 | 1240 | -247 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 989 | 1240 | 1240 | -251 | 80 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1207 | 1517 | 1517 | -310 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1206 | 1517 | 1517 | -311 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 985 | 1240 | 1240 | -255 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 | 1240 | 1240 | -256 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 979 | 1240 | 1240 | -261 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 | 1240 | 1240 | -263 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 975 | 1240 | 1240 | -265 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -975 | 1240 | 1240 | -265 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 974 | 1240 | 1240 | -266 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 974 | 1240 | 1240 | -266 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 971 | 1240 | 1240 | -269 | 78 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 | 1240 | 1240 | -270 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 969 | 1240 | 1240 | -271 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 969 | 1240 | 1240 | -271 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1184 | 1517 | 1517 | -333 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 965 | 1240 | 1240 | -275 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 962 | 1240 | 1240 | -278 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 960 | 1240 | 1240 | -280 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1174 | 1517 | 1517 | -343 | 77 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 959 | 1240 | 1240 | -281 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 959 | 1240 | 1240 | -281 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -950 | 1240 | 1240 | -290 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1161 | 1517 | 1517 | -356 | 77 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1158 | 1517 | 1517 | -359 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1146 | 1517 | 1517 | -371 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 937 | 1240 | 1240 | -303 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1146 | 1517 | 1517 | -371 | 76 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1145 | 1517 | 1517 | -372 | 75 | []
RO_CO_00031 | N-1 Resita-Timisoara c2 | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 566 | 750 | 750 | -184 | 75 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1141 | 1517 | 1517 | -376 | 75 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1137 | 1517 | 1517 | -380 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1137 | 1517 | 1517 | -380 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1136 | 1517 | 1517 | -381 | 75 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1135 | 1517 | 1517 | -382 | 75 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1132 | 1517 | 1517 | -385 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 924 | 1240 | 1240 | -316 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1130 | 1517 | 1517 | -387 | 75 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1129 | 1517 | 1517 | -388 | 74 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1128 | 1517 | 1517 | -389 | 74 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1127 | 1517 | 1517 | -390 | 74 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1127 | 1517 | 1517 | -390 | 74 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1125 | 1517 | 1517 | -392 | 74 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1125 | 1517 | 1517 | -392 | 74 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1121 | 1517 | 1517 | -396 | 74 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 550 | 750 | 750 | -200 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -905 | 1240 | 1240 | -335 | 73 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1105 | 1517 | 1517 | -412 | 73 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1361 | 1888 | 1888 | -527 | 72 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1084 | 1517 | 1517 | -433 | 71 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RO] Baru Mare - Hasdat [DIR] [RO] | RBARU22 _RHAS122 _1:line | 529 | 750 | 750 | -221 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2201
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1236 |  | 1240 | -4 | 100 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1153 |  | 1240 | -87 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1152 |  | 1240 | -88 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1137 |  | 1240 | -103 | 92 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1125 |  | 1240 | -115 | 91 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1375 |  | 1517 | -142 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1072 |  | 1240 | -168 | 86 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1047 |  | 1240 | -193 | 84 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1279 |  | 1517 | -238 | 84 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 |  | 1517 | -254 | 83 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1251 |  | 1517 | -266 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1016 |  | 1240 | -224 | 82 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1243 |  | 1517 | -274 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1006 |  | 1240 | -234 | 81 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1223 |  | 1517 | -294 | 81 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 |  | 1517 | -296 | 81 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 |  | 1517 | -296 | 80 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 994 |  | 1240 | -246 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -994 |  | 1240 | -246 | 80 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 993 |  | 1240 | -247 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 989 |  | 1240 | -251 | 80 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1207 |  | 1517 | -310 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1206 |  | 1517 | -311 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 985 |  | 1240 | -255 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 |  | 1240 | -256 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 979 |  | 1240 | -261 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 |  | 1240 | -263 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 975 |  | 1240 | -265 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -975 |  | 1240 | -265 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 974 |  | 1240 | -266 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 974 |  | 1240 | -266 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 971 |  | 1240 | -269 | 78 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 |  | 1240 | -270 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 969 |  | 1240 | -271 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 969 |  | 1240 | -271 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1184 |  | 1517 | -333 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 965 |  | 1240 | -275 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 962 |  | 1240 | -278 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 960 |  | 1240 | -280 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1174 |  | 1517 | -343 | 77 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 959 |  | 1240 | -281 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 959 |  | 1240 | -281 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -950 |  | 1240 | -290 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1161 |  | 1517 | -356 | 77 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1158 |  | 1517 | -359 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1146 |  | 1517 | -371 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 937 |  | 1240 | -303 | 76 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1146 |  | 1517 | -371 | 76 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1145 |  | 1517 | -372 | 75 | []
RO_CO_00031 | N-1 Resita-Timisoara c2 | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 566 |  | 750 | -184 | 75 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1141 |  | 1517 | -376 | 75 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1137 |  | 1517 | -380 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1137 |  | 1517 | -380 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1136 |  | 1517 | -381 | 75 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1135 |  | 1517 | -382 | 75 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1132 |  | 1517 | -385 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 924 |  | 1240 | -316 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1130 |  | 1517 | -387 | 75 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1129 |  | 1517 | -388 | 74 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1128 |  | 1517 | -389 | 74 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1127 |  | 1517 | -390 | 74 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1127 |  | 1517 | -390 | 74 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1125 |  | 1517 | -392 | 74 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1125 |  | 1517 | -392 | 74 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1121 |  | 1517 | -396 | 74 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 550 |  | 750 | -200 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -905 |  | 1240 | -335 | 73 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1105 |  | 1517 | -412 | 73 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1361 |  | 1888 | -527 | 72 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1084 |  | 1517 | -433 | 71 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RO] Baru Mare - Hasdat [DIR] [RO] | RBARU22 _RHAS122 _1:line | 529 |  | 750 | -221 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2244
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 | 1240 | 1240 | -6 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1160 | 1240 | 1240 | -80 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1155 | 1240 | 1240 | -85 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1146 | 1240 | 1240 | -94 | 92 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1144 | 1240 | 1240 | -96 | 92 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1325 | 1517 | 1517 | -192 | 87 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1079 | 1240 | 1240 | -161 | 87 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1076 | 1240 | 1240 | -164 | 87 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1039 | 1240 | 1240 | -201 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1033 | 1240 | 1240 | -207 | 83 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1251 | 1517 | 1517 | -266 | 82 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 | 1517 | 1517 | -282 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1000 | 1240 | 1240 | -240 | 81 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1222 | 1517 | 1517 | -295 | 81 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 999 | 1240 | 1240 | -241 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 995 | 1240 | 1240 | -245 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 992 | 1240 | 1240 | -248 | 80 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1211 | 1517 | 1517 | -306 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 988 | 1240 | 1240 | -252 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 | 1240 | 1240 | -256 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 | 1240 | 1240 | -256 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 980 | 1240 | 1240 | -260 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 980 | 1240 | 1240 | -260 | 79 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1196 | 1517 | 1517 | -321 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 | 1240 | 1240 | -263 | 79 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 | 1240 | 1240 | -263 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 | 1240 | 1240 | -263 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 975 | 1240 | 1240 | -265 | 79 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1192 | 1517 | 1517 | -325 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1191 | 1517 | 1517 | -326 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -973 | 1240 | 1240 | -267 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 972 | 1240 | 1240 | -268 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 972 | 1240 | 1240 | -268 | 78 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -970 | 1240 | 1240 | -270 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 969 | 1240 | 1240 | -271 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 | 1240 | 1240 | -273 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 | 1240 | 1240 | -273 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 963 | 1240 | 1240 | -277 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1170 | 1517 | 1517 | -347 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1169 | 1517 | 1517 | -348 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 948 | 1240 | 1240 | -292 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -941 | 1240 | 1240 | -299 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1150 | 1517 | 1517 | -367 | 76 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 934 | 1240 | 1240 | -306 | 75 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1139 | 1517 | 1517 | -378 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1131 | 1517 | 1517 | -386 | 75 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1131 | 1517 | 1517 | -386 | 75 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1122 | 1517 | 1517 | -395 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -914 | 1240 | 1240 | -326 | 74 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1117 | 1517 | 1517 | -400 | 74 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 | 1517 | 1517 | -403 | 73 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 | 1517 | 1517 | -403 | 73 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1112 | 1517 | 1517 | -405 | 73 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1111 | 1517 | 1517 | -406 | 73 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1110 | 1517 | 1517 | -407 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1108 | 1517 | 1517 | -409 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1107 | 1517 | 1517 | -410 | 73 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1103 | 1517 | 1517 | -414 | 73 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1103 | 1517 | 1517 | -414 | 73 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1100 | 1517 | 1517 | -417 | 72 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1099 | 1517 | 1517 | -418 | 72 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1098 | 1517 | 1517 | -419 | 72 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1098 | 1517 | 1517 | -419 | 72 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1098 | 1517 | 1517 | -419 | 72 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1097 | 1517 | 1517 | -420 | 72 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1076 | 1517 | 1517 | -441 | 71 | []
RO_CO_00031 | N-1 Resita-Timisoara c2 | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | -530 | -750 | -750 | -220 | 71 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1063 | 1517 | 1517 | -454 | 70 | []

## 2030Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2244
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 |  | 1240 | -6 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1160 |  | 1240 | -80 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1155 |  | 1240 | -85 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1146 |  | 1240 | -94 | 92 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1144 |  | 1240 | -96 | 92 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1325 |  | 1517 | -192 | 87 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1079 |  | 1240 | -161 | 87 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1076 |  | 1240 | -164 | 87 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1039 |  | 1240 | -201 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1033 |  | 1240 | -207 | 83 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1251 |  | 1517 | -266 | 82 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 |  | 1517 | -282 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1000 |  | 1240 | -240 | 81 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1222 |  | 1517 | -295 | 81 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 999 |  | 1240 | -241 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 995 |  | 1240 | -245 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 992 |  | 1240 | -248 | 80 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1211 |  | 1517 | -306 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 988 |  | 1240 | -252 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 |  | 1240 | -256 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 |  | 1240 | -256 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 980 |  | 1240 | -260 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 980 |  | 1240 | -260 | 79 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1196 |  | 1517 | -321 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 |  | 1240 | -263 | 79 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 |  | 1240 | -263 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 |  | 1240 | -263 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 975 |  | 1240 | -265 | 79 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1192 |  | 1517 | -325 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1191 |  | 1517 | -326 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -973 |  | 1240 | -267 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 972 |  | 1240 | -268 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 972 |  | 1240 | -268 | 78 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -970 |  | 1240 | -270 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 969 |  | 1240 | -271 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 |  | 1240 | -273 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 |  | 1240 | -273 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 963 |  | 1240 | -277 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1170 |  | 1517 | -347 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1169 |  | 1517 | -348 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 948 |  | 1240 | -292 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -941 |  | 1240 | -299 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1150 |  | 1517 | -367 | 76 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 934 |  | 1240 | -306 | 75 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1139 |  | 1517 | -378 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1131 |  | 1517 | -386 | 75 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1131 |  | 1517 | -386 | 75 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1122 |  | 1517 | -395 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -914 |  | 1240 | -326 | 74 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1117 |  | 1517 | -400 | 74 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 |  | 1517 | -403 | 73 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 |  | 1517 | -403 | 73 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1112 |  | 1517 | -405 | 73 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1111 |  | 1517 | -406 | 73 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1110 |  | 1517 | -407 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1108 |  | 1517 | -409 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1107 |  | 1517 | -410 | 73 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1103 |  | 1517 | -414 | 73 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1103 |  | 1517 | -414 | 73 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1100 |  | 1517 | -417 | 72 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1099 |  | 1517 | -418 | 72 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1098 |  | 1517 | -419 | 72 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1098 |  | 1517 | -419 | 72 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1098 |  | 1517 | -419 | 72 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1097 |  | 1517 | -420 | 72 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1076 |  | 1517 | -441 | 71 | []
RO_CO_00031 | N-1 Resita-Timisoara c2 | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | -530 |  | -750 | -220 | 71 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1063 |  | 1517 | -454 | 70 | []

## 2130Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2216
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 | 1240 | 1240 | -6 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1165 | 1240 | 1240 | -75 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1154 | 1240 | 1240 | -86 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1150 | 1240 | 1240 | -90 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1144 | 1240 | 1240 | -96 | 92 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1325 | 1517 | 1517 | -192 | 87 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1077 | 1240 | 1240 | -163 | 87 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1061 | 1240 | 1240 | -179 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1026 | 1240 | 1240 | -214 | 83 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1254 | 1517 | 1517 | -263 | 83 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1018 | 1240 | 1240 | -222 | 82 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 | 1517 | 1517 | -277 | 82 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1227 | 1517 | 1517 | -290 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1001 | 1240 | 1240 | -239 | 81 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 999 | 1240 | 1240 | -241 | 81 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 995 | 1240 | 1240 | -245 | 80 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1216 | 1517 | 1517 | -301 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 990 | 1240 | 1240 | -250 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 989 | 1240 | 1240 | -251 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 988 | 1240 | 1240 | -252 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -987 | 1240 | 1240 | -253 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 | 1240 | 1240 | -256 | 79 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1200 | 1517 | 1517 | -317 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 981 | 1240 | 1240 | -259 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 980 | 1240 | 1240 | -260 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 978 | 1240 | 1240 | -262 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 978 | 1240 | 1240 | -262 | 79 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 | 1240 | 1240 | -263 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -976 | 1240 | 1240 | -264 | 79 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1192 | 1517 | 1517 | -325 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1192 | 1517 | 1517 | -325 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 974 | 1240 | 1240 | -266 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 972 | 1240 | 1240 | -268 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 969 | 1240 | 1240 | -271 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 969 | 1240 | 1240 | -271 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 | 1240 | 1240 | -273 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 966 | 1240 | 1240 | -274 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 963 | 1240 | 1240 | -277 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1172 | 1517 | 1517 | -345 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1171 | 1517 | 1517 | -346 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -949 | 1240 | 1240 | -291 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 945 | 1240 | 1240 | -295 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1148 | 1517 | 1517 | -369 | 76 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 934 | 1240 | 1240 | -306 | 75 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1142 | 1517 | 1517 | -375 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1133 | 1517 | 1517 | -384 | 75 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1131 | 1517 | 1517 | -386 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -916 | 1240 | 1240 | -324 | 74 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1120 | 1517 | 1517 | -397 | 74 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1118 | 1517 | 1517 | -399 | 74 | []
RO_CO_00031 | N-1 Resita-Timisoara c2 | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 552 | 750 | 750 | -198 | 74 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1113 | 1517 | 1517 | -404 | 73 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1111 | 1517 | 1517 | -406 | 73 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1110 | 1517 | 1517 | -407 | 73 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1109 | 1517 | 1517 | -408 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1109 | 1517 | 1517 | -408 | 73 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1107 | 1517 | 1517 | -410 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1104 | 1517 | 1517 | -413 | 73 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1103 | 1517 | 1517 | -414 | 73 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1100 | 1517 | 1517 | -417 | 73 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1100 | 1517 | 1517 | -417 | 72 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1098 | 1517 | 1517 | -419 | 72 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1097 | 1517 | 1517 | -420 | 72 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1097 | 1517 | 1517 | -420 | 72 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1096 | 1517 | 1517 | -421 | 72 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1094 | 1517 | 1517 | -423 | 72 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1076 | 1517 | 1517 | -441 | 71 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 531 | 750 | 750 | -219 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2216
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 |  | 1240 | -6 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1165 |  | 1240 | -75 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1154 |  | 1240 | -86 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1150 |  | 1240 | -90 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1144 |  | 1240 | -96 | 92 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1325 |  | 1517 | -192 | 87 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1077 |  | 1240 | -163 | 87 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1061 |  | 1240 | -179 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1026 |  | 1240 | -214 | 83 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1254 |  | 1517 | -263 | 83 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1018 |  | 1240 | -222 | 82 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 |  | 1517 | -277 | 82 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1227 |  | 1517 | -290 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1001 |  | 1240 | -239 | 81 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 999 |  | 1240 | -241 | 81 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 995 |  | 1240 | -245 | 80 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1216 |  | 1517 | -301 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 990 |  | 1240 | -250 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 989 |  | 1240 | -251 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 988 |  | 1240 | -252 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -987 |  | 1240 | -253 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 984 |  | 1240 | -256 | 79 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1200 |  | 1517 | -317 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 981 |  | 1240 | -259 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 980 |  | 1240 | -260 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 978 |  | 1240 | -262 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 978 |  | 1240 | -262 | 79 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 |  | 1240 | -263 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -976 |  | 1240 | -264 | 79 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1192 |  | 1517 | -325 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1192 |  | 1517 | -325 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 974 |  | 1240 | -266 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 972 |  | 1240 | -268 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 969 |  | 1240 | -271 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 969 |  | 1240 | -271 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 |  | 1240 | -273 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 966 |  | 1240 | -274 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 963 |  | 1240 | -277 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1172 |  | 1517 | -345 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1171 |  | 1517 | -346 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -949 |  | 1240 | -291 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 945 |  | 1240 | -295 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1148 |  | 1517 | -369 | 76 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 934 |  | 1240 | -306 | 75 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1142 |  | 1517 | -375 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1133 |  | 1517 | -384 | 75 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1131 |  | 1517 | -386 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -916 |  | 1240 | -324 | 74 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1120 |  | 1517 | -397 | 74 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1118 |  | 1517 | -399 | 74 | []
RO_CO_00031 | N-1 Resita-Timisoara c2 | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 552 |  | 750 | -198 | 74 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1113 |  | 1517 | -404 | 73 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1111 |  | 1517 | -406 | 73 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1110 |  | 1517 | -407 | 73 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1109 |  | 1517 | -408 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1109 |  | 1517 | -408 | 73 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1107 |  | 1517 | -410 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1104 |  | 1517 | -413 | 73 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1103 |  | 1517 | -414 | 73 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1100 |  | 1517 | -417 | 73 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1100 |  | 1517 | -417 | 72 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1098 |  | 1517 | -419 | 72 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1097 |  | 1517 | -420 | 72 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1097 |  | 1517 | -420 | 72 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1096 |  | 1517 | -421 | 72 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1094 |  | 1517 | -423 | 72 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1076 |  | 1517 | -441 | 71 | []
RO_CO_00030 | N-1 Portile de Fier-Resita c2 | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 531 |  | 750 | -219 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2214
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1236 | 1240 | 1240 | -4 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1160 | 1240 | 1240 | -80 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1153 | 1240 | 1240 | -87 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1148 | 1240 | 1240 | -92 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1138 | 1240 | 1240 | -102 | 92 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1370 | 1517 | 1517 | -147 | 90 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1076 | 1240 | 1240 | -164 | 87 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1042 | 1240 | 1240 | -198 | 84 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1270 | 1517 | 1517 | -247 | 84 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1259 | 1517 | 1517 | -258 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1017 | 1240 | 1240 | -223 | 82 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1243 | 1517 | 1517 | -274 | 82 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 | 1517 | 1517 | -282 | 81 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1005 | 1240 | 1240 | -235 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1000 | 1240 | 1240 | -240 | 81 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 | 1517 | 1517 | -296 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 997 | 1240 | 1240 | -243 | 80 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 995 | 1240 | 1240 | -245 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 990 | 1240 | 1240 | -250 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 990 | 1240 | 1240 | -250 | 80 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 | 1517 | 1517 | -308 | 80 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 | 1517 | 1517 | -308 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -985 | 1240 | 1240 | -255 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 980 | 1240 | 1240 | -260 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 | 1240 | 1240 | -263 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 | 1240 | 1240 | -263 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 976 | 1240 | 1240 | -264 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 976 | 1240 | 1240 | -264 | 79 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1194 | 1517 | 1517 | -323 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1193 | 1517 | 1517 | -324 | 79 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 973 | 1240 | 1240 | -267 | 78 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -972 | 1240 | 1240 | -268 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 971 | 1240 | 1240 | -269 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 | 1240 | 1240 | -270 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 | 1240 | 1240 | -273 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 966 | 1240 | 1240 | -274 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 964 | 1240 | 1240 | -276 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 962 | 1240 | 1240 | -278 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 961 | 1240 | 1240 | -279 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 958 | 1240 | 1240 | -282 | 77 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1161 | 1517 | 1517 | -356 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 947 | 1240 | 1240 | -293 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1157 | 1517 | 1517 | -360 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 943 | 1240 | 1240 | -297 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1152 | 1517 | 1517 | -365 | 76 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1147 | 1517 | 1517 | -370 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1140 | 1517 | 1517 | -377 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 924 | 1240 | 1240 | -316 | 75 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1130 | 1517 | 1517 | -387 | 75 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1129 | 1517 | 1517 | -388 | 74 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1126 | 1517 | 1517 | -391 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1126 | 1517 | 1517 | -391 | 74 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1124 | 1517 | 1517 | -393 | 74 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1121 | 1517 | 1517 | -396 | 74 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1121 | 1517 | 1517 | -396 | 74 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1120 | 1517 | 1517 | -397 | 74 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1118 | 1517 | 1517 | -399 | 74 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1117 | 1517 | 1517 | -400 | 74 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 | 1517 | 1517 | -403 | 73 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 | 1517 | 1517 | -403 | 73 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 | 1517 | 1517 | -403 | 73 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 | 1517 | 1517 | -403 | 73 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1386 | 1888 | 1888 | -502 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 910 | 1240 | 1240 | -330 | 73 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1112 | 1517 | 1517 | -405 | 73 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1110 | 1517 | 1517 | -407 | 73 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1092 | 1517 | 1517 | -425 | 72 | []

## 2230Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2214
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1236 |  | 1240 | -4 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1160 |  | 1240 | -80 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1153 |  | 1240 | -87 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1148 |  | 1240 | -92 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1138 |  | 1240 | -102 | 92 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1370 |  | 1517 | -147 | 90 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1076 |  | 1240 | -164 | 87 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1042 |  | 1240 | -198 | 84 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1270 |  | 1517 | -247 | 84 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1259 |  | 1517 | -258 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1017 |  | 1240 | -223 | 82 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1243 |  | 1517 | -274 | 82 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1235 |  | 1517 | -282 | 81 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1005 |  | 1240 | -235 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1000 |  | 1240 | -240 | 81 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1221 |  | 1517 | -296 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 997 |  | 1240 | -243 | 80 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 995 |  | 1240 | -245 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 990 |  | 1240 | -250 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 990 |  | 1240 | -250 | 80 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 |  | 1517 | -308 | 80 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 |  | 1517 | -308 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -985 |  | 1240 | -255 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 980 |  | 1240 | -260 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 |  | 1240 | -263 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 977 |  | 1240 | -263 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 976 |  | 1240 | -264 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 976 |  | 1240 | -264 | 79 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1194 |  | 1517 | -323 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1193 |  | 1517 | -324 | 79 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 973 |  | 1240 | -267 | 78 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -972 |  | 1240 | -268 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 971 |  | 1240 | -269 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 970 |  | 1240 | -270 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 967 |  | 1240 | -273 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 966 |  | 1240 | -274 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 964 |  | 1240 | -276 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 962 |  | 1240 | -278 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 961 |  | 1240 | -279 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 958 |  | 1240 | -282 | 77 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1161 |  | 1517 | -356 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 947 |  | 1240 | -293 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1157 |  | 1517 | -360 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 943 |  | 1240 | -297 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1152 |  | 1517 | -365 | 76 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1147 |  | 1517 | -370 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1140 |  | 1517 | -377 | 75 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 924 |  | 1240 | -316 | 75 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1130 |  | 1517 | -387 | 75 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1129 |  | 1517 | -388 | 74 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1126 |  | 1517 | -391 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1126 |  | 1517 | -391 | 74 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1124 |  | 1517 | -393 | 74 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1121 |  | 1517 | -396 | 74 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1121 |  | 1517 | -396 | 74 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1120 |  | 1517 | -397 | 74 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1118 |  | 1517 | -399 | 74 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1117 |  | 1517 | -400 | 74 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 |  | 1517 | -403 | 73 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 |  | 1517 | -403 | 73 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 |  | 1517 | -403 | 73 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1114 |  | 1517 | -403 | 73 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1386 |  | 1888 | -502 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 910 |  | 1240 | -330 | 73 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1112 |  | 1517 | -405 | 73 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1110 |  | 1517 | -407 | 73 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1092 |  | 1517 | -425 | 72 | []

## 2330Preventive
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2171
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1512 | 1517 | 1517 | -5 | 100 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1187 | 1240 | 1240 | -53 | 96 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1395 | 1517 | 1517 | -122 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1378 | 1517 | 1517 | -139 | 91 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1370 | 1517 | 1517 | -147 | 90 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1363 | 1517 | 1517 | -154 | 90 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1348 | 1517 | 1517 | -169 | 89 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1095 | 1240 | 1240 | -145 | 88 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1091 | 1240 | 1240 | -149 | 88 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1322 | 1517 | 1517 | -195 | 87 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1321 | 1517 | 1517 | -196 | 87 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1319 | 1517 | 1517 | -198 | 87 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1319 | 1517 | 1517 | -198 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1073 | 1240 | 1240 | -167 | 87 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1280 | 1517 | 1517 | -237 | 84 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1277 | 1517 | 1517 | -240 | 84 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1272 | 1517 | 1517 | -245 | 84 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 | 1517 | 1517 | -254 | 83 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1030 | 1240 | 1240 | -210 | 83 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1259 | 1517 | 1517 | -258 | 83 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1246 | 1517 | 1517 | -271 | 82 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1244 | 1517 | 1517 | -273 | 82 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1243 | 1517 | 1517 | -274 | 82 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1241 | 1517 | 1517 | -276 | 82 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -674 | 824 | 824 | -150 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 | 1517 | 1517 | -277 | 82 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1239 | 1517 | 1517 | -278 | 82 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1239 | 1517 | 1517 | -278 | 82 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1236 | 1517 | 1517 | -281 | 81 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1234 | 1517 | 1517 | -283 | 81 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1233 | 1517 | 1517 | -284 | 81 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1233 | 1517 | 1517 | -284 | 81 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1232 | 1517 | 1517 | -285 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1231 | 1517 | 1517 | -286 | 81 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1230 | 1517 | 1517 | -287 | 81 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1229 | 1517 | 1517 | -288 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1004 | 1240 | 1240 | -236 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1228 | 1517 | 1517 | -289 | 81 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1524 | 1888 | 1888 | -364 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 | 1517 | 1517 | -308 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1177 | 1517 | 1517 | -340 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1154 | 1517 | 1517 | -363 | 76 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 938 | 1240 | 1240 | -302 | 76 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1145 | 1517 | 1517 | -372 | 75 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 932 | 1240 | 1240 | -308 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1136 | 1517 | 1517 | -381 | 75 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1130 | 1517 | 1517 | -387 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 924 | 1240 | 1240 | -316 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | -1130 | 1517 | 1517 | -387 | 74 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 920 | 1240 | 1240 | -320 | 74 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 918 | 1240 | 1240 | -322 | 74 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 915 | 1240 | 1240 | -325 | 74 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1295 | 1760 | 1760 | -465 | 74 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 911 | 1240 | 1240 | -329 | 73 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -910 | 1240 | 1240 | -330 | 73 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 904 | 1240 | 1240 | -336 | 73 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 903 | 1240 | 1240 | -337 | 73 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -900 | 1240 | 1240 | -340 | 73 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 900 | 1240 | 1240 | -340 | 73 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 899 | 1240 | 1240 | -341 | 73 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 899 | 1240 | 1240 | -341 | 73 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 898 | 1240 | 1240 | -342 | 72 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 896 | 1240 | 1240 | -344 | 72 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 894 | 1240 | 1240 | -346 | 72 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 893 | 1240 | 1240 | -347 | 72 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 890 | 1240 | 1240 | -350 | 72 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 890 | 1240 | 1240 | -350 | 72 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1260 | 1760 | 1760 | -500 | 72 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 885 | 1240 | 1240 | -355 | 71 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 883 | 1240 | 1240 | -357 | 71 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 883 | 1240 | 1240 | -357 | 71 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 881 | 1240 | 1240 | -359 | 71 | []

## 2330Curative
Detailed results
Generated at: | 2022-07-23 21:41
Business day: | 25.07.2022
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2171
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1512 |  | 1517 | -5 | 100 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1187 |  | 1240 | -53 | 96 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1395 |  | 1517 | -122 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1378 |  | 1517 | -139 | 91 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1370 |  | 1517 | -147 | 90 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1363 |  | 1517 | -154 | 90 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1348 |  | 1517 | -169 | 89 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1095 |  | 1240 | -145 | 88 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1091 |  | 1240 | -149 | 88 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1322 |  | 1517 | -195 | 87 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1321 |  | 1517 | -196 | 87 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1319 |  | 1517 | -198 | 87 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1319 |  | 1517 | -198 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1073 |  | 1240 | -167 | 87 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1280 |  | 1517 | -237 | 84 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1277 |  | 1517 | -240 | 84 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1272 |  | 1517 | -245 | 84 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1263 |  | 1517 | -254 | 83 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1030 |  | 1240 | -210 | 83 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1259 |  | 1517 | -258 | 83 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1246 |  | 1517 | -271 | 82 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1244 |  | 1517 | -273 | 82 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1243 |  | 1517 | -274 | 82 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1241 |  | 1517 | -276 | 82 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -674 |  | 824 | -150 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1240 |  | 1517 | -277 | 82 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1239 |  | 1517 | -278 | 82 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1239 |  | 1517 | -278 | 82 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1236 |  | 1517 | -281 | 81 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1234 |  | 1517 | -283 | 81 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1233 |  | 1517 | -284 | 81 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1233 |  | 1517 | -284 | 81 | []
BC | Base Case | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1232 |  | 1517 | -285 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1231 |  | 1517 | -286 | 81 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1230 |  | 1517 | -287 | 81 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1229 |  | 1517 | -288 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1004 |  | 1240 | -236 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1228 |  | 1517 | -289 | 81 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1524 |  | 1888 | -364 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1209 |  | 1517 | -308 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1177 |  | 1517 | -340 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1154 |  | 1517 | -363 | 76 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 938 |  | 1240 | -302 | 76 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1145 |  | 1517 | -372 | 75 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 932 |  | 1240 | -308 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1136 |  | 1517 | -381 | 75 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1130 |  | 1517 | -387 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 924 |  | 1240 | -316 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | -1130 |  | 1517 | -387 | 74 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 920 |  | 1240 | -320 | 74 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 918 |  | 1240 | -322 | 74 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 915 |  | 1240 | -325 | 74 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1295 |  | 1760 | -465 | 74 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 911 |  | 1240 | -329 | 73 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -910 |  | 1240 | -330 | 73 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 904 |  | 1240 | -336 | 73 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 903 |  | 1240 | -337 | 73 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -900 |  | 1240 | -340 | 73 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 900 |  | 1240 | -340 | 73 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 899 |  | 1240 | -341 | 73 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 899 |  | 1240 | -341 | 73 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 898 |  | 1240 | -342 | 72 | []
BG_CO_00003, BG_CO_00012 | N-1 400kV Varna - Burgas, Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 896 |  | 1240 | -344 | 72 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 894 |  | 1240 | -346 | 72 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 893 |  | 1240 | -347 | 72 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 890 |  | 1240 | -350 | 72 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 890 |  | 1240 | -350 | 72 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1260 |  | 1760 | -500 | 72 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 885 |  | 1240 | -355 | 71 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Vetren - Chervena Mogila | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 883 |  | 1240 | -357 | 71 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 883 |  | 1240 | -357 | 71 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 881 |  | 1240 | -359 | 71 | []