## 0030Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 00:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2944
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 | 1601 | 1601 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1594 | 1601 | 1601 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1270 | -1500 | -1500 | -230 | 85 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1270 | -1500 | -1500 | -230 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1268 | 1601 | 1601 | -333 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1268 | 1601 | 1601 | -333 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | -1263 | -1600 | -1600 | -337 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | -1263 | -1600 | -1600 | -337 | 79 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1161 | -1500 | -1500 | -339 | 77 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1127 | -1500 | -1500 | -373 | 75 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1123 | -1500 | -1500 | -377 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1117 | -1500 | -1500 | -383 | 74 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1109 | -1500 | -1500 | -391 | 74 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1108 | -1500 | -1500 | -392 | 74 | []

## 0030Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 00:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2944
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 |  | 1601 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1594 |  | 1601 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1270 |  | -1500 | -230 | 85 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1270 |  | -1500 | -230 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1268 |  | 1601 | -333 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1268 |  | 1601 | -333 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | -1263 |  | -1600 | -337 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | -1263 |  | -1600 | -337 | 79 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1161 |  | -1500 | -339 | 77 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1127 |  | -1500 | -373 | 75 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1123 |  | -1500 | -377 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1117 |  | -1500 | -383 | 74 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1109 |  | -1500 | -391 | 74 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1108 |  | -1500 | -392 | 74 | []

## 0130Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 01:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2599
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1598 | 1601 | 1601 | -3 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1598 | 1601 | 1601 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1151 | 1601 | 1601 | -450 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1151 | 1601 | 1601 | -450 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | -1146 | -1600 | -1600 | -454 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | -1146 | -1600 | -1600 | -454 | 72 | []

## 0130Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 01:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2599
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1598 |  | 1601 | -3 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1598 |  | 1601 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1151 |  | 1601 | -450 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1151 |  | 1601 | -450 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | -1146 |  | -1600 | -454 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | -1146 |  | -1600 | -454 | 72 | []

## 0230Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 02:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2550
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 | 1601 | 1601 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1594 | 1601 | 1601 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1136 | 1601 | 1601 | -465 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1136 | 1601 | 1601 | -465 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | -1131 | -1600 | -1600 | -469 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | -1131 | -1600 | -1600 | -469 | 71 | []

## 0230Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 02:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2550
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 |  | 1601 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1594 |  | 1601 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1136 |  | 1601 | -465 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1136 |  | 1601 | -465 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | -1131 |  | -1600 | -469 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | -1131 |  | -1600 | -469 | 71 | []

## 0330Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 03:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2509
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 | 1601 | 1601 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1594 | 1601 | 1601 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1123 | 1601 | 1601 | -478 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1123 | 1601 | 1601 | -478 | 70 | []

## 0330Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 03:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2509
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 |  | 1601 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1594 |  | 1601 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1123 |  | 1601 | -478 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1123 |  | 1601 | -478 | 70 | []

## 0430Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 04:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2404
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1594 | 1601 | 1601 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 | 1601 | 1601 | -7 | 100 | []

## 0430Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 04:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2404
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | 1594 |  | 1601 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 |  | 1601 | -7 | 100 | []

## 0530Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 05:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2192
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1495 | -1500 | -1500 | -5 | 100 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1441 | -1500 | -1500 | -59 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1437 | -1500 | -1500 | -63 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1433 | -1500 | -1500 | -67 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1417 | -1500 | -1500 | -83 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1402 | -1500 | -1500 | -98 | 93 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1402 | -1500 | -1500 | -98 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1402 | -1500 | -1500 | -98 | 93 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1420 | 1600 | 1600 | -180 | 89 | []
RO-BG_CO_00004 | N-1 Stupina-Varna | [RO-RO] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1372 | 1600 | 1600 | -228 | 86 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1281 | -1500 | -1500 | -219 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -853 | -999 | -999 | -146 | 85 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1245 | -1500 | -1500 | -255 | 83 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gura Ialomitei - Bucuresti Sud [OPP] [RO] | RBUC141 _RGIAL21 _1:line | -1102 | -1500 | -1500 | -398 | 73 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Bucuresti Sud - Fundeni c2 [DIR] [RO] | RBUCU22 _RFUD222 _2:line | 548 | 750 | 750 | -202 | 73 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Bucuresti Sud - Fundeni c1 [OPP] [RO] | RBUCU22 _RFUD212 _1:line | 548 | 750 | 750 | -202 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Pelicanu [OPP] [RO] | RPELI41 _RCERN41 _1:line | -1092 | -1500 | -1500 | -408 | 73 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Stupina - Varna [DIR] [RO] | RSTUP41 _XVA_ST11_1:line | -1444 | -2000 | -2000 | -556 | 72 | []

## 0530Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 05:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2192
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1495 |  | -1500 | -5 | 100 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1441 |  | -1500 | -59 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1437 |  | -1500 | -63 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1433 |  | -1500 | -67 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1417 |  | -1500 | -83 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1402 |  | -1500 | -98 | 93 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1402 |  | -1500 | -98 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1402 |  | -1500 | -98 | 93 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1420 |  | 1600 | -180 | 89 | []
RO-BG_CO_00004 | N-1 Stupina-Varna | [RO-RO] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1372 |  | 1600 | -228 | 86 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1281 |  | -1500 | -219 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -853 |  | -999 | -146 | 85 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1245 |  | -1500 | -255 | 83 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gura Ialomitei - Bucuresti Sud [OPP] [RO] | RBUC141 _RGIAL21 _1:line | -1102 |  | -1500 | -398 | 73 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Bucuresti Sud - Fundeni c2 [DIR] [RO] | RBUCU22 _RFUD222 _2:line | 548 |  | 750 | -202 | 73 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Bucuresti Sud - Fundeni c1 [OPP] [RO] | RBUCU22 _RFUD212 _1:line | 548 |  | 750 | -202 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Pelicanu [OPP] [RO] | RPELI41 _RCERN41 _1:line | -1092 |  | -1500 | -408 | 73 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Stupina - Varna [DIR] [RO] | RSTUP41 _XVA_ST11_1:line | -1444 |  | -2000 | -556 | 72 | []

## 0630Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 06:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2173
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1499 | -1500 | -1500 | -1 | 100 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1446 | -1500 | -1500 | -54 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1439 | -1500 | -1500 | -61 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1427 | -1500 | -1500 | -73 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1426 | -1500 | -1500 | -74 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1418 | -1500 | -1500 | -82 | 95 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1418 | -1500 | -1500 | -82 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1418 | -1500 | -1500 | -82 | 95 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1432 | 1600 | 1600 | -168 | 90 | []
RO-BG_CO_00004 | N-1 Stupina-Varna | [RO-RO] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1367 | 1600 | 1600 | -233 | 85 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Bucuresti Sud - Fundeni c2 [DIR] [RO] | RBUCU22 _RFUD222 _2:line | 637 | 750 | 750 | -113 | 85 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Bucuresti Sud - Fundeni c1 [OPP] [RO] | RBUCU22 _RFUD212 _1:line | 637 | 750 | 750 | -113 | 85 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1236 | -1500 | -1500 | -264 | 82 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1204 | -1500 | -1500 | -296 | 80 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gura Ialomitei - Bucuresti Sud [OPP] [RO] | RBUC141 _RGIAL21 _1:line | -1100 | -1500 | -1500 | -400 | 73 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Smardan - Isaccea c1 [OPP] [RO] | RSMIR41 _RISAC41 _1:line | -1097 | -1500 | -1500 | -403 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Gutinas - Smardan [DIR] [RO] | RGUTI41 _RSMIR41 _1:line | -1093 | -1500 | -1500 | -407 | 73 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Stupina - Varna [OPP] [RO] | RSTUP41 _XVA_ST11_1:line | -1455 | -2000 | -2000 | -545 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Pelicanu [OPP] [RO] | RPELI41 _RCERN41 _1:line | -1088 | -1500 | -1500 | -412 | 73 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [DIR] [RO] | RGUTI41 _RSMIR41 _1:line | -1062 | -1500 | -1500 | -438 | 71 | []

## 0630Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 06:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2173
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1499 |  | -1500 | -1 | 100 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1446 |  | -1500 | -54 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1439 |  | -1500 | -61 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1427 |  | -1500 | -73 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1426 |  | -1500 | -74 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1418 |  | -1500 | -82 | 95 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1418 |  | -1500 | -82 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1418 |  | -1500 | -82 | 95 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1432 |  | 1600 | -168 | 90 | []
RO-BG_CO_00004 | N-1 Stupina-Varna | [RO-RO] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1367 |  | 1600 | -233 | 85 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Bucuresti Sud - Fundeni c2 [DIR] [RO] | RBUCU22 _RFUD222 _2:line | 637 |  | 750 | -113 | 85 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Bucuresti Sud - Fundeni c1 [OPP] [RO] | RBUCU22 _RFUD212 _1:line | 637 |  | 750 | -113 | 85 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1236 |  | -1500 | -264 | 82 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1204 |  | -1500 | -296 | 80 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gura Ialomitei - Bucuresti Sud [OPP] [RO] | RBUC141 _RGIAL21 _1:line | -1100 |  | -1500 | -400 | 73 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Smardan - Isaccea c1 [OPP] [RO] | RSMIR41 _RISAC41 _1:line | -1097 |  | -1500 | -403 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Gutinas - Smardan [DIR] [RO] | RGUTI41 _RSMIR41 _1:line | -1093 |  | -1500 | -407 | 73 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Stupina - Varna [OPP] [RO] | RSTUP41 _XVA_ST11_1:line | -1455 |  | -2000 | -545 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Pelicanu [OPP] [RO] | RPELI41 _RCERN41 _1:line | -1088 |  | -1500 | -412 | 73 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [DIR] [RO] | RGUTI41 _RSMIR41 _1:line | -1062 |  | -1500 | -438 | 71 | []

## 0730Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 07:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 491
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 689 | 690 | 690 | -1 | 100 | []

## 0730Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 07:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 491
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 689 |  | 690 | -1 | 100 | []

## 0830Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 08:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 415
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 687 | 690 | 690 | -3 | 99 | []

## 0830Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 08:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 415
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 687 |  | 690 | -3 | 99 | []

## 0930Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 09:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 528
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 687 | 690 | 690 | -3 | 100 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -721 | 824 | 824 | -103 | 88 | []

## 0930Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 09:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 528
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 687 |  | 690 | -3 | 100 | []
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -721 |  | 824 | -103 | 88 | []

## 1030Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 10:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 867
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -821 | 824 | 824 | -3 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 651 | 690 | 690 | -39 | 94 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [OPP] [RO] | RGUTI41 _RSMIR41 _1:line | -1136 | -1500 | -1500 | -364 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Cernavoda - Pelicanu [OPP] [RO] | RPELI41 _RCERN41 _1:line | -1104 | -1500 | -1500 | -396 | 74 | []

## 1030Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 10:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 867
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -821 |  | 824 | -3 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 651 |  | 690 | -39 | 94 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [OPP] [RO] | RGUTI41 _RSMIR41 _1:line | -1136 |  | -1500 | -364 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Cernavoda - Pelicanu [OPP] [RO] | RPELI41 _RCERN41 _1:line | -1104 |  | -1500 | -396 | 74 | []

## 1130Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 11:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 740
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -822 | 824 | 824 | -2 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 665 | 690 | 690 | -25 | 96 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [OPP] [RO] | RGUTI41 _RSMIR41 _1:line | -1152 | -1500 | -1500 | -348 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Cernavoda - Pelicanu [DIR] [RO] | RPELI41 _RCERN41 _1:line | -1119 | -1500 | -1500 | -381 | 75 | []

## 1130Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 11:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 740
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_CO_00004, BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv , N-1 400kV Maritsa Iztok - Plovdiv | [BG-MK] 220kV Aleko - Plovdiv [DIR] [BG] | VALEKO21_VPLOVD21_1:line | -822 |  | 824 | -2 | 100 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 665 |  | 690 | -25 | 96 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [OPP] [RO] | RGUTI41 _RSMIR41 _1:line | -1152 |  | -1500 | -348 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Cernavoda - Pelicanu [DIR] [RO] | RPELI41 _RCERN41 _1:line | -1119 |  | -1500 | -381 | 75 | []

## 1230Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 12:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 916
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 688 | 690 | 690 | -2 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [OPP] [RO] | RGUTI41 _RSMIR41 _1:line | -1201 | -1500 | -1500 | -299 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Cernavoda - Pelicanu [DIR] [RO] | RPELI41 _RCERN41 _1:line | -1176 | -1500 | -1500 | -324 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1136 | 1517 | 1517 | -381 | 75 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1400 | 1888 | 1888 | -488 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Pelicanu - Bucuresti Sud [DIR] [RO] | RBUC241 _RPELI41 _1:line | -1066 | -1500 | -1500 | -434 | 71 | []

## 1230Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 12:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 916
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 688 |  | 690 | -2 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [OPP] [RO] | RGUTI41 _RSMIR41 _1:line | -1201 |  | -1500 | -299 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Cernavoda - Pelicanu [DIR] [RO] | RPELI41 _RCERN41 _1:line | -1176 |  | -1500 | -324 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1136 |  | 1517 | -381 | 75 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1400 |  | 1888 | -488 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Pelicanu - Bucuresti Sud [DIR] [RO] | RBUC241 _RPELI41 _1:line | -1066 |  | -1500 | -434 | 71 | []

## 1330Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 13:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 937
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 688 | 690 | 690 | -2 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [DIR] [RO] | RGUTI41 _RSMIR41 _1:line | -1193 | -1500 | -1500 | -307 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Cernavoda - Pelicanu [DIR] [RO] | RPELI41 _RCERN41 _1:line | -1164 | -1500 | -1500 | -336 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1117 | 1517 | 1517 | -400 | 74 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1363 | 1888 | 1888 | -525 | 72 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Pelicanu - Bucuresti Sud [OPP] [RO] | RBUC241 _RPELI41 _1:line | -1054 | -1500 | -1500 | -446 | 70 | []

## 1330Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 13:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 937
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 688 |  | 690 | -2 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [DIR] [RO] | RGUTI41 _RSMIR41 _1:line | -1193 |  | -1500 | -307 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Cernavoda - Pelicanu [DIR] [RO] | RPELI41 _RCERN41 _1:line | -1164 |  | -1500 | -336 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1117 |  | 1517 | -400 | 74 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1363 |  | 1888 | -525 | 72 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Pelicanu - Bucuresti Sud [OPP] [RO] | RBUC241 _RPELI41 _1:line | -1054 |  | -1500 | -446 | 70 | []

## 1430Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 14:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 233
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 689 | 690 | 690 | -1 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [DIR] [RO] | RGUTI41 _RSMIR41 _1:line | -1199 | -1500 | -1500 | -301 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Cernavoda - Pelicanu [OPP] [RO] | RPELI41 _RCERN41 _1:line | -1151 | -1500 | -1500 | -349 | 77 | []

## 1430Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 14:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 233
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [OPP] [RO] | RBARB22 _RFCSV22 _1:line | 689 |  | 690 | -1 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gutinas - Smardan [DIR] [RO] | RGUTI41 _RSMIR41 _1:line | -1199 |  | -1500 | -301 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Cernavoda - Pelicanu [OPP] [RO] | RPELI41 _RCERN41 _1:line | -1151 |  | -1500 | -349 | 77 | []

## 1530Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 15:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1017
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 687 | 690 | 690 | -3 | 100 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1184 | 1517 | 1517 | -333 | 78 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1461 | 1888 | 1888 | -427 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gura Ialomitei - Bucuresti Sud [DIR] [RO] | RBUC141 _RGIAL21 _1:line | -1117 | -1500 | -1500 | -383 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Pelicanu [DIR] [RO] | RPELI41 _RCERN41 _1:line | -1063 | -1500 | -1500 | -437 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 15:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1017
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Barbosi - Focsani Vest [DIR] [RO] | RBARB22 _RFCSV22 _1:line | 687 |  | 690 | -3 | 100 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1184 |  | 1517 | -333 | 78 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [BG-BG] 400kV Maritsa Iztok - Plovdiv [DIR] [BG] | VPLOVD11_VMA_IZ11_1:line | 1461 |  | 1888 | -427 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gura Ialomitei - Bucuresti Sud [DIR] [RO] | RBUC141 _RGIAL21 _1:line | -1117 |  | -1500 | -383 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Pelicanu [DIR] [RO] | RPELI41 _RCERN41 _1:line | -1063 |  | -1500 | -437 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 16:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1833
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1484 | -1500 | -1500 | -16 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1408 | -1500 | -1500 | -92 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1407 | -1500 | -1500 | -93 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1401 | -1500 | -1500 | -99 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1394 | -1500 | -1500 | -106 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1363 | -1500 | -1500 | -137 | 91 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1363 | -1500 | -1500 | -137 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1363 | -1500 | -1500 | -137 | 91 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1238 | -1500 | -1500 | -262 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1188 | -1500 | -1500 | -312 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -739 | -999 | -999 | -260 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gura Ialomitei - Bucuresti Sud [OPP] [RO] | RBUC141 _RGIAL21 _1:line | -1069 | -1500 | -1500 | -431 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 16:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1833
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1484 |  | -1500 | -16 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1408 |  | -1500 | -92 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1407 |  | -1500 | -93 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1401 |  | -1500 | -99 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1394 |  | -1500 | -106 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1363 |  | -1500 | -137 | 91 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1363 |  | -1500 | -137 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1363 |  | -1500 | -137 | 91 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1238 |  | -1500 | -262 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1188 |  | -1500 | -312 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -739 |  | -999 | -260 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Gura Ialomitei - Bucuresti Sud [OPP] [RO] | RBUC141 _RGIAL21 _1:line | -1069 |  | -1500 | -431 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 17:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1914
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1492 | -1500 | -1500 | -8 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1420 | -1500 | -1500 | -80 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1419 | -1500 | -1500 | -81 | 95 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1418 | -1500 | -1500 | -82 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1397 | -1500 | -1500 | -103 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1380 | -1500 | -1500 | -120 | 92 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1380 | -1500 | -1500 | -120 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1380 | -1500 | -1500 | -120 | 92 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1251 | -1500 | -1500 | -249 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -813 | -999 | -999 | -186 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1203 | -1500 | -1500 | -297 | 80 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1132 | 1600 | 1600 | -468 | 71 | []

## 1730Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 17:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1914
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1492 |  | -1500 | -8 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1420 |  | -1500 | -80 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1419 |  | -1500 | -81 | 95 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1418 |  | -1500 | -82 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1397 |  | -1500 | -103 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1380 |  | -1500 | -120 | 92 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1380 |  | -1500 | -120 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1380 |  | -1500 | -120 | 92 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1251 |  | -1500 | -249 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -813 |  | -999 | -186 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1203 |  | -1500 | -297 | 80 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1132 |  | 1600 | -468 | 71 | []

## 1830Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 18:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1869
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1492 | -1500 | -1500 | -8 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1421 | -1500 | -1500 | -79 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1418 | -1500 | -1500 | -82 | 95 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1417 | -1500 | -1500 | -83 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1398 | -1500 | -1500 | -102 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1379 | -1500 | -1500 | -121 | 92 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1379 | -1500 | -1500 | -121 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1379 | -1500 | -1500 | -121 | 92 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1242 | -1500 | -1500 | -258 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -809 | -999 | -999 | -190 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1194 | -1500 | -1500 | -306 | 80 | []

## 1830Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 18:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1869
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1492 |  | -1500 | -8 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1421 |  | -1500 | -79 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1418 |  | -1500 | -82 | 95 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1417 |  | -1500 | -83 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1398 |  | -1500 | -102 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1379 |  | -1500 | -121 | 92 | []
RO-BG_CO_00002 | N-1 Tantareni-Kozlodui 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1379 |  | -1500 | -121 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1379 |  | -1500 | -121 | 92 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1242 |  | -1500 | -258 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -809 |  | -999 | -190 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1194 |  | -1500 | -306 | 80 | []

## 1930Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 19:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2051
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 | 1601 | 1601 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1590 | -1600 | -1600 | -10 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1360 | -1500 | -1500 | -140 | 91 | []
BC | Base Case | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1248 | 1601 | 1601 | -353 | 78 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1248 | 1601 | 1601 | -353 | 78 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1243 | -1600 | -1600 | -357 | 78 | []

## 1930Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 19:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2051
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 |  | 1601 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1590 |  | -1600 | -10 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1360 |  | -1500 | -140 | 91 | []
BC | Base Case | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1248 |  | 1601 | -353 | 78 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1248 |  | 1601 | -353 | 78 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1243 |  | -1600 | -357 | 78 | []

## 2030Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 20:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2141
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1598 | 1601 | 1601 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | -1595 | -1600 | -1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1458 | -1500 | -1500 | -42 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -940 | -999 | -999 | -59 | 94 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1212 | 1601 | 1601 | -389 | 76 | []
BC | Base Case | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1212 | 1601 | 1601 | -389 | 76 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | -1207 | -1600 | -1600 | -393 | 75 | []

## 2030Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 20:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2141
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1598 |  | 1601 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | -1595 |  | -1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1458 |  | -1500 | -42 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -940 |  | -999 | -59 | 94 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1212 |  | 1601 | -389 | 76 | []
BC | Base Case | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1212 |  | 1601 | -389 | 76 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | -1207 |  | -1600 | -393 | 75 | []

## 2130Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 21:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2159
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1492 | -1500 | -1500 | -8 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1591 | 1601 | 1601 | -10 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1587 | -1600 | -1600 | -13 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -893 | -999 | -999 | -106 | 89 | []
BC | Base Case | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1183 | 1601 | 1601 | -418 | 74 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1183 | 1601 | 1601 | -418 | 74 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1179 | -1600 | -1600 | -421 | 74 | []

## 2130Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 21:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2159
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1492 |  | -1500 | -8 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1591 |  | 1601 | -10 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1587 |  | -1600 | -13 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -893 |  | -999 | -106 | 89 | []
BC | Base Case | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1183 |  | 1601 | -418 | 74 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1183 |  | 1601 | -418 | 74 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1179 |  | -1600 | -421 | 74 | []

## 2230Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 22:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2191
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 | 1601 | 1601 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1591 | -1600 | -1600 | -9 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1461 | -1500 | -1500 | -39 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -904 | -999 | -999 | -96 | 90 | []
BC | Base Case | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1203 | 1601 | 1601 | -398 | 75 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1203 | 1601 | 1601 | -398 | 75 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1199 | -1600 | -1600 | -401 | 75 | []

## 2230Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 22:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2191
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1594 |  | 1601 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1591 |  | -1600 | -9 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1461 |  | -1500 | -39 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -904 |  | -999 | -96 | 90 | []
BC | Base Case | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1203 |  | 1601 | -398 | 75 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1203 |  | 1601 | -398 | 75 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1199 |  | -1600 | -401 | 75 | []

## 2330Preventive
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 23:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2182
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1591 | 1601 | 1601 | -10 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1587 | -1600 | -1600 | -13 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1459 | -1500 | -1500 | -41 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -885 | -999 | -999 | -114 | 89 | []
BC | Base Case | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1203 | 1601 | 1601 | -398 | 75 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1203 | 1601 | 1601 | -398 | 75 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1197 | -1600 | -1600 | -403 | 75 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1132 | 1517 | 1517 | -385 | 75 | []

## 2330Curative
Detailed results
Generated at: | 2022-07-23 21:42
Business day: | 25.07.2022
Timestamp: | 23:30
Border & direction: | South-Romania Import
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2182
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1591 |  | 1601 | -10 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1587 |  | -1600 | -13 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1459 |  | -1500 | -41 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -885 |  | -999 | -114 | 89 | []
BC | Base Case | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1203 |  | 1601 | -398 | 75 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | 1203 |  | 1601 | -398 | 75 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | -1197 |  | -1600 | -403 | 75 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | 1132 |  | 1517 | -385 | 75 | []