## 1230Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2758
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1489 | 1600 | 1600 | -111 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1481 | 1600 | 1600 | -119 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1401 | 1600 | 1600 | -199 | 88 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1350 | 1600 | 1600 | -250 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1327 | 1600 | 1600 | -273 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 | 1600 | 1600 | -289 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1177 | 1600 | 1600 | -423 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1171 | 1600 | 1600 | -429 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1156 | 1600 | 1600 | -444 | 72 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1151 | 1600 | 1600 | -449 | 72 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1148 | 1600 | 1600 | -452 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []

## 1230Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2758
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1591 |  | 1600 | -9 | 99 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1489 |  | 1600 | -111 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1481 |  | 1600 | -119 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1401 |  | 1600 | -199 | 88 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1370 |  | 1600 | -230 | 86 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1350 |  | 1600 | -250 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1327 |  | 1600 | -273 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 |  | 1600 | -289 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1271 |  | 1600 | -329 | 79 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1271 |  | 1600 | -329 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1177 |  | 1600 | -423 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1171 |  | 1600 | -429 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1165 |  | 1600 | -435 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1159 |  | 1600 | -441 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1156 |  | 1600 | -444 | 72 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1151 |  | 1600 | -449 | 72 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1150 |  | 1600 | -450 | 72 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1148 |  | 1600 | -452 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1147 |  | 1600 | -453 | 72 | []

## 1330Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2743
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1480 | 1600 | 1600 | -120 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1480 | 1600 | 1600 | -120 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1394 | 1600 | 1600 | -206 | 87 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1359 | 1600 | 1600 | -241 | 85 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1337 | 1600 | 1600 | -263 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1320 | 1600 | 1600 | -280 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 | 1600 | 1600 | -293 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1280 | 1600 | 1600 | -320 | 80 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 | 1600 | 1600 | -336 | 79 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 | 1600 | 1600 | -338 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 | 1600 | 1600 | -393 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1168 | 1600 | 1600 | -432 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1163 | 1600 | 1600 | -437 | 73 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1155 | 1600 | 1600 | -445 | 72 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1141 | 1600 | 1600 | -459 | 71 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1140 | 1600 | 1600 | -460 | 71 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []

## 1330Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2743
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1591 |  | 1600 | -9 | 99 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1480 |  | 1600 | -120 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1480 |  | 1600 | -120 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1394 |  | 1600 | -206 | 87 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1359 |  | 1600 | -241 | 85 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1337 |  | 1600 | -263 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1320 |  | 1600 | -280 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 |  | 1600 | -293 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1280 |  | 1600 | -320 | 80 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 |  | 1600 | -336 | 79 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 |  | 1600 | -338 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 |  | 1600 | -393 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1168 |  | 1600 | -432 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1163 |  | 1600 | -437 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1163 |  | 1600 | -437 | 73 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1155 |  | 1600 | -445 | 72 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1150 |  | 1600 | -450 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1147 |  | 1600 | -453 | 72 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1141 |  | 1600 | -459 | 71 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1140 |  | 1600 | -460 | 71 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1140 |  | 1600 | -460 | 71 | []

## 1430Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2721
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1490 | 1600 | 1600 | -110 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1483 | 1600 | 1600 | -117 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1394 | 1600 | 1600 | -206 | 87 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1362 | 1600 | 1600 | -238 | 85 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1336 | 1600 | 1600 | -264 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1321 | 1600 | 1600 | -279 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1310 | 1600 | 1600 | -290 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1281 | 1600 | 1600 | -319 | 80 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1268 | 1600 | 1600 | -332 | 79 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1266 | 1600 | 1600 | -334 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1217 | 1600 | 1600 | -383 | 76 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1216 | 1600 | 1600 | -384 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1174 | 1600 | 1600 | -426 | 73 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1171 | 1600 | 1600 | -429 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1169 | 1600 | 1600 | -431 | 73 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1167 | 1600 | 1600 | -433 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 72 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1153 | 1600 | 1600 | -447 | 72 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1152 | 1600 | 1600 | -448 | 72 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1151 | 1600 | 1600 | -449 | 72 | []

## 1430Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2721
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1595 |  | 1600 | -5 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1490 |  | 1600 | -110 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1483 |  | 1600 | -117 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1394 |  | 1600 | -206 | 87 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1362 |  | 1600 | -238 | 85 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1336 |  | 1600 | -264 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1321 |  | 1600 | -279 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1310 |  | 1600 | -290 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1281 |  | 1600 | -319 | 80 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1268 |  | 1600 | -332 | 79 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1266 |  | 1600 | -334 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1217 |  | 1600 | -383 | 76 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1216 |  | 1600 | -384 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1174 |  | 1600 | -426 | 73 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1171 |  | 1600 | -429 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1169 |  | 1600 | -431 | 73 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1167 |  | 1600 | -433 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1161 |  | 1600 | -439 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 72 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1153 |  | 1600 | -447 | 72 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1152 |  | 1600 | -448 | 72 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1151 |  | 1600 | -449 | 72 | []

## 1530Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2755
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1592 | 1600 | 1600 | -8 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1523 | 1600 | 1600 | -77 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1489 | 1600 | 1600 | -111 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1430 | 1600 | 1600 | -170 | 89 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1399 | 1600 | 1600 | -201 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1372 | 1600 | 1600 | -228 | 86 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1354 | 1600 | 1600 | -246 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1327 | 1600 | 1600 | -273 | 83 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1313 | 1600 | 1600 | -287 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1299 | 1600 | 1600 | -301 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1298 | 1600 | 1600 | -302 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1266 | 1600 | 1600 | -334 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1221 | 1600 | 1600 | -379 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1202 | 1600 | 1600 | -398 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1197 | 1600 | 1600 | -403 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1197 | 1600 | 1600 | -403 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1173 | 1600 | 1600 | -427 | 73 | []

## 1530Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2755
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1592 |  | 1600 | -8 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1523 |  | 1600 | -77 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1489 |  | 1600 | -111 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1430 |  | 1600 | -170 | 89 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1399 |  | 1600 | -201 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1372 |  | 1600 | -228 | 86 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1354 |  | 1600 | -246 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1327 |  | 1600 | -273 | 83 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1313 |  | 1600 | -287 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1299 |  | 1600 | -301 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1298 |  | 1600 | -302 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1266 |  | 1600 | -334 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1221 |  | 1600 | -379 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1210 |  | 1600 | -390 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1202 |  | 1600 | -398 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1197 |  | 1600 | -403 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1197 |  | 1600 | -403 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1175 |  | 1600 | -425 | 73 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1173 |  | 1600 | -427 | 73 | []

## 1630Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2808
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1520 | 1600 | 1600 | -80 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1496 | 1600 | 1600 | -104 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1447 | 1600 | 1600 | -153 | 90 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1413 | 1600 | 1600 | -187 | 88 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1386 | 1600 | 1600 | -214 | 87 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1368 | 1600 | 1600 | -232 | 86 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1329 | 1600 | 1600 | -271 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 | 1600 | 1600 | -276 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1309 | 1600 | 1600 | -291 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1308 | 1600 | 1600 | -292 | 82 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 | 1600 | 1600 | -328 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 | 1600 | 1600 | -328 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 | 1600 | 1600 | -336 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 | 1600 | 1600 | -336 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 | 1600 | 1600 | -336 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1263 | 1600 | 1600 | -337 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1263 | 1600 | 1600 | -337 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 | 1600 | 1600 | -341 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1252 | 1600 | 1600 | -348 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 | 1600 | 1600 | -369 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1176 | 1600 | 1600 | -424 | 73 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1161 | 1600 | 1600 | -439 | 73 | []

## 1630Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2808
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 |  | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1520 |  | 1600 | -80 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1496 |  | 1600 | -104 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1447 |  | 1600 | -153 | 90 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1413 |  | 1600 | -187 | 88 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1386 |  | 1600 | -214 | 87 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1368 |  | 1600 | -232 | 86 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1329 |  | 1600 | -271 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 |  | 1600 | -276 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1309 |  | 1600 | -291 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1308 |  | 1600 | -292 | 82 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 |  | 1600 | -328 | 80 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 |  | 1600 | -328 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1271 |  | 1600 | -329 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1271 |  | 1600 | -329 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 |  | 1600 | -336 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 |  | 1600 | -336 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 |  | 1600 | -336 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1263 |  | 1600 | -337 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1263 |  | 1600 | -337 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 |  | 1600 | -341 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1252 |  | 1600 | -348 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 |  | 1600 | -369 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1199 |  | 1600 | -401 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1176 |  | 1600 | -424 | 73 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1163 |  | 1600 | -437 | 73 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1161 |  | 1600 | -439 | 73 | []

## 1730Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2902
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1559 | 1600 | 1600 | -41 | 97 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1510 | 1600 | 1600 | -90 | 94 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1499 | 1600 | 1600 | -101 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1466 | 1600 | 1600 | -134 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1444 | 1600 | 1600 | -156 | 90 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1429 | 1600 | 1600 | -171 | 89 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1389 | 1600 | 1600 | -211 | 87 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1356 | 1600 | 1600 | -244 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1347 | 1600 | 1600 | -253 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1318 | 1600 | 1600 | -282 | 82 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1316 | 1600 | 1600 | -284 | 82 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1315 | 1600 | 1600 | -285 | 82 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 | 1600 | 1600 | -288 | 82 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1308 | 1600 | 1600 | -292 | 82 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1308 | 1600 | 1600 | -292 | 82 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 | 1600 | 1600 | -293 | 82 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 | 1600 | 1600 | -293 | 82 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 | 1600 | 1600 | -293 | 82 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1306 | 1600 | 1600 | -294 | 82 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1306 | 1600 | 1600 | -294 | 82 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1305 | 1600 | 1600 | -295 | 82 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 | 1600 | 1600 | -296 | 82 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 | 1600 | 1600 | -296 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1298 | 1600 | 1600 | -302 | 81 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1297 | 1600 | 1600 | -303 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1288 | 1600 | 1600 | -312 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1287 | 1600 | 1600 | -313 | 80 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1286 | 1600 | 1600 | -314 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1285 | 1600 | 1600 | -315 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 | 1600 | 1600 | -328 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1196 | 1600 | 1600 | -404 | 75 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1179 | 1600 | 1600 | -421 | 74 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1177 | 1600 | 1600 | -423 | 74 | []

## 1730Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2902
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1598 |  | 1600 | -2 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1559 |  | 1600 | -41 | 97 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1510 |  | 1600 | -90 | 94 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1499 |  | 1600 | -101 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1466 |  | 1600 | -134 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1444 |  | 1600 | -156 | 90 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1429 |  | 1600 | -171 | 89 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1389 |  | 1600 | -211 | 87 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 |  | 1600 | -243 | 85 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 |  | 1600 | -243 | 85 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1356 |  | 1600 | -244 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1347 |  | 1600 | -253 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1318 |  | 1600 | -282 | 82 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1316 |  | 1600 | -284 | 82 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1315 |  | 1600 | -285 | 82 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 |  | 1600 | -288 | 82 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1308 |  | 1600 | -292 | 82 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1308 |  | 1600 | -292 | 82 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 |  | 1600 | -293 | 82 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 |  | 1600 | -293 | 82 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 |  | 1600 | -293 | 82 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1306 |  | 1600 | -294 | 82 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1306 |  | 1600 | -294 | 82 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1305 |  | 1600 | -295 | 82 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 |  | 1600 | -296 | 82 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 |  | 1600 | -296 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1298 |  | 1600 | -302 | 81 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1297 |  | 1600 | -303 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1290 |  | 1600 | -310 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1288 |  | 1600 | -312 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1287 |  | 1600 | -313 | 80 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1286 |  | 1600 | -314 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1285 |  | 1600 | -315 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 |  | 1600 | -328 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1196 |  | 1600 | -404 | 75 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1179 |  | 1600 | -421 | 74 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1177 |  | 1600 | -423 | 74 | []

## 1830Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2937
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1577 | 1600 | 1600 | -23 | 99 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1535 | 1600 | 1600 | -65 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1501 | 1600 | 1600 | -99 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1491 | 1600 | 1600 | -109 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1465 | 1600 | 1600 | -135 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1451 | 1600 | 1600 | -149 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1411 | 1600 | 1600 | -189 | 88 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1386 | 1600 | 1600 | -214 | 87 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1376 | 1600 | 1600 | -224 | 86 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1374 | 1600 | 1600 | -226 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1338 | 1600 | 1600 | -262 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1336 | 1600 | 1600 | -264 | 83 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1332 | 1600 | 1600 | -268 | 83 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 | 1600 | 1600 | -270 | 83 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 | 1600 | 1600 | -276 | 83 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 | 1600 | 1600 | -276 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 | 1600 | 1600 | -276 | 83 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 | 1600 | 1600 | -276 | 83 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 | 1600 | 1600 | -276 | 83 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1323 | 1600 | 1600 | -277 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1323 | 1600 | 1600 | -277 | 83 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 | 1600 | 1600 | -278 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1321 | 1600 | 1600 | -279 | 83 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1321 | 1600 | 1600 | -279 | 83 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1315 | 1600 | 1600 | -285 | 82 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1314 | 1600 | 1600 | -286 | 82 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1313 | 1600 | 1600 | -287 | 82 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1311 | 1600 | 1600 | -289 | 82 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1301 | 1600 | 1600 | -299 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1298 | 1600 | 1600 | -302 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1286 | 1600 | 1600 | -314 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1190 | 1600 | 1600 | -410 | 74 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1189 | 1600 | 1600 | -411 | 74 | []

## 1830Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2937
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 |  | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1577 |  | 1600 | -23 | 99 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1535 |  | 1600 | -65 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1501 |  | 1600 | -99 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1491 |  | 1600 | -109 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1465 |  | 1600 | -135 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1451 |  | 1600 | -149 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1411 |  | 1600 | -189 | 88 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1386 |  | 1600 | -214 | 87 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1376 |  | 1600 | -224 | 86 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1374 |  | 1600 | -226 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 |  | 1600 | -243 | 85 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1338 |  | 1600 | -262 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1336 |  | 1600 | -264 | 83 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1332 |  | 1600 | -268 | 83 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 |  | 1600 | -270 | 83 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 |  | 1600 | -276 | 83 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 |  | 1600 | -276 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 |  | 1600 | -276 | 83 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 |  | 1600 | -276 | 83 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 |  | 1600 | -276 | 83 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1323 |  | 1600 | -277 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1323 |  | 1600 | -277 | 83 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 |  | 1600 | -278 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1321 |  | 1600 | -279 | 83 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1321 |  | 1600 | -279 | 83 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1315 |  | 1600 | -285 | 82 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1314 |  | 1600 | -286 | 82 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1313 |  | 1600 | -287 | 82 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1311 |  | 1600 | -289 | 82 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 |  | 1600 | -298 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1301 |  | 1600 | -299 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1298 |  | 1600 | -302 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1286 |  | 1600 | -314 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1205 |  | 1600 | -395 | 75 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1190 |  | 1600 | -410 | 74 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1189 |  | 1600 | -411 | 74 | []

## 1930Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2924
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1576 | 1600 | 1600 | -24 | 99 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1532 | 1600 | 1600 | -68 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1494 | 1600 | 1600 | -106 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1485 | 1600 | 1600 | -115 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1465 | 1600 | 1600 | -135 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1448 | 1600 | 1600 | -152 | 90 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1408 | 1600 | 1600 | -192 | 88 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1386 | 1600 | 1600 | -214 | 87 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1374 | 1600 | 1600 | -226 | 86 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1372 | 1600 | 1600 | -228 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 | 1600 | 1600 | -247 | 85 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1337 | 1600 | 1600 | -263 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1333 | 1600 | 1600 | -267 | 83 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 | 1600 | 1600 | -270 | 83 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1328 | 1600 | 1600 | -272 | 83 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1323 | 1600 | 1600 | -277 | 83 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1323 | 1600 | 1600 | -277 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 | 1600 | 1600 | -278 | 83 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 | 1600 | 1600 | -278 | 83 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 | 1600 | 1600 | -278 | 83 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 | 1600 | 1600 | -278 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1321 | 1600 | 1600 | -279 | 83 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1320 | 1600 | 1600 | -280 | 82 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1320 | 1600 | 1600 | -280 | 82 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1319 | 1600 | 1600 | -281 | 82 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1313 | 1600 | 1600 | -287 | 82 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 | 1600 | 1600 | -288 | 82 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 | 1600 | 1600 | -288 | 82 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1309 | 1600 | 1600 | -291 | 82 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1301 | 1600 | 1600 | -299 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1299 | 1600 | 1600 | -301 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1294 | 1600 | 1600 | -306 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1287 | 1600 | 1600 | -313 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1247 | 1600 | 1600 | -353 | 78 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1191 | 1600 | 1600 | -409 | 74 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1190 | 1600 | 1600 | -410 | 74 | []

## 1930Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2924
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1591 |  | 1600 | -9 | 99 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1576 |  | 1600 | -24 | 99 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1532 |  | 1600 | -68 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1494 |  | 1600 | -106 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1485 |  | 1600 | -115 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1465 |  | 1600 | -135 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1448 |  | 1600 | -152 | 90 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1408 |  | 1600 | -192 | 88 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1386 |  | 1600 | -214 | 87 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1374 |  | 1600 | -226 | 86 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1372 |  | 1600 | -228 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 |  | 1600 | -247 | 85 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1337 |  | 1600 | -263 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1333 |  | 1600 | -267 | 83 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 |  | 1600 | -270 | 83 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1328 |  | 1600 | -272 | 83 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1323 |  | 1600 | -277 | 83 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1323 |  | 1600 | -277 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 |  | 1600 | -278 | 83 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 |  | 1600 | -278 | 83 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 |  | 1600 | -278 | 83 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 |  | 1600 | -278 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1321 |  | 1600 | -279 | 83 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1320 |  | 1600 | -280 | 82 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1320 |  | 1600 | -280 | 82 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1319 |  | 1600 | -281 | 82 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1313 |  | 1600 | -287 | 82 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 |  | 1600 | -288 | 82 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 |  | 1600 | -288 | 82 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1309 |  | 1600 | -291 | 82 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1301 |  | 1600 | -299 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1299 |  | 1600 | -301 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1294 |  | 1600 | -306 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1287 |  | 1600 | -313 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1247 |  | 1600 | -353 | 78 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1191 |  | 1600 | -409 | 74 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1190 |  | 1600 | -410 | 74 | []

## 2030Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2972
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1541 | 1600 | 1600 | -59 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1504 | 1600 | 1600 | -96 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1502 | 1600 | 1600 | -98 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1480 | 1600 | 1600 | -120 | 93 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1454 | 1600 | 1600 | -146 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1415 | 1600 | 1600 | -185 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1382 | 1600 | 1600 | -218 | 86 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1382 | 1600 | 1600 | -218 | 86 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1379 | 1600 | 1600 | -221 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1364 | 1600 | 1600 | -236 | 85 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1347 | 1600 | 1600 | -253 | 84 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1338 | 1600 | 1600 | -262 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1336 | 1600 | 1600 | -264 | 84 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1333 | 1600 | 1600 | -267 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1331 | 1600 | 1600 | -269 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 | 1600 | 1600 | -270 | 83 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 | 1600 | 1600 | -270 | 83 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 | 1600 | 1600 | -270 | 83 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 | 1600 | 1600 | -270 | 83 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 | 1600 | 1600 | -270 | 83 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1329 | 1600 | 1600 | -271 | 83 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1328 | 1600 | 1600 | -272 | 83 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1326 | 1600 | 1600 | -274 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1326 | 1600 | 1600 | -274 | 83 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 | 1600 | 1600 | -278 | 83 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1320 | 1600 | 1600 | -280 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1315 | 1600 | 1600 | -285 | 82 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 | 1600 | 1600 | -288 | 82 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1309 | 1600 | 1600 | -291 | 82 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1308 | 1600 | 1600 | -292 | 82 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 | 1600 | 1600 | -297 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1296 | 1600 | 1600 | -304 | 81 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 | 1600 | 1600 | -393 | 75 | []

## 2030Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2972
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1594 |  | 1600 | -6 | 100 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1541 |  | 1600 | -59 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1504 |  | 1600 | -96 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1502 |  | 1600 | -98 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1480 |  | 1600 | -120 | 93 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1454 |  | 1600 | -146 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1415 |  | 1600 | -185 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1382 |  | 1600 | -218 | 86 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1382 |  | 1600 | -218 | 86 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1379 |  | 1600 | -221 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1364 |  | 1600 | -236 | 85 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1347 |  | 1600 | -253 | 84 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1338 |  | 1600 | -262 | 84 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1336 |  | 1600 | -264 | 84 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1333 |  | 1600 | -267 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1331 |  | 1600 | -269 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 |  | 1600 | -270 | 83 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 |  | 1600 | -270 | 83 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 |  | 1600 | -270 | 83 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 |  | 1600 | -270 | 83 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 |  | 1600 | -270 | 83 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1329 |  | 1600 | -271 | 83 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1328 |  | 1600 | -272 | 83 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1326 |  | 1600 | -274 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1326 |  | 1600 | -274 | 83 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1322 |  | 1600 | -278 | 83 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1320 |  | 1600 | -280 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1315 |  | 1600 | -285 | 82 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 |  | 1600 | -288 | 82 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1309 |  | 1600 | -291 | 82 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1308 |  | 1600 | -292 | 82 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 |  | 1600 | -297 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1296 |  | 1600 | -304 | 81 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1215 |  | 1600 | -385 | 76 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1214 |  | 1600 | -386 | 76 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 |  | 1600 | -393 | 75 | []

## 2130Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2870
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1587 | 1600 | 1600 | -13 | 99 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1504 | 1600 | 1600 | -96 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1496 | 1600 | 1600 | -104 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1476 | 1600 | 1600 | -124 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1452 | 1600 | 1600 | -148 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1419 | 1600 | 1600 | -181 | 89 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1383 | 1600 | 1600 | -217 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1363 | 1600 | 1600 | -237 | 85 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1354 | 1600 | 1600 | -246 | 85 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1325 | 1600 | 1600 | -275 | 83 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1318 | 1600 | 1600 | -282 | 82 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1313 | 1600 | 1600 | -287 | 82 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 | 1600 | 1600 | -289 | 82 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 | 1600 | 1600 | -289 | 82 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 | 1600 | 1600 | -289 | 82 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 | 1600 | 1600 | -289 | 82 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 | 1600 | 1600 | -289 | 82 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 | 1600 | 1600 | -289 | 82 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1309 | 1600 | 1600 | -291 | 82 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 | 1600 | 1600 | -293 | 82 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1306 | 1600 | 1600 | -294 | 82 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1305 | 1600 | 1600 | -295 | 82 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 | 1600 | 1600 | -296 | 82 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1300 | 1600 | 1600 | -300 | 81 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1295 | 1600 | 1600 | -305 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1295 | 1600 | 1600 | -305 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1293 | 1600 | 1600 | -307 | 81 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1289 | 1600 | 1600 | -311 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1273 | 1600 | 1600 | -327 | 80 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 | 1600 | 1600 | -393 | 75 | []

## 2130Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2870
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1587 |  | 1600 | -13 | 99 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1504 |  | 1600 | -96 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1496 |  | 1600 | -104 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1476 |  | 1600 | -124 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1452 |  | 1600 | -148 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1419 |  | 1600 | -181 | 89 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1383 |  | 1600 | -217 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1363 |  | 1600 | -237 | 85 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 |  | 1600 | -243 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1354 |  | 1600 | -246 | 85 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1325 |  | 1600 | -275 | 83 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1318 |  | 1600 | -282 | 82 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1313 |  | 1600 | -287 | 82 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 |  | 1600 | -289 | 82 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 |  | 1600 | -289 | 82 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 |  | 1600 | -289 | 82 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 |  | 1600 | -289 | 82 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 |  | 1600 | -289 | 82 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1311 |  | 1600 | -289 | 82 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1309 |  | 1600 | -291 | 82 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 |  | 1600 | -293 | 82 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1306 |  | 1600 | -294 | 82 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1305 |  | 1600 | -295 | 82 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 |  | 1600 | -296 | 82 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 |  | 1600 | -298 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1300 |  | 1600 | -300 | 81 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1295 |  | 1600 | -305 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1295 |  | 1600 | -305 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1293 |  | 1600 | -307 | 81 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1289 |  | 1600 | -311 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1273 |  | 1600 | -327 | 80 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1225 |  | 1600 | -375 | 77 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1224 |  | 1600 | -376 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 |  | 1600 | -393 | 75 | []

## 2230Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3028
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1573 | 1600 | 1600 | -27 | 98 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1507 | 1600 | 1600 | -93 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1496 | 1600 | 1600 | -104 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1491 | 1600 | 1600 | -109 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1473 | 1600 | 1600 | -127 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1426 | 1600 | 1600 | -174 | 89 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1391 | 1600 | 1600 | -209 | 87 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1360 | 1600 | 1600 | -240 | 85 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1356 | 1600 | 1600 | -244 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1348 | 1600 | 1600 | -252 | 84 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1314 | 1600 | 1600 | -286 | 82 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1310 | 1600 | 1600 | -290 | 82 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1305 | 1600 | 1600 | -295 | 82 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 | 1600 | 1600 | -296 | 82 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 | 1600 | 1600 | -296 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 | 1600 | 1600 | -297 | 81 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 | 1600 | 1600 | -297 | 81 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 | 1600 | 1600 | -297 | 81 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1297 | 1600 | 1600 | -303 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1297 | 1600 | 1600 | -303 | 81 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1297 | 1600 | 1600 | -303 | 81 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1293 | 1600 | 1600 | -307 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1291 | 1600 | 1600 | -309 | 81 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1285 | 1600 | 1600 | -315 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1285 | 1600 | 1600 | -315 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1278 | 1600 | 1600 | -322 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 | 1600 | 1600 | -336 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []

## 2230Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3028
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1596 |  | 1600 | -4 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1573 |  | 1600 | -27 | 98 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1507 |  | 1600 | -93 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1496 |  | 1600 | -104 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1491 |  | 1600 | -109 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1473 |  | 1600 | -127 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1426 |  | 1600 | -174 | 89 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1391 |  | 1600 | -209 | 87 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1360 |  | 1600 | -240 | 85 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1356 |  | 1600 | -244 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1348 |  | 1600 | -252 | 84 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1314 |  | 1600 | -286 | 82 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1310 |  | 1600 | -290 | 82 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1305 |  | 1600 | -295 | 82 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 |  | 1600 | -296 | 82 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 |  | 1600 | -296 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 |  | 1600 | -297 | 81 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 |  | 1600 | -297 | 81 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 |  | 1600 | -297 | 81 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 |  | 1600 | -298 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1297 |  | 1600 | -303 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1297 |  | 1600 | -303 | 81 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1297 |  | 1600 | -303 | 81 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1293 |  | 1600 | -307 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1291 |  | 1600 | -309 | 81 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1290 |  | 1600 | -310 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1290 |  | 1600 | -310 | 81 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1285 |  | 1600 | -315 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1285 |  | 1600 | -315 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1278 |  | 1600 | -322 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 |  | 1600 | -336 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1212 |  | 1600 | -388 | 76 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1210 |  | 1600 | -390 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1178 |  | 1600 | -422 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1163 |  | 1600 | -437 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1158 |  | 1600 | -442 | 72 | []

## 2330Preventive
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2995
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1567 | 1600 | 1600 | -33 | 98 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1508 | 1600 | 1600 | -92 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1505 | 1600 | 1600 | -95 | 94 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1481 | 1600 | 1600 | -119 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1462 | 1600 | 1600 | -138 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1426 | 1600 | 1600 | -174 | 89 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1390 | 1600 | 1600 | -210 | 87 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 | 1600 | 1600 | -247 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1345 | 1600 | 1600 | -255 | 84 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1314 | 1600 | 1600 | -286 | 82 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1309 | 1600 | 1600 | -291 | 82 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 | 1600 | 1600 | -296 | 81 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 | 1600 | 1600 | -296 | 81 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 | 1600 | 1600 | -297 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 | 1600 | 1600 | -297 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1301 | 1600 | 1600 | -299 | 81 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1301 | 1600 | 1600 | -299 | 81 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1300 | 1600 | 1600 | -300 | 81 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1296 | 1600 | 1600 | -304 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1296 | 1600 | 1600 | -304 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1295 | 1600 | 1600 | -305 | 81 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1287 | 1600 | 1600 | -313 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1286 | 1600 | 1600 | -314 | 80 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1283 | 1600 | 1600 | -317 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1282 | 1600 | 1600 | -318 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1276 | 1600 | 1600 | -324 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1204 | 1600 | 1600 | -396 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1179 | 1600 | 1600 | -421 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []

## 2330Curative
Detailed results
Generated at: | 2023-11-28 08:13
Business day: | 28.11.2023
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2995
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 |  | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1567 |  | 1600 | -33 | 98 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1508 |  | 1600 | -92 | 94 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1505 |  | 1600 | -95 | 94 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1481 |  | 1600 | -119 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1462 |  | 1600 | -138 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1426 |  | 1600 | -174 | 89 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1390 |  | 1600 | -210 | 87 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 |  | 1600 | -243 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 |  | 1600 | -247 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1345 |  | 1600 | -255 | 84 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1314 |  | 1600 | -286 | 82 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1309 |  | 1600 | -291 | 82 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 |  | 1600 | -296 | 81 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 |  | 1600 | -296 | 81 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 |  | 1600 | -297 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1303 |  | 1600 | -297 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1301 |  | 1600 | -299 | 81 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1301 |  | 1600 | -299 | 81 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1300 |  | 1600 | -300 | 81 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1296 |  | 1600 | -304 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1296 |  | 1600 | -304 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1295 |  | 1600 | -305 | 81 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1290 |  | 1600 | -310 | 81 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1287 |  | 1600 | -313 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1286 |  | 1600 | -314 | 80 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1283 |  | 1600 | -317 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1282 |  | 1600 | -318 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1276 |  | 1600 | -324 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1205 |  | 1600 | -395 | 75 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | 1204 |  | 1600 | -396 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1179 |  | 1600 | -421 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1166 |  | 1600 | -434 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1159 |  | 1600 | -441 | 72 | []