## 1230Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1366
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1461 | 1600 | 1600 | -139 | 91 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1445 | 1600 | 1600 | -155 | 90 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1402 | 1600 | 1600 | -198 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1394 | 1600 | 1600 | -206 | 87 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1394 | 1600 | 1600 | -206 | 87 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1394 | 1600 | 1600 | -206 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1389 | 1600 | 1600 | -211 | 87 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1320 | 1600 | 1600 | -280 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1297 | 1600 | 1600 | -303 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -702 | -999 | -999 | -297 | 70 | []

## 1230Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1366
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1461 |  | 1600 | -139 | 91 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1445 |  | 1600 | -155 | 90 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1402 |  | 1600 | -198 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1394 |  | 1600 | -206 | 87 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1394 |  | 1600 | -206 | 87 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1394 |  | 1600 | -206 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1389 |  | 1600 | -211 | 87 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1320 |  | 1600 | -280 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1297 |  | 1600 | -303 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -702 |  | -999 | -297 | 70 | []

## 1330Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1021
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1459 | 1600 | 1600 | -141 | 91 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1443 | 1600 | 1600 | -157 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1387 | 1600 | 1600 | -213 | 87 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1387 | 1600 | 1600 | -213 | 87 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1387 | 1600 | 1600 | -213 | 87 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1380 | 1600 | 1600 | -220 | 86 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1377 | 1600 | 1600 | -223 | 86 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1314 | 1600 | 1600 | -286 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1277 | 1600 | 1600 | -323 | 80 | []

## 1330Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1021
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1459 |  | 1600 | -141 | 91 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1443 |  | 1600 | -157 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1387 |  | 1600 | -213 | 87 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1387 |  | 1600 | -213 | 87 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1387 |  | 1600 | -213 | 87 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1380 |  | 1600 | -220 | 86 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1377 |  | 1600 | -223 | 86 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1314 |  | 1600 | -286 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1277 |  | 1600 | -323 | 80 | []

## 1430Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 957
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1456 | 1600 | 1600 | -144 | 91 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1439 | 1600 | 1600 | -161 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1373 | 1600 | 1600 | -227 | 86 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1373 | 1600 | 1600 | -227 | 86 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1373 | 1600 | 1600 | -227 | 86 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1354 | 1600 | 1600 | -246 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1349 | 1600 | 1600 | -251 | 84 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1301 | 1600 | 1600 | -299 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1246 | 1600 | 1600 | -354 | 78 | []

## 1430Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 957
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1456 |  | 1600 | -144 | 91 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1439 |  | 1600 | -161 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1373 |  | 1600 | -227 | 86 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1373 |  | 1600 | -227 | 86 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1373 |  | 1600 | -227 | 86 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1354 |  | 1600 | -246 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1349 |  | 1600 | -251 | 84 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1301 |  | 1600 | -299 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1246 |  | 1600 | -354 | 78 | []

## 1530Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 986
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1583 | 1600 | 1600 | -17 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1520 | 1600 | 1600 | -80 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1485 | 1600 | 1600 | -115 | 93 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1485 | 1600 | 1600 | -115 | 93 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1485 | 1600 | 1600 | -115 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1484 | 1600 | 1600 | -116 | 93 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1442 | 1600 | 1600 | -158 | 90 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1392 | 1600 | 1600 | -208 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1312 | 1600 | 1600 | -288 | 82 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Lacu Sarat - Smardan [OPP] [RO] | RSMIR41 _RLACS41 _1:line | -1147 | -1600 | -1600 | -453 | 72 | []

## 1530Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 986
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1583 |  | 1600 | -17 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1520 |  | 1600 | -80 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1485 |  | 1600 | -115 | 93 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1485 |  | 1600 | -115 | 93 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1485 |  | 1600 | -115 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1484 |  | 1600 | -116 | 93 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1442 |  | 1600 | -158 | 90 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1392 |  | 1600 | -208 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1312 |  | 1600 | -288 | 82 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Lacu Sarat - Smardan [OPP] [RO] | RSMIR41 _RLACS41 _1:line | -1147 |  | -1600 | -453 | 72 | []

## 1630Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 939
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1583 | 1600 | 1600 | -17 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1514 | 1600 | 1600 | -86 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1473 | 1600 | 1600 | -127 | 92 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1473 | 1600 | 1600 | -127 | 92 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1473 | 1600 | 1600 | -127 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1470 | 1600 | 1600 | -130 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1418 | 1600 | 1600 | -182 | 89 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1377 | 1600 | 1600 | -223 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1275 | 1600 | 1600 | -325 | 80 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Lacu Sarat - Smardan [DIR] [RO] | RSMIR41 _RLACS41 _1:line | -1120 | -1600 | -1600 | -480 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 939
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1583 |  | 1600 | -17 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1514 |  | 1600 | -86 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1473 |  | 1600 | -127 | 92 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1473 |  | 1600 | -127 | 92 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1473 |  | 1600 | -127 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1470 |  | 1600 | -130 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1418 |  | 1600 | -182 | 89 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1377 |  | 1600 | -223 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1275 |  | 1600 | -325 | 80 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Lacu Sarat - Smardan [DIR] [RO] | RSMIR41 _RLACS41 _1:line | -1120 |  | -1600 | -480 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 992
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1585 | 1600 | 1600 | -15 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1563 | 1600 | 1600 | -37 | 98 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1505 | 1600 | 1600 | -95 | 94 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1504 | 1600 | 1600 | -96 | 94 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1499 | 1600 | 1600 | -101 | 94 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1450 | 1600 | 1600 | -150 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1450 | 1600 | 1600 | -150 | 91 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1448 | 1600 | 1600 | -152 | 90 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1384 | 1600 | 1600 | -216 | 86 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1352 | 1600 | 1600 | -248 | 85 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1264 | 1600 | 1600 | -336 | 79 | []

## 1730Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 992
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1585 |  | 1600 | -15 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1563 |  | 1600 | -37 | 98 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1505 |  | 1600 | -95 | 94 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1504 |  | 1600 | -96 | 94 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1499 |  | 1600 | -101 | 94 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1450 |  | 1600 | -150 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1450 |  | 1600 | -150 | 91 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1448 |  | 1600 | -152 | 90 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1384 |  | 1600 | -216 | 86 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1352 |  | 1600 | -248 | 85 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1264 |  | 1600 | -336 | 79 | []

## 1830Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 971
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1585 | 1600 | 1600 | -15 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1563 | 1600 | 1600 | -37 | 98 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1508 | 1600 | 1600 | -92 | 94 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1505 | 1600 | 1600 | -95 | 94 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1501 | 1600 | 1600 | -99 | 94 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1454 | 1600 | 1600 | -146 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1454 | 1600 | 1600 | -146 | 91 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1452 | 1600 | 1600 | -148 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1391 | 1600 | 1600 | -209 | 87 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1358 | 1600 | 1600 | -242 | 85 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1274 | 1600 | 1600 | -326 | 80 | []

## 1830Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 971
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1585 |  | 1600 | -15 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1563 |  | 1600 | -37 | 98 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1508 |  | 1600 | -92 | 94 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1505 |  | 1600 | -95 | 94 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1501 |  | 1600 | -99 | 94 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1454 |  | 1600 | -146 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1454 |  | 1600 | -146 | 91 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1452 |  | 1600 | -148 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1391 |  | 1600 | -209 | 87 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1358 |  | 1600 | -242 | 85 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1274 |  | 1600 | -326 | 80 | []

## 1930Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1480
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1583 | 1600 | 1600 | -17 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1560 | 1600 | 1600 | -40 | 97 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1509 | 1600 | 1600 | -91 | 94 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1506 | 1600 | 1600 | -94 | 94 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1505 | 1600 | 1600 | -95 | 94 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1470 | 1600 | 1600 | -130 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1470 | 1600 | 1600 | -130 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1470 | 1600 | 1600 | -130 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1446 | 1600 | 1600 | -154 | 90 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1379 | 1600 | 1600 | -221 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1319 | 1600 | 1600 | -281 | 82 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Lacu Sarat - Smardan [OPP] [RO] | RSMIR41 _RLACS41 _1:line | -1125 | -1600 | -1600 | -475 | 70 | []

## 1930Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1480
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1583 |  | 1600 | -17 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1560 |  | 1600 | -40 | 97 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1509 |  | 1600 | -91 | 94 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1506 |  | 1600 | -94 | 94 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1505 |  | 1600 | -95 | 94 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1470 |  | 1600 | -130 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1470 |  | 1600 | -130 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1470 |  | 1600 | -130 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1446 |  | 1600 | -154 | 90 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1379 |  | 1600 | -221 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1319 |  | 1600 | -281 | 82 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Lacu Sarat - Smardan [OPP] [RO] | RSMIR41 _RLACS41 _1:line | -1125 |  | -1600 | -475 | 70 | []

## 2030Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1827
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1584 | 1600 | 1600 | -16 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1555 | 1600 | 1600 | -45 | 97 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1514 | 1600 | 1600 | -86 | 95 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1510 | 1600 | 1600 | -90 | 94 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1505 | 1600 | 1600 | -95 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1482 | 1600 | 1600 | -118 | 93 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1482 | 1600 | 1600 | -118 | 93 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1482 | 1600 | 1600 | -118 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1482 | 1600 | 1600 | -118 | 93 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1391 | 1600 | 1600 | -209 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1357 | 1600 | 1600 | -243 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1308 | 1600 | 1600 | -292 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1304 | 1601 | 1601 | -297 | 81 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Lacu Sarat - Smardan [DIR] [RO] | RSMIR41 _RLACS41 _1:line | -1160 | -1600 | -1600 | -440 | 73 | []

## 2030Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1827
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1584 |  | 1600 | -16 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1555 |  | 1600 | -45 | 97 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1514 |  | 1600 | -86 | 95 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1510 |  | 1600 | -90 | 94 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1505 |  | 1600 | -95 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1482 |  | 1600 | -118 | 93 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1482 |  | 1600 | -118 | 93 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1482 |  | 1600 | -118 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1482 |  | 1600 | -118 | 93 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1391 |  | 1600 | -209 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1357 |  | 1600 | -243 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1308 |  | 1600 | -292 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1304 |  | 1601 | -297 | 81 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Lacu Sarat - Smardan [DIR] [RO] | RSMIR41 _RLACS41 _1:line | -1160 |  | -1600 | -440 | 73 | []

## 2130Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2473
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1479 | 1600 | 1600 | -121 | 92 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1468 | 1600 | 1600 | -132 | 92 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1437 | 1600 | 1600 | -163 | 90 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1410 | 1600 | 1600 | -190 | 88 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1402 | 1600 | 1600 | -198 | 88 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1395 | 1600 | 1600 | -205 | 87 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1389 | 1600 | 1600 | -211 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1389 | 1600 | 1600 | -211 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1376 | 1600 | 1600 | -224 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1304 | 1600 | 1600 | -296 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1304 | 1600 | 1600 | -296 | 82 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1304 | 1600 | 1600 | -296 | 82 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1300 | 1601 | 1601 | -301 | 81 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1300 | 1601 | 1601 | -301 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1297 | 1600 | 1600 | -303 | 81 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Smardan - Isaccea c1 [DIR] [RO] | RSMIR41 _RIS1A41 _1:line | 1129 | 1600 | 1600 | -471 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2473
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1479 |  | 1600 | -121 | 92 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1468 |  | 1600 | -132 | 92 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1437 |  | 1600 | -163 | 90 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1410 |  | 1600 | -190 | 88 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1402 |  | 1600 | -198 | 88 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1395 |  | 1600 | -205 | 87 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1389 |  | 1600 | -211 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1389 |  | 1600 | -211 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1376 |  | 1600 | -224 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1304 |  | 1600 | -296 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1304 |  | 1600 | -296 | 82 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1304 |  | 1600 | -296 | 82 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1300 |  | 1601 | -301 | 81 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1300 |  | 1601 | -301 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1297 |  | 1600 | -303 | 81 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Smardan - Isaccea c1 [DIR] [RO] | RSMIR41 _RIS1A41 _1:line | 1129 |  | 1600 | -471 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3083
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1596 | 1600 | 1600 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1475 | 1600 | 1600 | -125 | 92 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1466 | 1600 | 1600 | -134 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1431 | 1600 | 1600 | -169 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1430 | 1600 | 1600 | -170 | 89 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1399 | 1600 | 1600 | -201 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1390 | 1600 | 1600 | -210 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1385 | 1600 | 1600 | -215 | 87 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1385 | 1600 | 1600 | -215 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1374 | 1600 | 1600 | -226 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -840 | -999 | -999 | -159 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1298 | 1600 | 1600 | -302 | 81 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1297 | 1600 | 1600 | -303 | 81 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Smardan - Isaccea c1 [DIR] [RO] | RSMIR41 _RIS1A41 _1:line | 1238 | 1600 | 1600 | -362 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1230 | 1601 | 1601 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1230 | 1601 | 1601 | -371 | 77 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1294 | -1836 | -1836 | -542 | 71 | []

## 2230Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3083
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1596 |  | 1600 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 |  | 1600 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 |  | 1600 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1475 |  | 1600 | -125 | 92 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1466 |  | 1600 | -134 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1431 |  | 1600 | -169 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1430 |  | 1600 | -170 | 89 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1399 |  | 1600 | -201 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1390 |  | 1600 | -210 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1385 |  | 1600 | -215 | 87 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1385 |  | 1600 | -215 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1374 |  | 1600 | -226 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -840 |  | -999 | -159 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1298 |  | 1600 | -302 | 81 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [OPP] [RO] | RGIAL11 _RCERN41 _1:line | 1297 |  | 1600 | -303 | 81 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Smardan - Isaccea c1 [DIR] [RO] | RSMIR41 _RIS1A41 _1:line | 1238 |  | 1600 | -362 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1235 |  | 1600 | -365 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1235 |  | 1600 | -365 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1230 |  | 1601 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1230 |  | 1601 | -371 | 77 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1294 |  | -1836 | -542 | 71 | []

## 2330Preventive
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3377
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1587 | 1601 | 1601 | -14 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1587 | 1601 | 1601 | -14 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1476 | 1600 | 1600 | -124 | 92 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1472 | 1600 | 1600 | -128 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1433 | 1600 | 1600 | -167 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1429 | 1600 | 1600 | -171 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -889 | -999 | -999 | -110 | 89 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1392 | 1600 | 1600 | -208 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1391 | 1600 | 1600 | -209 | 87 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1379 | 1600 | 1600 | -221 | 86 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1379 | 1600 | 1600 | -221 | 86 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1363 | 1600 | 1600 | -237 | 85 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1546 | -1836 | -1836 | -290 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1528 | -1836 | -1836 | -308 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1515 | -1836 | -1836 | -321 | 82 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1515 | -1836 | -1836 | -321 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1307 | 1600 | 1600 | -293 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1307 | 1600 | 1600 | -293 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1303 | 1601 | 1601 | -298 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1303 | 1601 | 1601 | -298 | 81 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Smardan - Isaccea c1 [DIR] [RO] | RSMIR41 _RIS1A41 _1:line | 1299 | 1600 | 1600 | -301 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1290 | 1600 | 1600 | -310 | 81 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1286 | 1600 | 1600 | -314 | 80 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1422 | -1836 | -1836 | -414 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1403 | -1836 | -1836 | -433 | 76 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1396 | -1836 | -1836 | -440 | 76 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1394 | -1836 | -1836 | -442 | 76 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1388 | -1836 | -1836 | -448 | 76 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1356 | -1836 | -1836 | -480 | 74 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Lacu Sarat - Smardan [OPP] [RO] | RSMIR41 _RLACS41 _1:line | -1126 | -1600 | -1600 | -474 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2023-12-14 08:01
Business day: | 14.12.2023
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3377
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1591 |  | 1600 | -9 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1591 |  | 1600 | -9 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1587 |  | 1601 | -14 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1587 |  | 1601 | -14 | 99 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1476 |  | 1600 | -124 | 92 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1472 |  | 1600 | -128 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1433 |  | 1600 | -167 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1429 |  | 1600 | -171 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -889 |  | -999 | -110 | 89 | []
RO_CO_00020 | N-1 Bucuresti Sud - Domnesti | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1392 |  | 1600 | -208 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1391 |  | 1600 | -209 | 87 | []
BC | Base Case | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1379 |  | 1600 | -221 | 86 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1379 |  | 1600 | -221 | 86 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1363 |  | 1600 | -237 | 85 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1546 |  | -1836 | -290 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1528 |  | -1836 | -308 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1515 |  | -1836 | -321 | 82 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1515 |  | -1836 | -321 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1307 |  | 1600 | -293 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1307 |  | 1600 | -293 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1303 |  | 1601 | -298 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1303 |  | 1601 | -298 | 81 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Smardan - Isaccea c1 [DIR] [RO] | RSMIR41 _RIS1A41 _1:line | 1299 |  | 1600 | -301 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1290 |  | 1600 | -310 | 81 | []
BC | Base Case | [RO-RO] Cernavoda - Gura Ialomitei c1 [DIR] [RO] | RGIAL11 _RCERN41 _1:line | 1286 |  | 1600 | -314 | 80 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1422 |  | -1836 | -414 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1403 |  | -1836 | -433 | 76 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1396 |  | -1836 | -440 | 76 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1394 |  | -1836 | -442 | 76 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1388 |  | -1836 | -448 | 76 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1356 |  | -1836 | -480 | 74 | []
RO_CO_00014 | N-1 Lacu Sarat - Isaccea | [RO-RO] Lacu Sarat - Smardan [OPP] [RO] | RSMIR41 _RLACS41 _1:line | -1126 |  | -1600 | -474 | 70 | []