## 1230Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2790
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1597 | 1600 | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1584 | 1600 | 1600 | -16 | 99 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1470 | 1600 | 1600 | -130 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1469 | 1600 | 1600 | -131 | 92 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1386 | 1600 | 1600 | -214 | 87 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1379 | 1600 | 1600 | -221 | 86 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1363 | 1600 | 1600 | -237 | 85 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1322 | 1600 | 1600 | -278 | 83 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1313 | 1600 | 1600 | -287 | 82 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1309 | 1600 | 1600 | -291 | 82 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 | 1600 | 1600 | -299 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 | 1600 | 1600 | -304 | 81 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 | 1600 | 1600 | -307 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 | 1600 | 1600 | -316 | 80 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 | 1600 | 1600 | -317 | 80 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1280 | 1600 | 1600 | -320 | 80 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1267 | 1600 | 1600 | -333 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1256 | 1600 | 1600 | -344 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1238 | 1600 | 1600 | -362 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1235 | 1600 | 1600 | -365 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1234 | 1600 | 1600 | -366 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1233 | 1600 | 1600 | -367 | 77 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 | 1600 | 1600 | -380 | 76 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 | 1600 | 1600 | -380 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1201 | 1600 | 1600 | -399 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1179 | 1600 | 1600 | -421 | 74 | []

## 1230Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2790
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1597 |  | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1584 |  | 1600 | -16 | 99 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1470 |  | 1600 | -130 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1469 |  | 1600 | -131 | 92 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1386 |  | 1600 | -214 | 87 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1379 |  | 1600 | -221 | 86 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1363 |  | 1600 | -237 | 85 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1322 |  | 1600 | -278 | 83 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1313 |  | 1600 | -287 | 82 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1309 |  | 1600 | -291 | 82 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 |  | 1600 | -299 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 |  | 1600 | -304 | 81 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 |  | 1600 | -307 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 |  | 1600 | -316 | 80 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 |  | 1600 | -317 | 80 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1280 |  | 1600 | -320 | 80 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1267 |  | 1600 | -333 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1256 |  | 1600 | -344 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1238 |  | 1600 | -362 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1235 |  | 1600 | -365 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1234 |  | 1600 | -366 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1233 |  | 1600 | -367 | 77 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 |  | 1600 | -380 | 76 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 |  | 1600 | -380 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1201 |  | 1600 | -399 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1179 |  | 1600 | -421 | 74 | []

## 1330Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2814
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1592 | 1600 | 1600 | -8 | 100 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1591 | 1600 | 1600 | -9 | 99 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1487 | 1600 | 1600 | -113 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1466 | 1600 | 1600 | -134 | 92 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1439 | 1600 | 1600 | -161 | 90 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1419 | 1600 | 1600 | -181 | 89 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1390 | 1600 | 1600 | -210 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1348 | 1600 | 1600 | -252 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 | 1600 | 1600 | -276 | 83 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1312 | 1600 | 1600 | -288 | 82 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1310 | 1600 | 1600 | -290 | 82 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1306 | 1600 | 1600 | -294 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1306 | 1600 | 1600 | -294 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 | 1600 | 1600 | -298 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 | 1600 | 1600 | -299 | 81 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 | 1600 | 1600 | -307 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 | 1600 | 1600 | -315 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 | 1600 | 1600 | -316 | 80 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1281 | 1600 | 1600 | -319 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1281 | 1600 | 1600 | -319 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 | 1600 | 1600 | -328 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1267 | 1600 | 1600 | -333 | 79 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1251 | 1600 | 1600 | -349 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1251 | 1600 | 1600 | -349 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1251 | 1600 | 1600 | -349 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1250 | 1600 | 1600 | -350 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1249 | 1600 | 1600 | -351 | 78 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 | 1600 | 1600 | -360 | 77 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1232 | 1600 | 1600 | -368 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 | 1600 | 1600 | -370 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1206 | 1600 | 1600 | -394 | 75 | []

## 1330Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2814
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1592 |  | 1600 | -8 | 100 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1591 |  | 1600 | -9 | 99 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1487 |  | 1600 | -113 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1466 |  | 1600 | -134 | 92 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1439 |  | 1600 | -161 | 90 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1419 |  | 1600 | -181 | 89 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1390 |  | 1600 | -210 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1348 |  | 1600 | -252 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 |  | 1600 | -276 | 83 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1312 |  | 1600 | -288 | 82 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1310 |  | 1600 | -290 | 82 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1306 |  | 1600 | -294 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1306 |  | 1600 | -294 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 |  | 1600 | -298 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 |  | 1600 | -299 | 81 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 |  | 1600 | -307 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 |  | 1600 | -315 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 |  | 1600 | -316 | 80 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1281 |  | 1600 | -319 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1281 |  | 1600 | -319 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 |  | 1600 | -328 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1267 |  | 1600 | -333 | 79 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1251 |  | 1600 | -349 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1251 |  | 1600 | -349 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1251 |  | 1600 | -349 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1250 |  | 1600 | -350 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1249 |  | 1600 | -351 | 78 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 |  | 1600 | -360 | 77 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1232 |  | 1600 | -368 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 |  | 1600 | -370 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 |  | 1600 | -385 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1206 |  | 1600 | -394 | 75 | []

## 1430Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2789
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1599 | 1600 | 1600 | -1 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1598 | 1600 | 1600 | -2 | 100 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1506 | 1600 | 1600 | -94 | 94 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1499 | 1600 | 1600 | -101 | 94 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1478 | 1600 | 1600 | -122 | 92 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1470 | 1600 | 1600 | -130 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1440 | 1600 | 1600 | -160 | 90 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1395 | 1600 | 1600 | -205 | 87 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1385 | 1600 | 1600 | -215 | 87 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1375 | 1600 | 1600 | -225 | 86 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1346 | 1600 | 1600 | -254 | 84 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1339 | 1600 | 1600 | -261 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1338 | 1600 | 1600 | -262 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1330 | 1600 | 1600 | -270 | 83 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1328 | 1600 | 1600 | -272 | 83 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 | 1600 | 1600 | -276 | 83 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1323 | 1600 | 1600 | -277 | 83 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1321 | 1600 | 1600 | -279 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1308 | 1600 | 1600 | -292 | 82 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 | 1600 | 1600 | -299 | 81 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 | 1600 | 1600 | -304 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 | 1600 | 1600 | -304 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1291 | 1600 | 1600 | -309 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1289 | 1600 | 1600 | -311 | 81 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1289 | 1600 | 1600 | -311 | 81 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1288 | 1600 | 1600 | -312 | 81 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1286 | 1600 | 1600 | -314 | 80 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 | 1600 | 1600 | -322 | 80 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1276 | 1600 | 1600 | -324 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 | 1600 | 1600 | -328 | 79 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1272 | 1600 | 1600 | -328 | 79 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1265 | 1600 | 1600 | -335 | 79 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1234 | 1600 | 1600 | -366 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1131 | 1600 | 1600 | -469 | 71 | []

## 1430Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2789
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1599 |  | 1600 | -1 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1598 |  | 1600 | -2 | 100 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1506 |  | 1600 | -94 | 94 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1499 |  | 1600 | -101 | 94 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1478 |  | 1600 | -122 | 92 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1470 |  | 1600 | -130 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1440 |  | 1600 | -160 | 90 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1395 |  | 1600 | -205 | 87 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1385 |  | 1600 | -215 | 87 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1375 |  | 1600 | -225 | 86 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1346 |  | 1600 | -254 | 84 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1339 |  | 1600 | -261 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1338 |  | 1600 | -262 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1330 |  | 1600 | -270 | 83 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1328 |  | 1600 | -272 | 83 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 |  | 1600 | -276 | 83 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1323 |  | 1600 | -277 | 83 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1321 |  | 1600 | -279 | 83 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1308 |  | 1600 | -292 | 82 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 |  | 1600 | -299 | 81 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 |  | 1600 | -304 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 |  | 1600 | -304 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1291 |  | 1600 | -309 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1289 |  | 1600 | -311 | 81 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1289 |  | 1600 | -311 | 81 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1288 |  | 1600 | -312 | 81 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1286 |  | 1600 | -314 | 80 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 |  | 1600 | -322 | 80 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1276 |  | 1600 | -324 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 |  | 1600 | -328 | 79 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1272 |  | 1600 | -328 | 79 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1265 |  | 1600 | -335 | 79 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1234 |  | 1600 | -366 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1131 |  | 1600 | -469 | 71 | []

## 1530Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2800
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1594 | 1600 | 1600 | -6 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1585 | 1600 | 1600 | -15 | 99 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1490 | 1600 | 1600 | -110 | 93 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1464 | 1600 | 1600 | -136 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1460 | 1600 | 1600 | -140 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1446 | 1600 | 1600 | -154 | 90 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1434 | 1600 | 1600 | -166 | 90 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1386 | 1600 | 1600 | -214 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1385 | 1600 | 1600 | -215 | 87 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1379 | 1600 | 1600 | -221 | 86 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1356 | 1600 | 1600 | -244 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 | 1600 | 1600 | -256 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1339 | 1600 | 1600 | -261 | 84 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1329 | 1600 | 1600 | -271 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1323 | 1600 | 1600 | -277 | 83 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1320 | 1600 | 1600 | -280 | 83 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1318 | 1600 | 1600 | -282 | 82 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1317 | 1600 | 1600 | -283 | 82 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 | 1600 | 1600 | -297 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 | 1600 | 1600 | -304 | 81 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 | 1600 | 1600 | -305 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 | 1600 | 1600 | -307 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1288 | 1600 | 1600 | -312 | 80 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 | 1600 | 1600 | -315 | 80 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 | 1600 | 1600 | -315 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 | 1600 | 1600 | -315 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 | 1600 | 1600 | -316 | 80 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 | 1600 | 1600 | -316 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 | 1600 | 1600 | -316 | 80 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 | 1600 | 1600 | -317 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1232 | 1600 | 1600 | -368 | 77 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | -1093 | 1517 | 1517 | -424 | 72 | []

## 1530Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2800
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1594 |  | 1600 | -6 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1585 |  | 1600 | -15 | 99 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1490 |  | 1600 | -110 | 93 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1464 |  | 1600 | -136 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1460 |  | 1600 | -140 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1446 |  | 1600 | -154 | 90 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1434 |  | 1600 | -166 | 90 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1386 |  | 1600 | -214 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1385 |  | 1600 | -215 | 87 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1379 |  | 1600 | -221 | 86 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1356 |  | 1600 | -244 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 |  | 1600 | -256 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1339 |  | 1600 | -261 | 84 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1329 |  | 1600 | -271 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1323 |  | 1600 | -277 | 83 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1320 |  | 1600 | -280 | 83 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1318 |  | 1600 | -282 | 82 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1317 |  | 1600 | -283 | 82 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 |  | 1600 | -297 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 |  | 1600 | -304 | 81 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 |  | 1600 | -305 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 |  | 1600 | -307 | 81 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1288 |  | 1600 | -312 | 80 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 |  | 1600 | -315 | 80 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 |  | 1600 | -315 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 |  | 1600 | -315 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 |  | 1600 | -316 | 80 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 |  | 1600 | -316 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 |  | 1600 | -316 | 80 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 |  | 1600 | -317 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 |  | 1600 | -334 | 79 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 |  | 1600 | -334 | 79 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1258 |  | 1600 | -342 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1258 |  | 1600 | -342 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1253 |  | 1600 | -347 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1232 |  | 1600 | -368 | 77 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | -1093 |  | 1517 | -424 | 72 | []

## 1630Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2738
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1592 | 1600 | 1600 | -8 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1556 | 1600 | 1600 | -44 | 97 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1453 | 1600 | 1600 | -147 | 91 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1406 | 1600 | 1600 | -194 | 88 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1389 | 1600 | 1600 | -211 | 87 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1389 | 1600 | 1600 | -211 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1369 | 1600 | 1600 | -231 | 86 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1351 | 1600 | 1600 | -249 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 | 1600 | 1600 | -256 | 84 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1313 | 1600 | 1600 | -287 | 82 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1311 | 1600 | 1600 | -289 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1305 | 1600 | 1600 | -295 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1304 | 1600 | 1600 | -296 | 81 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 | 1600 | 1600 | -298 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1291 | 1600 | 1600 | -309 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 | 1600 | 1600 | -315 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 | 1600 | 1600 | -315 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 | 1600 | 1600 | -328 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1270 | 1600 | 1600 | -330 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 | 1600 | 1600 | -332 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1238 | 1600 | 1600 | -362 | 77 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1235 | 1600 | 1600 | -365 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1234 | 1600 | 1600 | -366 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1233 | 1600 | 1600 | -367 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 | 1600 | 1600 | -369 | 77 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1230 | 1600 | 1600 | -370 | 77 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1225 | 1600 | 1600 | -375 | 77 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1218 | 1600 | 1600 | -382 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []

## 1630Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2738
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1592 |  | 1600 | -8 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1556 |  | 1600 | -44 | 97 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1453 |  | 1600 | -147 | 91 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1406 |  | 1600 | -194 | 88 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1389 |  | 1600 | -211 | 87 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1389 |  | 1600 | -211 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1369 |  | 1600 | -231 | 86 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1351 |  | 1600 | -249 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 |  | 1600 | -256 | 84 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1313 |  | 1600 | -287 | 82 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1311 |  | 1600 | -289 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1305 |  | 1600 | -295 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1304 |  | 1600 | -296 | 81 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 |  | 1600 | -298 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1291 |  | 1600 | -309 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 |  | 1600 | -315 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 |  | 1600 | -315 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 |  | 1600 | -328 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1270 |  | 1600 | -330 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 |  | 1600 | -332 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1238 |  | 1600 | -362 | 77 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1235 |  | 1600 | -365 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1234 |  | 1600 | -366 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1233 |  | 1600 | -367 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 |  | 1600 | -369 | 77 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1230 |  | 1600 | -370 | 77 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1225 |  | 1600 | -375 | 77 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1218 |  | 1600 | -382 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []

## 1730Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2822
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 | 1600 | 1600 | -5 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1576 | 1600 | 1600 | -24 | 98 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1471 | 1600 | 1600 | -129 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1442 | 1600 | 1600 | -158 | 90 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1420 | 1600 | 1600 | -180 | 89 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1401 | 1600 | 1600 | -199 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1397 | 1600 | 1600 | -203 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1365 | 1600 | 1600 | -235 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1335 | 1600 | 1600 | -265 | 83 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1330 | 1600 | 1600 | -270 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1319 | 1600 | 1600 | -281 | 82 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1316 | 1600 | 1600 | -284 | 82 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 | 1600 | 1600 | -290 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 | 1600 | 1600 | -290 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 | 1600 | 1600 | -304 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 | 1600 | 1600 | -307 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1275 | 1600 | 1600 | -325 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 | 1600 | 1600 | -328 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 | 1600 | 1600 | -332 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 | 1600 | 1600 | -332 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 | 1600 | 1600 | -370 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1223 | 1600 | 1600 | -377 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1218 | 1600 | 1600 | -382 | 76 | []

## 1730Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2822
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 |  | 1600 | -5 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1576 |  | 1600 | -24 | 98 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1471 |  | 1600 | -129 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1442 |  | 1600 | -158 | 90 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1420 |  | 1600 | -180 | 89 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1401 |  | 1600 | -199 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1397 |  | 1600 | -203 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1365 |  | 1600 | -235 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1335 |  | 1600 | -265 | 83 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1330 |  | 1600 | -270 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1319 |  | 1600 | -281 | 82 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1316 |  | 1600 | -284 | 82 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 |  | 1600 | -290 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 |  | 1600 | -290 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 |  | 1600 | -304 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 |  | 1600 | -307 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1275 |  | 1600 | -325 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 |  | 1600 | -328 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 |  | 1600 | -332 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 |  | 1600 | -332 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1266 |  | 1600 | -334 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1262 |  | 1600 | -338 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 |  | 1600 | -370 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1223 |  | 1600 | -377 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1218 |  | 1600 | -382 | 76 | []

## 1830Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2863
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1587 | 1600 | 1600 | -13 | 99 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1566 | 1600 | 1600 | -34 | 98 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1478 | 1600 | 1600 | -122 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1444 | 1600 | 1600 | -156 | 90 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1407 | 1600 | 1600 | -193 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1395 | 1600 | 1600 | -205 | 87 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1391 | 1600 | 1600 | -209 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1352 | 1600 | 1600 | -248 | 84 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 | 1600 | 1600 | -276 | 83 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1322 | 1600 | 1600 | -278 | 83 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 | 1600 | 1600 | -290 | 82 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1306 | 1600 | 1600 | -294 | 82 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 | 1600 | 1600 | -297 | 81 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1299 | 1600 | 1600 | -301 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1292 | 1600 | 1600 | -308 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 | 1600 | 1600 | -316 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 | 1600 | 1600 | -322 | 80 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 | 1600 | 1600 | -322 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1265 | 1600 | 1600 | -335 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1257 | 1600 | 1600 | -343 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1225 | 1600 | 1600 | -375 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 | 1600 | 1600 | -380 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 76 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | -1079 | 1517 | 1517 | -438 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2863
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1587 |  | 1600 | -13 | 99 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1566 |  | 1600 | -34 | 98 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1478 |  | 1600 | -122 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1444 |  | 1600 | -156 | 90 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1407 |  | 1600 | -193 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1395 |  | 1600 | -205 | 87 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1391 |  | 1600 | -209 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1352 |  | 1600 | -248 | 84 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 |  | 1600 | -276 | 83 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1322 |  | 1600 | -278 | 83 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 |  | 1600 | -290 | 82 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1306 |  | 1600 | -294 | 82 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 |  | 1600 | -297 | 81 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1299 |  | 1600 | -301 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1292 |  | 1600 | -308 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 |  | 1600 | -316 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 |  | 1600 | -322 | 80 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 |  | 1600 | -322 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1265 |  | 1600 | -335 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1260 |  | 1600 | -340 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1257 |  | 1600 | -343 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1255 |  | 1600 | -345 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1225 |  | 1600 | -375 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 |  | 1600 | -380 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1219 |  | 1600 | -381 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 76 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | -1079 |  | 1517 | -438 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2876
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1596 | 1600 | 1600 | -4 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1550 | 1600 | 1600 | -50 | 97 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1463 | 1600 | 1600 | -137 | 91 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1444 | 1600 | 1600 | -156 | 90 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1388 | 1600 | 1600 | -212 | 87 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1385 | 1600 | 1600 | -215 | 87 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1373 | 1600 | 1600 | -227 | 86 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1340 | 1600 | 1600 | -260 | 84 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 | 1600 | 1600 | -290 | 82 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 | 1600 | 1600 | -290 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 | 1600 | 1600 | -300 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1291 | 1600 | 1600 | -309 | 81 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1288 | 1600 | 1600 | -312 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 | 1600 | 1600 | -317 | 80 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1271 | 1600 | 1600 | -329 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1267 | 1600 | 1600 | -333 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1246 | 1600 | 1600 | -354 | 78 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 | 1600 | 1600 | -360 | 77 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 | 1600 | 1600 | -360 | 77 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1234 | 1600 | 1600 | -366 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 | 1600 | 1600 | -380 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1194 | 1600 | 1600 | -406 | 75 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | -1115 | 1517 | 1517 | -402 | 74 | []

## 1930Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2876
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1596 |  | 1600 | -4 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1550 |  | 1600 | -50 | 97 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1463 |  | 1600 | -137 | 91 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1444 |  | 1600 | -156 | 90 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1388 |  | 1600 | -212 | 87 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1385 |  | 1600 | -215 | 87 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1373 |  | 1600 | -227 | 86 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1340 |  | 1600 | -260 | 84 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 |  | 1600 | -290 | 82 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 |  | 1600 | -290 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 |  | 1600 | -300 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1291 |  | 1600 | -309 | 81 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1288 |  | 1600 | -312 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 |  | 1600 | -317 | 80 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1271 |  | 1600 | -329 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1267 |  | 1600 | -333 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 |  | 1600 | -334 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1246 |  | 1600 | -354 | 78 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1242 |  | 1600 | -358 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 |  | 1600 | -360 | 77 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 |  | 1600 | -360 | 77 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1234 |  | 1600 | -366 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 |  | 1600 | -380 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 |  | 1600 | -385 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1194 |  | 1600 | -406 | 75 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [TR-GR] 400 kV Babaeski-Nea Santa | XNS_BA11_GNSANT13_1:line | -1115 |  | 1517 | -402 | 74 | []

## 2030Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2752
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 | 1600 | 1600 | -5 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1528 | 1600 | 1600 | -72 | 96 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1458 | 1600 | 1600 | -142 | 91 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1448 | 1600 | 1600 | -152 | 91 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1387 | 1600 | 1600 | -213 | 87 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1384 | 1600 | 1600 | -216 | 86 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1353 | 1600 | 1600 | -247 | 85 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1317 | 1600 | 1600 | -283 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 | 1600 | 1600 | -298 | 81 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 | 1600 | 1600 | -300 | 81 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1286 | 1600 | 1600 | -314 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1275 | 1600 | 1600 | -325 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1256 | 1600 | 1600 | -344 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1233 | 1600 | 1600 | -367 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 | 1600 | 1600 | -369 | 77 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 | 1600 | 1600 | -369 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 | 1600 | 1600 | -369 | 77 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 | 1600 | 1600 | -370 | 77 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 | 1600 | 1600 | -370 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1209 | 1600 | 1600 | -391 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1207 | 1600 | 1600 | -393 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1206 | 1600 | 1600 | -394 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1183 | 1600 | 1600 | -417 | 74 | []

## 2030Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2752
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 |  | 1600 | -5 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1528 |  | 1600 | -72 | 96 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1458 |  | 1600 | -142 | 91 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1448 |  | 1600 | -152 | 91 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1387 |  | 1600 | -213 | 87 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1384 |  | 1600 | -216 | 86 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1353 |  | 1600 | -247 | 85 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1317 |  | 1600 | -283 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 |  | 1600 | -298 | 81 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 |  | 1600 | -300 | 81 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1286 |  | 1600 | -314 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1277 |  | 1600 | -323 | 80 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1275 |  | 1600 | -325 | 80 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1258 |  | 1600 | -342 | 79 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1256 |  | 1600 | -344 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1233 |  | 1600 | -367 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 |  | 1600 | -369 | 77 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 |  | 1600 | -369 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 |  | 1600 | -369 | 77 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 |  | 1600 | -370 | 77 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 |  | 1600 | -370 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1219 |  | 1600 | -381 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1219 |  | 1600 | -381 | 76 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1215 |  | 1600 | -385 | 76 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1209 |  | 1600 | -391 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1207 |  | 1600 | -393 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1206 |  | 1600 | -394 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1183 |  | 1600 | -417 | 74 | []

## 2130Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2509
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1598 | 1600 | 1600 | -2 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1485 | 1600 | 1600 | -115 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1447 | 1600 | 1600 | -153 | 90 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1366 | 1600 | 1600 | -234 | 85 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1362 | 1600 | 1600 | -238 | 85 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1334 | 1600 | 1600 | -266 | 83 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1314 | 1600 | 1600 | -286 | 82 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1307 | 1600 | 1600 | -293 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1304 | 1600 | 1600 | -296 | 82 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 | 1600 | 1600 | -302 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 | 1600 | 1600 | -332 | 79 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1247 | 1600 | 1600 | -353 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1243 | 1600 | 1600 | -357 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 | 1600 | 1600 | -380 | 76 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1213 | 1600 | 1600 | -387 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1213 | 1600 | 1600 | -387 | 76 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1213 | 1600 | 1600 | -387 | 76 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1212 | 1600 | 1600 | -388 | 76 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1210 | 1600 | 1600 | -390 | 76 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1210 | 1600 | 1600 | -390 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1206 | 1600 | 1600 | -394 | 75 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1200 | 1600 | 1600 | -400 | 75 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1190 | 1600 | 1600 | -410 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1188 | 1600 | 1600 | -412 | 74 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1170 | 1600 | 1600 | -430 | 73 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1163 | 1600 | 1600 | -437 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1160 | 1600 | 1600 | -440 | 72 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1158 | 1600 | 1600 | -442 | 72 | []

## 2130Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2509
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1598 |  | 1600 | -2 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1485 |  | 1600 | -115 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1447 |  | 1600 | -153 | 90 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1366 |  | 1600 | -234 | 85 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1362 |  | 1600 | -238 | 85 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1334 |  | 1600 | -266 | 83 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1314 |  | 1600 | -286 | 82 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1307 |  | 1600 | -293 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1304 |  | 1600 | -296 | 82 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 |  | 1600 | -302 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 |  | 1600 | -332 | 79 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1247 |  | 1600 | -353 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1243 |  | 1600 | -357 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 |  | 1600 | -380 | 76 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1213 |  | 1600 | -387 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1213 |  | 1600 | -387 | 76 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1213 |  | 1600 | -387 | 76 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1212 |  | 1600 | -388 | 76 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1210 |  | 1600 | -390 | 76 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1210 |  | 1600 | -390 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1206 |  | 1600 | -394 | 75 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1200 |  | 1600 | -400 | 75 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1190 |  | 1600 | -410 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1188 |  | 1600 | -412 | 74 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1170 |  | 1600 | -430 | 73 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1163 |  | 1600 | -437 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1160 |  | 1600 | -440 | 72 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1158 |  | 1600 | -442 | 72 | []

## 2230Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2460
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1597 | 1600 | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1479 | 1600 | 1600 | -121 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1450 | 1600 | 1600 | -150 | 91 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1338 | 1600 | 1600 | -262 | 84 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1334 | 1600 | 1600 | -266 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1327 | 1600 | 1600 | -273 | 83 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 | 1600 | 1600 | -302 | 81 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1238 | 1600 | 1600 | -362 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1225 | 1600 | 1600 | -375 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1225 | 1600 | 1600 | -375 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 | 1600 | 1600 | -380 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1210 | 1600 | 1600 | -390 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 76 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1204 | 1600 | 1600 | -396 | 75 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1201 | 1600 | 1600 | -399 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1200 | 1600 | 1600 | -400 | 75 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1194 | 1600 | 1600 | -406 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1193 | 1600 | 1600 | -407 | 75 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1191 | 1600 | 1600 | -409 | 74 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1191 | 1600 | 1600 | -409 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1190 | 1600 | 1600 | -410 | 74 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1190 | 1600 | 1600 | -410 | 74 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1188 | 1600 | 1600 | -412 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1179 | 1600 | 1600 | -421 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1174 | 1600 | 1600 | -426 | 73 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1174 | 1600 | 1600 | -426 | 73 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1172 | 1600 | 1600 | -428 | 73 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1170 | 1600 | 1600 | -430 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 | 1600 | 1600 | -455 | 72 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1137 | 1600 | 1600 | -463 | 71 | []

## 2230Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2460
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1597 |  | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1479 |  | 1600 | -121 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1450 |  | 1600 | -150 | 91 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1338 |  | 1600 | -262 | 84 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1334 |  | 1600 | -266 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1327 |  | 1600 | -273 | 83 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 |  | 1600 | -302 | 81 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1277 |  | 1600 | -323 | 80 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 |  | 1600 | -334 | 79 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1238 |  | 1600 | -362 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1225 |  | 1600 | -375 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1225 |  | 1600 | -375 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 |  | 1600 | -380 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1210 |  | 1600 | -390 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 76 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1204 |  | 1600 | -396 | 75 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1201 |  | 1600 | -399 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1200 |  | 1600 | -400 | 75 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1194 |  | 1600 | -406 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1193 |  | 1600 | -407 | 75 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1191 |  | 1600 | -409 | 74 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1191 |  | 1600 | -409 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1190 |  | 1600 | -410 | 74 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1190 |  | 1600 | -410 | 74 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1188 |  | 1600 | -412 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1179 |  | 1600 | -421 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1174 |  | 1600 | -426 | 73 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1174 |  | 1600 | -426 | 73 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1172 |  | 1600 | -428 | 73 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1170 |  | 1600 | -430 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 |  | 1600 | -455 | 72 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1137 |  | 1600 | -463 | 71 | []

## 2330Preventive
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2441
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1591 | 1600 | 1600 | -9 | 99 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1487 | 1600 | 1600 | -113 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1447 | 1600 | 1600 | -153 | 90 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1389 | 1600 | 1600 | -211 | 87 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1345 | 1600 | 1600 | -255 | 84 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1337 | 1600 | 1600 | -263 | 84 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1315 | 1600 | 1600 | -285 | 82 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1286 | 1600 | 1600 | -314 | 80 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1279 | 1600 | 1600 | -321 | 80 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1270 | 1600 | 1600 | -330 | 79 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1257 | 1600 | 1600 | -343 | 79 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 | 1600 | 1600 | -369 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1226 | 1600 | 1600 | -374 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1226 | 1600 | 1600 | -374 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1223 | 1600 | 1600 | -377 | 76 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 76 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1204 | 1600 | 1600 | -396 | 75 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1198 | 1600 | 1600 | -402 | 75 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1198 | 1600 | 1600 | -402 | 75 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1197 | 1600 | 1600 | -403 | 75 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1194 | 1600 | 1600 | -406 | 75 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1194 | 1600 | 1600 | -406 | 75 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1194 | 1600 | 1600 | -406 | 75 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1192 | 1600 | 1600 | -408 | 75 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1190 | 1600 | 1600 | -410 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1189 | 1600 | 1600 | -411 | 74 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1185 | 1600 | 1600 | -415 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1182 | 1600 | 1600 | -418 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1175 | 1600 | 1600 | -425 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 | 1600 | 1600 | -455 | 72 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1143 | 1600 | 1600 | -457 | 71 | []

## 2330Curative
Detailed results
Generated at: | 2023-12-31 07:53
Business day: | 31.12.2023
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2441
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1591 |  | 1600 | -9 | 99 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1487 |  | 1600 | -113 | 93 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1447 |  | 1600 | -153 | 90 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1389 |  | 1600 | -211 | 87 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1345 |  | 1600 | -255 | 84 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1337 |  | 1600 | -263 | 84 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1315 |  | 1600 | -285 | 82 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1286 |  | 1600 | -314 | 80 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1279 |  | 1600 | -321 | 80 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1270 |  | 1600 | -330 | 79 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1257 |  | 1600 | -343 | 79 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1231 |  | 1600 | -369 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1226 |  | 1600 | -374 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1226 |  | 1600 | -374 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1223 |  | 1600 | -377 | 76 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 76 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1204 |  | 1600 | -396 | 75 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1198 |  | 1600 | -402 | 75 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1198 |  | 1600 | -402 | 75 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1197 |  | 1600 | -403 | 75 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1194 |  | 1600 | -406 | 75 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1194 |  | 1600 | -406 | 75 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1194 |  | 1600 | -406 | 75 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1192 |  | 1600 | -408 | 75 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1190 |  | 1600 | -410 | 74 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1189 |  | 1600 | -411 | 74 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS11_1:line | -1185 |  | 1600 | -415 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1182 |  | 1600 | -418 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1175 |  | 1600 | -425 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 |  | 1600 | -455 | 72 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1143 |  | 1600 | -457 | 71 | []