## 1230Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2767
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1592 | 1601 | 1601 | -9 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1592 | 1601 | 1601 | -9 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1272 | 1600 | 1600 | -328 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1238 | 1600 | 1600 | -362 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1236 | 1600 | 1600 | -364 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1225 | 1600 | 1600 | -375 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -925 | -1248 | -1248 | -324 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -923 | -1248 | -1248 | -325 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -919 | -1248 | -1248 | -329 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -918 | -1248 | -1248 | -331 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1176 | 1601 | 1601 | -425 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1176 | 1601 | 1601 | -425 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -912 | -1248 | -1248 | -336 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -912 | -1248 | -1248 | -337 | 73 | []

## 1230Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2767
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 |  | 1600 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1597 |  | 1600 | -3 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1592 |  | 1601 | -9 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1592 |  | 1601 | -9 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1272 |  | 1600 | -328 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1238 |  | 1600 | -362 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1236 |  | 1600 | -364 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1225 |  | 1600 | -375 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -925 |  | -1248 | -324 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -923 |  | -1248 | -325 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1182 |  | 1600 | -418 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1182 |  | 1600 | -418 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -919 |  | -1248 | -329 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -918 |  | -1248 | -331 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1176 |  | 1601 | -425 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1176 |  | 1601 | -425 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -912 |  | -1248 | -336 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -912 |  | -1248 | -337 | 73 | []

## 1330Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2694
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1279 | 1600 | 1600 | -321 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -978 | -1248 | -1248 | -270 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -977 | -1248 | -1248 | -272 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -973 | -1248 | -1248 | -275 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -973 | -1248 | -1248 | -276 | 78 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1243 | 1600 | 1600 | -357 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -968 | -1248 | -1248 | -281 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -967 | -1248 | -1248 | -282 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1229 | 1600 | 1600 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1162 | 1600 | 1600 | -438 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1162 | 1600 | 1600 | -438 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1156 | 1601 | 1601 | -445 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1156 | 1601 | 1601 | -445 | 72 | []

## 1330Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2694
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 |  | 1600 | 0 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 |  | 1600 | 0 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 |  | 1601 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 |  | 1601 | -6 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1279 |  | 1600 | -321 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -978 |  | -1248 | -270 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -977 |  | -1248 | -272 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -973 |  | -1248 | -275 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -973 |  | -1248 | -276 | 78 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1243 |  | 1600 | -357 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -968 |  | -1248 | -281 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1239 |  | 1600 | -361 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -967 |  | -1248 | -282 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1229 |  | 1600 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1162 |  | 1600 | -438 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1162 |  | 1600 | -438 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1156 |  | 1601 | -445 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1156 |  | 1601 | -445 | 72 | []

## 1430Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2548
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1592 | 1600 | 1600 | -8 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1592 | 1600 | 1600 | -8 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1587 | 1601 | 1601 | -14 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1587 | 1601 | 1601 | -14 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1276 | 1600 | 1600 | -324 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -966 | -1248 | -1248 | -282 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -964 | -1248 | -1248 | -284 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -962 | -1248 | -1248 | -286 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -960 | -1248 | -1248 | -288 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1229 | 1600 | 1600 | -371 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -956 | -1248 | -1248 | -293 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -956 | -1248 | -1248 | -293 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1221 | 1600 | 1600 | -379 | 76 | []

## 1430Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2548
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1592 |  | 1600 | -8 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1592 |  | 1600 | -8 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1587 |  | 1601 | -14 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1587 |  | 1601 | -14 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1276 |  | 1600 | -324 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1239 |  | 1600 | -361 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -966 |  | -1248 | -282 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -964 |  | -1248 | -284 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -962 |  | -1248 | -286 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -960 |  | -1248 | -288 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1229 |  | 1600 | -371 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -956 |  | -1248 | -293 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -956 |  | -1248 | -293 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1221 |  | 1600 | -379 | 76 | []

## 1530Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2603
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 | 1601 | 1601 | -8 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 | 1601 | 1601 | -8 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1298 | 1600 | 1600 | -302 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1245 | 1600 | 1600 | -355 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -962 | -1248 | -1248 | -287 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -960 | -1248 | -1248 | -289 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -957 | -1248 | -1248 | -292 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -956 | -1248 | -1248 | -293 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -951 | -1248 | -1248 | -297 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -951 | -1248 | -1248 | -298 | 76 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1217 | 1600 | 1600 | -383 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1210 | 1600 | 1600 | -390 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1381 | -1920 | -1920 | -539 | 72 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1128 | 1600 | 1600 | -472 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1124 | 1600 | 1600 | -476 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1124 | 1600 | 1600 | -476 | 70 | []

## 1530Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2603
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 |  | 1600 | -2 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 |  | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 |  | 1601 | -8 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 |  | 1601 | -8 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1298 |  | 1600 | -302 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1245 |  | 1600 | -355 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -962 |  | -1248 | -287 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -960 |  | -1248 | -289 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -957 |  | -1248 | -292 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -956 |  | -1248 | -293 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -951 |  | -1248 | -297 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -951 |  | -1248 | -298 | 76 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1217 |  | 1600 | -383 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1210 |  | 1600 | -390 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1381 |  | -1920 | -539 | 72 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1128 |  | 1600 | -472 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1124 |  | 1600 | -476 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1124 |  | 1600 | -476 | 70 | []

## 1630Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2768
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1361 | 1600 | 1600 | -239 | 85 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1276 | 1600 | 1600 | -324 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -981 | -1248 | -1248 | -268 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -980 | -1248 | -1248 | -269 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -976 | -1248 | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -975 | -1248 | -1248 | -274 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -970 | -1248 | -1248 | -278 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -968 | -1248 | -1248 | -280 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1221 | 1600 | 1600 | -379 | 76 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1215 | 1600 | 1600 | -385 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1202 | 1600 | 1600 | -398 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1415 | -1920 | -1920 | -505 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1173 | 1600 | 1600 | -427 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1173 | 1600 | 1600 | -427 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1168 | 1601 | 1601 | -433 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1168 | 1601 | 1601 | -433 | 73 | []

## 1630Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2768
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 |  | 1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 |  | 1600 | -5 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1361 |  | 1600 | -239 | 85 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1276 |  | 1600 | -324 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -981 |  | -1248 | -268 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -980 |  | -1248 | -269 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -976 |  | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -975 |  | -1248 | -274 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -970 |  | -1248 | -278 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -968 |  | -1248 | -280 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1221 |  | 1600 | -379 | 76 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1215 |  | 1600 | -385 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1202 |  | 1600 | -398 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1415 |  | -1920 | -505 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1173 |  | 1600 | -427 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1173 |  | 1600 | -427 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1168 |  | 1601 | -433 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1168 |  | 1601 | -433 | 73 | []

## 1730Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2841
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 | 1601 | 1601 | -8 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 | 1601 | 1601 | -8 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1398 | 1600 | 1600 | -202 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1290 | 1600 | 1600 | -310 | 81 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1271 | 1600 | 1600 | -329 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 | -1248 | -1248 | -272 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 | -1248 | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -972 | -1248 | -1248 | -277 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -970 | -1248 | -1248 | -278 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -966 | -1248 | -1248 | -283 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -964 | -1248 | -1248 | -285 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1209 | 1600 | 1600 | -391 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1185 | 1600 | 1600 | -415 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1182 | 1601 | 1601 | -419 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1182 | 1601 | 1601 | -419 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1415 | -1920 | -1920 | -505 | 74 | []

## 1730Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2841
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 |  | 1600 | -2 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 |  | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 |  | 1601 | -8 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 |  | 1601 | -8 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1398 |  | 1600 | -202 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1290 |  | 1600 | -310 | 81 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1271 |  | 1600 | -329 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 |  | -1248 | -272 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 |  | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -972 |  | -1248 | -277 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -970 |  | -1248 | -278 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -966 |  | -1248 | -283 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -964 |  | -1248 | -285 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1209 |  | 1600 | -391 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1187 |  | 1600 | -413 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1187 |  | 1600 | -413 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1185 |  | 1600 | -415 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1182 |  | 1601 | -419 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1182 |  | 1601 | -419 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1415 |  | -1920 | -505 | 74 | []

## 1830Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2909
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1449 | 1600 | 1600 | -151 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1339 | 1600 | 1600 | -261 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1318 | 1600 | 1600 | -282 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -952 | -1248 | -1248 | -297 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -951 | -1248 | -1248 | -297 | 76 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1218 | 1600 | 1600 | -382 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -947 | -1248 | -1248 | -301 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -945 | -1248 | -1248 | -303 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -941 | -1248 | -1248 | -307 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -939 | -1248 | -1248 | -310 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1187 | 1601 | 1601 | -414 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1187 | 1601 | 1601 | -414 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1183 | 1600 | 1600 | -417 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1397 | -1920 | -1920 | -523 | 73 | []

## 1830Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2909
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1599 |  | 1600 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1599 |  | 1600 | -1 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 |  | 1601 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 |  | 1601 | -6 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1449 |  | 1600 | -151 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1339 |  | 1600 | -261 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1318 |  | 1600 | -282 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -952 |  | -1248 | -297 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -951 |  | -1248 | -297 | 76 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1218 |  | 1600 | -382 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -947 |  | -1248 | -301 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -945 |  | -1248 | -303 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -941 |  | -1248 | -307 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -939 |  | -1248 | -310 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1193 |  | 1600 | -407 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1193 |  | 1600 | -407 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1187 |  | 1601 | -414 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1187 |  | 1601 | -414 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1183 |  | 1600 | -417 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1397 |  | -1920 | -523 | 73 | []

## 1930Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3052
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1592 | 1601 | 1601 | -9 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1592 | 1601 | 1601 | -9 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1498 | 1600 | 1600 | -102 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1406 | 1600 | 1600 | -194 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1346 | 1600 | 1600 | -254 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1229 | 1600 | 1600 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1189 | 1601 | 1601 | -412 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1189 | 1601 | 1601 | -412 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1184 | 1600 | 1600 | -416 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -919 | -1248 | -1248 | -330 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -918 | -1248 | -1248 | -331 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -914 | -1248 | -1248 | -335 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -913 | -1248 | -1248 | -336 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -908 | -1248 | -1248 | -340 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -907 | -1248 | -1248 | -342 | 73 | []

## 1930Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3052
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1596 |  | 1600 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1596 |  | 1600 | -4 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1592 |  | 1601 | -9 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1592 |  | 1601 | -9 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1498 |  | 1600 | -102 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1406 |  | 1600 | -194 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1346 |  | 1600 | -254 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1229 |  | 1600 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1194 |  | 1600 | -406 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1194 |  | 1600 | -406 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1189 |  | 1601 | -412 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1189 |  | 1601 | -412 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1184 |  | 1600 | -416 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -919 |  | -1248 | -330 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -918 |  | -1248 | -331 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -914 |  | -1248 | -335 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -913 |  | -1248 | -336 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -908 |  | -1248 | -340 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -907 |  | -1248 | -342 | 73 | []

## 2030Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2794
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1501 | 1600 | 1600 | -99 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1411 | 1600 | 1600 | -189 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1346 | 1600 | 1600 | -254 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1220 | 1600 | 1600 | -380 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1175 | 1600 | 1600 | -425 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -908 | -1248 | -1248 | -340 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -907 | -1248 | -1248 | -341 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -903 | -1248 | -1248 | -346 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1153 | 1600 | 1600 | -447 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1153 | 1600 | 1600 | -447 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -898 | -1248 | -1248 | -350 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -897 | -1248 | -1248 | -352 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1147 | 1601 | 1601 | -454 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1147 | 1601 | 1601 | -454 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1370 | -1920 | -1920 | -550 | 71 | []

## 2030Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2794
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1594 |  | 1600 | -6 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 |  | 1600 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1501 |  | 1600 | -99 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1411 |  | 1600 | -189 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1346 |  | 1600 | -254 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1220 |  | 1600 | -380 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1175 |  | 1600 | -425 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -908 |  | -1248 | -340 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -907 |  | -1248 | -341 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -903 |  | -1248 | -346 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1153 |  | 1600 | -447 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1153 |  | 1600 | -447 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -898 |  | -1248 | -350 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -897 |  | -1248 | -352 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1147 |  | 1601 | -454 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1147 |  | 1601 | -454 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1370 |  | -1920 | -550 | 71 | []

## 2130Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2873
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1464 | 1600 | 1600 | -136 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1391 | 1600 | 1600 | -209 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1303 | 1600 | 1600 | -297 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1168 | 1600 | 1600 | -432 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1136 | 1600 | 1600 | -464 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1136 | 1600 | 1600 | -464 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1131 | 1601 | 1601 | -470 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1131 | 1601 | 1601 | -470 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2873
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 |  | 1600 | -6 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1594 |  | 1600 | -6 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1464 |  | 1600 | -136 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1391 |  | 1600 | -209 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1303 |  | 1600 | -297 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1168 |  | 1600 | -432 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1136 |  | 1600 | -464 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1136 |  | 1600 | -464 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1131 |  | 1601 | -470 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1131 |  | 1601 | -470 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3053
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1592 | 1600 | 1600 | -8 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1592 | 1600 | 1600 | -8 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1464 | 1600 | 1600 | -136 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1405 | 1600 | 1600 | -195 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1290 | 1600 | 1600 | -310 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1180 | 1601 | 1601 | -421 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1180 | 1601 | 1601 | -421 | 74 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1144 | 1600 | 1600 | -456 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -880 | -1248 | -1248 | -368 | 70 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -880 | -1248 | -1248 | -369 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1348 | -1920 | -1920 | -572 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -876 | -1248 | -1248 | -373 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3053
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1592 |  | 1600 | -8 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1592 |  | 1600 | -8 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1464 |  | 1600 | -136 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1405 |  | 1600 | -195 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1290 |  | 1600 | -310 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1185 |  | 1600 | -415 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1185 |  | 1600 | -415 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1180 |  | 1601 | -421 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1180 |  | 1601 | -421 | 74 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1144 |  | 1600 | -456 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -880 |  | -1248 | -368 | 70 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -880 |  | -1248 | -369 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1348 |  | -1920 | -572 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -876 |  | -1248 | -373 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3281
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1594 | 1601 | 1601 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1594 | 1601 | 1601 | -7 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1446 | 1600 | 1600 | -154 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1398 | 1600 | 1600 | -202 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1270 | 1600 | 1600 | -330 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1195 | 1600 | 1600 | -405 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1195 | 1600 | 1600 | -405 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1191 | 1601 | 1601 | -410 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1191 | 1601 | 1601 | -410 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -891 | -1248 | -1248 | -357 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -891 | -1248 | -1248 | -358 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -887 | -1248 | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -886 | -1248 | -1248 | -363 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -881 | -1248 | -1248 | -367 | 71 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-RO] Stupina - Varna [DIR] [RO] | RSTUP41 _XVA_ST11_1:line | 1410 | 2000 | 2000 | -590 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -880 | -1248 | -1248 | -369 | 70 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1126 | 1600 | 1600 | -474 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2023-12-31 07:54
Business day: | 31.12.2023
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3281
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 |  | 1600 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1597 |  | 1600 | -3 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1594 |  | 1601 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1594 |  | 1601 | -7 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1446 |  | 1600 | -154 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1398 |  | 1600 | -202 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1270 |  | 1600 | -330 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1195 |  | 1600 | -405 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1195 |  | 1600 | -405 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1191 |  | 1601 | -410 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1191 |  | 1601 | -410 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -891 |  | -1248 | -357 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -891 |  | -1248 | -358 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -887 |  | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -886 |  | -1248 | -363 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -881 |  | -1248 | -367 | 71 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-RO] Stupina - Varna [DIR] [RO] | RSTUP41 _XVA_ST11_1:line | 1410 |  | 2000 | -590 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -880 |  | -1248 | -369 | 70 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1126 |  | 1600 | -474 | 70 | []