## 0030Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1111
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1526 | 1600 | 1600 | -74 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1206 | 1600 | 1600 | -394 | 75 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1164 | 1600 | 1600 | -436 | 73 | []

## 0030Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1111
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1526 |  | 1600 | -74 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1206 |  | 1600 | -394 | 75 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1164 |  | 1600 | -436 | 73 | []

## 0130Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 958
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1523 | 1600 | 1600 | -77 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1201 | 1600 | 1600 | -399 | 75 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1167 | 1600 | 1600 | -433 | 73 | []

## 0130Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 958
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1523 |  | 1600 | -77 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1201 |  | 1600 | -399 | 75 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1167 |  | 1600 | -433 | 73 | []

## 0230Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 995
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1520 | 1600 | 1600 | -80 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1197 | 1600 | 1600 | -403 | 75 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1168 | 1600 | 1600 | -432 | 73 | []

## 0230Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 995
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1520 |  | 1600 | -80 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1197 |  | 1600 | -403 | 75 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1168 |  | 1600 | -432 | 73 | []

## 0330Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 894
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1517 | 1600 | 1600 | -83 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1191 | 1600 | 1600 | -409 | 74 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1172 | 1600 | 1600 | -428 | 73 | []

## 0330Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 894
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1517 |  | 1600 | -83 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1191 |  | 1600 | -409 | 74 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1172 |  | 1600 | -428 | 73 | []

## 0430Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 884
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1520 | 1600 | 1600 | -80 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1197 | 1600 | 1600 | -403 | 75 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1167 | 1600 | 1600 | -433 | 73 | []

## 0430Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 884
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1520 |  | 1600 | -80 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1197 |  | 1600 | -403 | 75 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1167 |  | 1600 | -433 | 73 | []

## 0530Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1088
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1532 | 1600 | 1600 | -68 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1217 | 1600 | 1600 | -383 | 76 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1158 | 1600 | 1600 | -442 | 72 | []

## 0530Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1088
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1532 |  | 1600 | -68 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1217 |  | 1600 | -383 | 76 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1158 |  | 1600 | -442 | 72 | []

## 0630Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1093
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1544 | 1600 | 1600 | -56 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1147 | 1600 | 1600 | -453 | 72 | []

## 0630Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1093
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1544 |  | 1600 | -56 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1234 |  | 1600 | -366 | 77 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1147 |  | 1600 | -453 | 72 | []

## 0730Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 936
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1551 | 1600 | 1600 | -49 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1245 | 1600 | 1600 | -355 | 78 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1142 | 1600 | 1600 | -458 | 71 | []

## 0730Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 936
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1551 |  | 1600 | -49 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1245 |  | 1600 | -355 | 78 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1142 |  | 1600 | -458 | 71 | []

## 0830Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 611
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1558 | 1600 | 1600 | -42 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1253 | 1600 | 1600 | -347 | 78 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1135 | 1600 | 1600 | -465 | 71 | []

## 0830Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 611
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1558 |  | 1600 | -42 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1253 |  | 1600 | -347 | 78 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1135 |  | 1600 | -465 | 71 | []

## 0930Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 559
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1578 | 1600 | 1600 | -22 | 99 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1282 | 1600 | 1600 | -318 | 80 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1123 | 1600 | 1600 | -477 | 70 | []

## 0930Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 559
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1578 |  | 1600 | -22 | 99 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1282 |  | 1600 | -318 | 80 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1123 |  | 1600 | -477 | 70 | []

## 1030Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 816
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1585 | 1600 | 1600 | -15 | 99 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1325 | 1600 | 1600 | -275 | 83 | []

## 1030Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 816
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1585 |  | 1600 | -15 | 99 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1325 |  | 1600 | -275 | 83 | []

## 1130Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1250
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1563 | 1600 | 1600 | -37 | 98 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1346 | 1600 | 1600 | -254 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1158 | 1600 | 1600 | -442 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1127 | 1600 | 1600 | -473 | 70 | []

## 1130Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1250
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1563 |  | 1600 | -37 | 98 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1346 |  | 1600 | -254 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1158 |  | 1600 | -442 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1127 |  | 1600 | -473 | 70 | []

## 1230Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1841
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1547 | 1600 | 1600 | -53 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1358 | 1600 | 1600 | -242 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1416 | 1836 | 1836 | -420 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1196 | 1600 | 1600 | -404 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1338 | 1836 | 1836 | -498 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1163 | 1600 | 1600 | -437 | 73 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1334 | 1836 | 1836 | -502 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1147 | 1601 | 1601 | -454 | 72 | []

## 1230Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1841
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1547 |  | 1600 | -53 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1358 |  | 1600 | -242 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1416 |  | 1836 | -420 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1196 |  | 1600 | -404 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1338 |  | 1836 | -498 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1163 |  | 1600 | -437 | 73 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1334 |  | 1836 | -502 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1150 |  | 1600 | -450 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1147 |  | 1601 | -454 | 72 | []

## 1330Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2971
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1550 | 1600 | 1600 | -50 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -943 | -999 | -999 | -57 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1637 | 1836 | 1836 | -199 | 89 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 | 1836 | 1836 | -209 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1369 | 1600 | 1600 | -231 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1836 | 1836 | -267 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1836 | 1836 | -267 | 85 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1522 | 1836 | 1836 | -314 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1517 | 1836 | 1836 | -319 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1510 | 1836 | 1836 | -326 | 82 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1500 | 1836 | 1836 | -336 | 82 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1492 | 1836 | 1836 | -344 | 81 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 | 1836 | 1836 | -382 | 79 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1236 | 1600 | 1600 | -364 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1195 | 1600 | 1600 | -405 | 75 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1179 | 1600 | 1600 | -421 | 74 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1179 | 1600 | 1600 | -421 | 74 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1174 | 1601 | 1601 | -427 | 73 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1174 | 1601 | 1601 | -427 | 73 | []

## 1330Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2971
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1550 |  | 1600 | -50 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -943 |  | -999 | -57 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1637 |  | 1836 | -199 | 89 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 |  | 1836 | -209 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1369 |  | 1600 | -231 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1836 | -267 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1836 | -267 | 85 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1522 |  | 1836 | -314 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1517 |  | 1836 | -319 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1510 |  | 1836 | -326 | 82 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1500 |  | 1836 | -336 | 82 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1492 |  | 1836 | -344 | 81 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1836 | -382 | 79 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1236 |  | 1600 | -364 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1195 |  | 1600 | -405 | 75 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1179 |  | 1600 | -421 | 74 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1179 |  | 1600 | -421 | 74 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1174 |  | 1601 | -427 | 73 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1174 |  | 1601 | -427 | 73 | []

## 1430Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3436
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1591 | 1601 | 1601 | -10 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1591 | 1601 | 1601 | -10 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1556 | 1600 | 1600 | -44 | 97 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1499 | 1600 | 1600 | -101 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1343 | 1600 | 1600 | -257 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1298 | 1600 | 1600 | -302 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1298 | 1600 | 1600 | -302 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -809 | -999 | -999 | -190 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1293 | 1601 | 1601 | -308 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1293 | 1601 | 1601 | -308 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 | 1836 | 1836 | -378 | 79 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 | 1836 | 1836 | -378 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 | 1836 | 1836 | -391 | 79 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1435 | 1836 | 1836 | -401 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1231 | 1600 | 1600 | -369 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -953 | -1248 | -1248 | -296 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -951 | -1248 | -1248 | -297 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -948 | -1248 | -1248 | -300 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -943 | -1248 | -1248 | -306 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -941 | -1248 | -1248 | -308 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -936 | -1248 | -1248 | -312 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1194 | 1600 | 1600 | -406 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1360 | 1836 | 1836 | -476 | 74 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1344 | 1836 | 1836 | -492 | 73 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1334 | 1836 | 1836 | -502 | 73 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1334 | 1836 | 1836 | -502 | 73 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1330 | 1836 | 1836 | -506 | 72 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1304 | 1836 | 1836 | -532 | 71 | []

## 1430Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3436
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 |  | 1600 | -5 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 |  | 1600 | -5 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1591 |  | 1601 | -10 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1591 |  | 1601 | -10 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1556 |  | 1600 | -44 | 97 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1499 |  | 1600 | -101 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1343 |  | 1600 | -257 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1298 |  | 1600 | -302 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1298 |  | 1600 | -302 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -809 |  | -999 | -190 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1293 |  | 1601 | -308 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1293 |  | 1601 | -308 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 |  | 1836 | -378 | 79 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 |  | 1836 | -378 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1836 | -391 | 79 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1836 | -401 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1231 |  | 1600 | -369 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -953 |  | -1248 | -296 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -951 |  | -1248 | -297 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -948 |  | -1248 | -300 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -943 |  | -1248 | -306 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -941 |  | -1248 | -308 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -936 |  | -1248 | -312 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1194 |  | 1600 | -406 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1360 |  | 1836 | -476 | 74 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1344 |  | 1836 | -492 | 73 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1334 |  | 1836 | -502 | 73 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1334 |  | 1836 | -502 | 73 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1330 |  | 1836 | -506 | 72 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1304 |  | 1836 | -532 | 71 | []

## 1530Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3171
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1475 | 1600 | 1600 | -125 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1409 | 1600 | 1600 | -191 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1283 | 1600 | 1600 | -317 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1207 | 1601 | 1601 | -394 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1207 | 1601 | 1601 | -394 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -934 | -1248 | -1248 | -315 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -934 | -1248 | -1248 | -315 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -929 | -1248 | -1248 | -319 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -927 | -1248 | -1248 | -321 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -923 | -1248 | -1248 | -325 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -921 | -1248 | -1248 | -327 | 74 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1177 | 1600 | 1600 | -423 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1150 | 1600 | 1600 | -450 | 72 | []

## 1530Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3171
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 |  | 1600 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 |  | 1600 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1475 |  | 1600 | -125 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1409 |  | 1600 | -191 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1283 |  | 1600 | -317 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1212 |  | 1600 | -388 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1212 |  | 1600 | -388 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1207 |  | 1601 | -394 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1207 |  | 1601 | -394 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -934 |  | -1248 | -315 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -934 |  | -1248 | -315 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -929 |  | -1248 | -319 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -927 |  | -1248 | -321 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -923 |  | -1248 | -325 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -921 |  | -1248 | -327 | 74 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1177 |  | 1600 | -423 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1150 |  | 1600 | -450 | 72 | []

## 1630Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2988
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1594 | 1601 | 1601 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1594 | 1601 | 1601 | -7 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1480 | 1600 | 1600 | -120 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1408 | 1600 | 1600 | -192 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1292 | 1600 | 1600 | -308 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -942 | -1248 | -1248 | -306 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -942 | -1248 | -1248 | -306 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -938 | -1248 | -1248 | -310 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -936 | -1248 | -1248 | -313 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -932 | -1248 | -1248 | -316 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -930 | -1248 | -1248 | -319 | 74 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1189 | 1600 | 1600 | -411 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1423 | -1920 | -1920 | -497 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1177 | 1601 | 1601 | -424 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1177 | 1601 | 1601 | -424 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1166 | 1600 | 1600 | -434 | 73 | []

## 1630Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2988
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 |  | 1600 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 |  | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1594 |  | 1601 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1594 |  | 1601 | -7 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1480 |  | 1600 | -120 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1408 |  | 1600 | -192 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1292 |  | 1600 | -308 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -942 |  | -1248 | -306 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -942 |  | -1248 | -306 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -938 |  | -1248 | -310 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -936 |  | -1248 | -313 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -932 |  | -1248 | -316 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -930 |  | -1248 | -319 | 74 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1189 |  | 1600 | -411 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1423 |  | -1920 | -497 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1182 |  | 1600 | -418 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1182 |  | 1600 | -418 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1177 |  | 1601 | -424 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1177 |  | 1601 | -424 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1166 |  | 1600 | -434 | 73 | []

## 1730Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2780
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 | 1601 | 1601 | -8 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 | 1601 | 1601 | -8 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1389 | 1600 | 1600 | -211 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1289 | 1600 | 1600 | -311 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1263 | 1600 | 1600 | -337 | 79 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1172 | 1600 | 1600 | -428 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -908 | -1248 | -1248 | -340 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -907 | -1248 | -1248 | -341 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -898 | -1248 | -1248 | -350 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -897 | -1248 | -1248 | -351 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1137 | 1600 | 1600 | -463 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1360 | -1920 | -1920 | -560 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1132 | 1600 | 1600 | -468 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1132 | 1600 | 1600 | -468 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1126 | 1601 | 1601 | -475 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1126 | 1601 | 1601 | -475 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2780
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 |  | 1600 | -2 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 |  | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 |  | 1601 | -8 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 |  | 1601 | -8 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1389 |  | 1600 | -211 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1289 |  | 1600 | -311 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1263 |  | 1600 | -337 | 79 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1172 |  | 1600 | -428 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -908 |  | -1248 | -340 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -907 |  | -1248 | -341 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -898 |  | -1248 | -350 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -897 |  | -1248 | -351 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1137 |  | 1600 | -463 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1360 |  | -1920 | -560 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1132 |  | 1600 | -468 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1132 |  | 1600 | -468 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1126 |  | 1601 | -475 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1126 |  | 1601 | -475 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2700
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1347 | 1600 | 1600 | -253 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1246 | 1600 | 1600 | -354 | 78 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1179 | 1600 | 1600 | -421 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1153 | 1600 | 1600 | -447 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -895 | -1248 | -1248 | -353 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -894 | -1248 | -1248 | -355 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -890 | -1248 | -1248 | -358 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -890 | -1248 | -1248 | -359 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -885 | -1248 | -1248 | -364 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -884 | -1248 | -1248 | -364 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1353 | -1920 | -1920 | -567 | 70 | []

## 1830Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2700
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 |  | 1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 |  | 1600 | -5 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1347 |  | 1600 | -253 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1246 |  | 1600 | -354 | 78 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1227 |  | 1600 | -373 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1179 |  | 1600 | -421 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1153 |  | 1600 | -447 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -895 |  | -1248 | -353 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -894 |  | -1248 | -355 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -890 |  | -1248 | -358 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -890 |  | -1248 | -359 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -885 |  | -1248 | -364 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -884 |  | -1248 | -364 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1353 |  | -1920 | -567 | 70 | []

## 1930Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2724
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1339 | 1600 | 1600 | -261 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1252 | 1600 | 1600 | -348 | 78 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1205 | 1600 | 1600 | -395 | 75 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1200 | 1600 | 1600 | -400 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1174 | 1600 | 1600 | -426 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -904 | -1248 | -1248 | -344 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -899 | -1248 | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -899 | -1248 | -1248 | -350 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -894 | -1248 | -1248 | -354 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -893 | -1248 | -1248 | -356 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1368 | -1920 | -1920 | -552 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1135 | 1600 | 1600 | -465 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1135 | 1600 | 1600 | -465 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1130 | 1601 | 1601 | -471 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1130 | 1601 | 1601 | -471 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2724
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 |  | 1600 | 0 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 |  | 1600 | 0 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 |  | 1601 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 |  | 1601 | -6 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1339 |  | 1600 | -261 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1252 |  | 1600 | -348 | 78 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1205 |  | 1600 | -395 | 75 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1200 |  | 1600 | -400 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1174 |  | 1600 | -426 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -904 |  | -1248 | -344 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -899 |  | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -899 |  | -1248 | -350 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -894 |  | -1248 | -354 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -893 |  | -1248 | -356 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1368 |  | -1920 | -552 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1135 |  | 1600 | -465 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1135 |  | 1600 | -465 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1130 |  | 1601 | -471 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1130 |  | 1601 | -471 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2681
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1328 | 1600 | 1600 | -272 | 83 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1244 | 1600 | 1600 | -356 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1197 | 1600 | 1600 | -403 | 75 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1191 | 1600 | 1600 | -409 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1170 | 1600 | 1600 | -430 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -883 | -1248 | -1248 | -366 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -882 | -1248 | -1248 | -367 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -878 | -1248 | -1248 | -371 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1125 | 1600 | 1600 | -475 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1125 | 1600 | 1600 | -475 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -877 | -1248 | -1248 | -371 | 70 | []

## 2030Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2681
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 |  | 1600 | 0 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 |  | 1600 | 0 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 |  | 1601 | -6 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 |  | 1601 | -6 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1328 |  | 1600 | -272 | 83 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1244 |  | 1600 | -356 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1197 |  | 1600 | -403 | 75 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1191 |  | 1600 | -409 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1170 |  | 1600 | -430 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -883 |  | -1248 | -366 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -882 |  | -1248 | -367 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -878 |  | -1248 | -371 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1125 |  | 1600 | -475 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1125 |  | 1600 | -475 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -877 |  | -1248 | -371 | 70 | []

## 2130Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2748
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1326 | 1600 | 1600 | -274 | 83 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1238 | 1600 | 1600 | -362 | 77 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1195 | 1600 | 1600 | -405 | 75 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1185 | 1600 | 1600 | -415 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1156 | 1600 | 1600 | -444 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1142 | 1600 | 1600 | -458 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1142 | 1600 | 1600 | -458 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -890 | -1248 | -1248 | -358 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -890 | -1248 | -1248 | -359 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1137 | 1601 | 1601 | -464 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1137 | 1601 | 1601 | -464 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -885 | -1248 | -1248 | -363 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -885 | -1248 | -1248 | -363 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -880 | -1248 | -1248 | -368 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -879 | -1248 | -1248 | -370 | 70 | []

## 2130Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2748
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1594 |  | 1600 | -6 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 |  | 1600 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1326 |  | 1600 | -274 | 83 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1238 |  | 1600 | -362 | 77 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1195 |  | 1600 | -405 | 75 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1185 |  | 1600 | -415 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1156 |  | 1600 | -444 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1142 |  | 1600 | -458 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1142 |  | 1600 | -458 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -890 |  | -1248 | -358 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -890 |  | -1248 | -359 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1137 |  | 1601 | -464 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1137 |  | 1601 | -464 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -885 |  | -1248 | -363 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -885 |  | -1248 | -363 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -880 |  | -1248 | -368 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -879 |  | -1248 | -370 | 70 | []

## 2230Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2884
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1389 | 1600 | 1600 | -211 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1284 | 1600 | 1600 | -316 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1268 | 1600 | 1600 | -332 | 79 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1185 | 1600 | 1600 | -415 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1176 | 1601 | 1601 | -425 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1176 | 1601 | 1601 | -425 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1141 | 1600 | 1600 | -459 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -890 | -1248 | -1248 | -358 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -890 | -1248 | -1248 | -358 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -886 | -1248 | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -884 | -1248 | -1248 | -364 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1355 | -1920 | -1920 | -565 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -880 | -1248 | -1248 | -368 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -878 | -1248 | -1248 | -370 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2884
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 |  | 1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 |  | 1600 | -5 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1389 |  | 1600 | -211 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1284 |  | 1600 | -316 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1268 |  | 1600 | -332 | 79 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1185 |  | 1600 | -415 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1181 |  | 1600 | -419 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1181 |  | 1600 | -419 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1176 |  | 1601 | -425 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1176 |  | 1601 | -425 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1141 |  | 1600 | -459 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -890 |  | -1248 | -358 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -890 |  | -1248 | -358 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -886 |  | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -884 |  | -1248 | -364 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1355 |  | -1920 | -565 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -880 |  | -1248 | -368 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -878 |  | -1248 | -370 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3190
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1597 | 1601 | 1601 | -4 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1597 | 1601 | 1601 | -4 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1445 | 1600 | 1600 | -155 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1349 | 1600 | 1600 | -251 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1313 | 1600 | 1600 | -287 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1229 | 1600 | 1600 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1198 | 1601 | 1601 | -403 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1198 | 1601 | 1601 | -403 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1171 | 1600 | 1600 | -429 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -892 | -1248 | -1248 | -356 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -892 | -1248 | -1248 | -357 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -888 | -1248 | -1248 | -361 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -886 | -1248 | -1248 | -362 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -882 | -1248 | -1248 | -366 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -880 | -1248 | -1248 | -368 | 71 | []

## 2330Curative
Detailed results
Generated at: | 2024-01-04 19:09
Business day: | 05.01.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3190
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 |  | 1600 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 |  | 1600 | 0 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1597 |  | 1601 | -4 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1597 |  | 1601 | -4 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1445 |  | 1600 | -155 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1349 |  | 1600 | -251 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1313 |  | 1600 | -287 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1229 |  | 1600 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1201 |  | 1600 | -399 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1201 |  | 1600 | -399 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1198 |  | 1601 | -403 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1198 |  | 1601 | -403 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1171 |  | 1600 | -429 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -892 |  | -1248 | -356 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -892 |  | -1248 | -357 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -888 |  | -1248 | -361 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -886 |  | -1248 | -362 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -882 |  | -1248 | -366 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -880 |  | -1248 | -368 | 71 | []