## 0030Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 815
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1495 | 1600 | 1600 | -105 | 93 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1188 | 1600 | 1600 | -412 | 74 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1180 | 1600 | 1600 | -420 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1131 | 1600 | 1600 | -469 | 71 | []

## 0030Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 815
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1495 |  | 1600 | -105 | 93 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1188 |  | 1600 | -412 | 74 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1180 |  | 1600 | -420 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1131 |  | 1600 | -469 | 71 | []

## 0130Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 903
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1510 | 1600 | 1600 | -90 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1204 | 1600 | 1600 | -396 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1128 | 1600 | 1600 | -472 | 70 | []

## 0130Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 903
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1510 |  | 1600 | -90 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1204 |  | 1600 | -396 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1128 |  | 1600 | -472 | 70 | []

## 0230Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1060
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1515 | 1600 | 1600 | -85 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1212 | 1600 | 1600 | -388 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1127 | 1600 | 1600 | -473 | 70 | []

## 0230Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1060
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1515 |  | 1600 | -85 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1212 |  | 1600 | -388 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1127 |  | 1600 | -473 | 70 | []

## 0330Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1215
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1532 | 1600 | 1600 | -68 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1161 | 1600 | 1600 | -439 | 73 | []

## 0330Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1215
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1532 |  | 1600 | -68 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1242 |  | 1600 | -358 | 78 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1161 |  | 1600 | -439 | 73 | []

## 0430Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1266
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1545 | 1600 | 1600 | -55 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1263 | 1600 | 1600 | -337 | 79 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1153 | 1600 | 1600 | -447 | 72 | []

## 0430Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1266
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1545 |  | 1600 | -55 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1263 |  | 1600 | -337 | 79 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1153 |  | 1600 | -447 | 72 | []

## 0530Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2790
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1585 | 1600 | 1600 | -15 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1428 | 1600 | 1600 | -172 | 89 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1428 | 1600 | 1600 | -172 | 89 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1424 | 1601 | 1601 | -177 | 89 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1424 | 1601 | 1601 | -177 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1339 | 1600 | 1600 | -261 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -897 | -1248 | -1248 | -351 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -896 | -1248 | -1248 | -352 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -892 | -1248 | -1248 | -356 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -892 | -1248 | -1248 | -357 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -887 | -1248 | -1248 | -361 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -886 | -1248 | -1248 | -363 | 71 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1126 | 1600 | 1600 | -474 | 70 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1123 | 1600 | 1600 | -477 | 70 | []

## 0530Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2790
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1585 |  | 1600 | -15 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1428 |  | 1600 | -172 | 89 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1428 |  | 1600 | -172 | 89 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1424 |  | 1601 | -177 | 89 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1424 |  | 1601 | -177 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1339 |  | 1600 | -261 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -897 |  | -1248 | -351 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -896 |  | -1248 | -352 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -892 |  | -1248 | -356 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -892 |  | -1248 | -357 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -887 |  | -1248 | -361 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -886 |  | -1248 | -363 | 71 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1126 |  | 1600 | -474 | 70 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1123 |  | 1600 | -477 | 70 | []

## 0630Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2230
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1424 | 1600 | 1600 | -176 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1421 | 1601 | 1601 | -180 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1349 | 1600 | 1600 | -251 | 84 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
BC | Base Case | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1221 | 1601 | 1601 | -380 | 76 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1122 | 1600 | 1600 | -478 | 70 | []

## 0630Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2230
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1597 |  | 1600 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1424 |  | 1600 | -176 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1421 |  | 1601 | -180 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1349 |  | 1600 | -251 | 84 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1224 |  | 1600 | -376 | 76 | []
BC | Base Case | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1221 |  | 1601 | -380 | 76 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1122 |  | 1600 | -478 | 70 | []

## 0730Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2067
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1581 | 1600 | 1600 | -19 | 99 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1323 | 1600 | 1600 | -277 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1305 | 1600 | 1600 | -295 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1300 | 1601 | 1601 | -301 | 81 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
BC | Base Case | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1158 | 1601 | 1601 | -443 | 72 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | -1129 | -1600 | -1600 | -471 | 71 | []

## 0730Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2067
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1581 |  | 1600 | -19 | 99 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1323 |  | 1600 | -277 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1305 |  | 1600 | -295 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1300 |  | 1601 | -301 | 81 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1163 |  | 1600 | -437 | 73 | []
BC | Base Case | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1158 |  | 1601 | -443 | 72 | []
BC | Base Case | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | -1129 |  | -1600 | -471 | 71 | []

## 0830Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3138
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1580 | 1600 | 1600 | -20 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1527 | 1600 | 1600 | -73 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1527 | 1600 | 1600 | -73 | 95 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1522 | 1601 | 1601 | -79 | 95 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1522 | 1601 | 1601 | -79 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1375 | 1600 | 1600 | -225 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1197 | 1600 | 1600 | -403 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1168 | 1600 | 1600 | -432 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1168 | 1600 | 1600 | -432 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1163 | 1601 | 1601 | -438 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1163 | 1601 | 1601 | -438 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -704 | -999 | -999 | -295 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -879 | -1248 | -1248 | -370 | 70 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -878 | -1248 | -1248 | -370 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -874 | -1248 | -1248 | -374 | 70 | []

## 0830Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3138
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1580 |  | 1600 | -20 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1527 |  | 1600 | -73 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1527 |  | 1600 | -73 | 95 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1522 |  | 1601 | -79 | 95 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1522 |  | 1601 | -79 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1375 |  | 1600 | -225 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1197 |  | 1600 | -403 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1168 |  | 1600 | -432 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1168 |  | 1600 | -432 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1163 |  | 1601 | -438 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1163 |  | 1601 | -438 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -704 |  | -999 | -295 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -879 |  | -1248 | -370 | 70 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -878 |  | -1248 | -370 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -874 |  | -1248 | -374 | 70 | []

## 0930Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3350
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1562 | 1600 | 1600 | -38 | 98 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -926 | -999 | -999 | -73 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1448 | 1600 | 1600 | -152 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1448 | 1600 | 1600 | -152 | 90 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1443 | 1601 | 1601 | -158 | 90 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1443 | 1601 | 1601 | -158 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1627 | -1836 | -1836 | -209 | 89 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1614 | -1836 | -1836 | -222 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 | 1836 | 1836 | -230 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 | 1836 | 1836 | -230 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1364 | 1600 | 1600 | -236 | 85 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1532 | -1836 | -1836 | -304 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1523 | -1836 | -1836 | -313 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1511 | -1836 | -1836 | -325 | 82 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1509 | -1836 | -1836 | -327 | 82 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1505 | -1836 | -1836 | -331 | 82 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1467 | -1836 | -1836 | -369 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1252 | 1600 | 1600 | -348 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1252 | 1600 | 1600 | -348 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1247 | 1601 | 1601 | -354 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1247 | 1601 | 1601 | -354 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1238 | 1600 | 1600 | -362 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -921 | -1248 | -1248 | -327 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1179 | 1600 | 1600 | -421 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -919 | -1248 | -1248 | -330 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -917 | -1248 | -1248 | -332 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -909 | -1248 | -1248 | -339 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -908 | -1248 | -1248 | -340 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -903 | -1248 | -1248 | -346 | 72 | []

## 0930Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3350
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1562 |  | 1600 | -38 | 98 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -926 |  | -999 | -73 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1448 |  | 1600 | -152 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1448 |  | 1600 | -152 | 90 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1443 |  | 1601 | -158 | 90 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1443 |  | 1601 | -158 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1627 |  | -1836 | -209 | 89 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1614 |  | -1836 | -222 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 |  | 1836 | -230 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 |  | 1836 | -230 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1364 |  | 1600 | -236 | 85 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1532 |  | -1836 | -304 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1523 |  | -1836 | -313 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1511 |  | -1836 | -325 | 82 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1509 |  | -1836 | -327 | 82 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1505 |  | -1836 | -331 | 82 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1467 |  | -1836 | -369 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1252 |  | 1600 | -348 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1252 |  | 1600 | -348 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1247 |  | 1601 | -354 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1247 |  | 1601 | -354 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1238 |  | 1600 | -362 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -921 |  | -1248 | -327 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1179 |  | 1600 | -421 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -919 |  | -1248 | -330 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -917 |  | -1248 | -332 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -909 |  | -1248 | -339 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -908 |  | -1248 | -340 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -903 |  | -1248 | -346 | 72 | []

## 1030Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3313
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1809 | 1836 | 1836 | -27 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1803 | 1836 | 1836 | -33 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1803 | 1836 | 1836 | -33 | 98 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1566 | 1600 | 1600 | -34 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1794 | 1836 | 1836 | -42 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1732 | 1836 | 1836 | -104 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1720 | 1836 | 1836 | -116 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 | 1836 | 1836 | -121 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1707 | 1836 | 1836 | -129 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1487 | 1600 | 1600 | -113 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1695 | -1836 | -1836 | -141 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1667 | -1836 | -1836 | -169 | 91 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1415 | 1600 | 1600 | -185 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1415 | 1600 | 1600 | -185 | 88 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1410 | 1601 | 1601 | -191 | 88 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1410 | 1601 | 1601 | -191 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1396 | 1600 | 1600 | -204 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1292 | 1600 | 1600 | -308 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1284 | 1600 | 1600 | -316 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1284 | 1600 | 1600 | -316 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1278 | 1601 | 1601 | -323 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1278 | 1601 | 1601 | -323 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -963 | -1248 | -1248 | -285 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -959 | -1248 | -1248 | -289 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -959 | -1248 | -1248 | -290 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -949 | -1248 | -1248 | -300 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -948 | -1248 | -1248 | -301 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1213 | 1600 | 1600 | -387 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -941 | -1248 | -1248 | -307 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1434 | -1920 | -1920 | -486 | 75 | []

## 1030Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3313
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1809 |  | 1836 | -27 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1803 |  | 1836 | -33 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1803 |  | 1836 | -33 | 98 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1566 |  | 1600 | -34 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1794 |  | 1836 | -42 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1732 |  | 1836 | -104 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1720 |  | 1836 | -116 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 |  | 1836 | -121 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1707 |  | 1836 | -129 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1487 |  | 1600 | -113 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1695 |  | -1836 | -141 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1667 |  | -1836 | -169 | 91 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1415 |  | 1600 | -185 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1415 |  | 1600 | -185 | 88 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1410 |  | 1601 | -191 | 88 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1410 |  | 1601 | -191 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1396 |  | 1600 | -204 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1292 |  | 1600 | -308 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1284 |  | 1600 | -316 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1284 |  | 1600 | -316 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1278 |  | 1601 | -323 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1278 |  | 1601 | -323 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -963 |  | -1248 | -285 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -959 |  | -1248 | -289 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -959 |  | -1248 | -290 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -949 |  | -1248 | -300 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -948 |  | -1248 | -301 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1213 |  | 1600 | -387 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -941 |  | -1248 | -307 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1434 |  | -1920 | -486 | 75 | []

## 1130Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3205
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1833 | 1836 | 1836 | -3 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1818 | 1836 | 1836 | -18 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1573 | 1600 | 1600 | -27 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1770 | 1836 | 1836 | -66 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1770 | 1836 | 1836 | -66 | 96 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -960 | -999 | -999 | -39 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1502 | 1600 | 1600 | -98 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1713 | 1836 | 1836 | -123 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1701 | 1836 | 1836 | -135 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1697 | 1836 | 1836 | -139 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 | 1836 | 1836 | -144 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 | 1836 | 1836 | -149 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1648 | 1836 | 1836 | -188 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1396 | 1600 | 1600 | -204 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1286 | 1600 | 1600 | -314 | 80 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1247 | 1601 | 1601 | -354 | 78 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1247 | 1601 | 1601 | -354 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1201 | 1600 | 1600 | -399 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1178 | 1601 | 1601 | -423 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1178 | 1601 | 1601 | -423 | 74 | []

## 1130Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3205
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1833 |  | 1836 | -3 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1818 |  | 1836 | -18 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1573 |  | 1600 | -27 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1770 |  | 1836 | -66 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1770 |  | 1836 | -66 | 96 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -960 |  | -999 | -39 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1502 |  | 1600 | -98 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1713 |  | 1836 | -123 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1701 |  | 1836 | -135 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1697 |  | 1836 | -139 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 |  | 1836 | -144 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 |  | 1836 | -149 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1648 |  | 1836 | -188 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1396 |  | 1600 | -204 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1286 |  | 1600 | -314 | 80 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1253 |  | 1600 | -347 | 78 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1253 |  | 1600 | -347 | 78 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1247 |  | 1601 | -354 | 78 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1247 |  | 1601 | -354 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1201 |  | 1600 | -399 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1183 |  | 1600 | -417 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1183 |  | 1600 | -417 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1178 |  | 1601 | -423 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1178 |  | 1601 | -423 | 74 | []

## 1230Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3173
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1827 | 1836 | 1836 | -9 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1811 | 1836 | 1836 | -25 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1772 | 1836 | 1836 | -64 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1772 | 1836 | 1836 | -64 | 97 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1540 | 1600 | 1600 | -60 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1714 | 1836 | 1836 | -122 | 93 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -927 | -999 | -999 | -72 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 | 1836 | 1836 | -136 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1699 | 1836 | 1836 | -137 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1691 | 1836 | 1836 | -145 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 | 1836 | 1836 | -152 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1462 | 1600 | 1600 | -138 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1652 | 1836 | 1836 | -184 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1374 | 1600 | 1600 | -226 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1274 | 1600 | 1600 | -326 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1233 | 1601 | 1601 | -368 | 77 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1233 | 1601 | 1601 | -368 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1193 | 1600 | 1600 | -407 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1176 | 1600 | 1600 | -424 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1176 | 1600 | 1600 | -424 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1171 | 1601 | 1601 | -430 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1171 | 1601 | 1601 | -430 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -874 | -1248 | -1248 | -374 | 70 | []

## 1230Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3173
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1827 |  | 1836 | -9 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1811 |  | 1836 | -25 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1772 |  | 1836 | -64 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1772 |  | 1836 | -64 | 97 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1540 |  | 1600 | -60 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1714 |  | 1836 | -122 | 93 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -927 |  | -999 | -72 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 |  | 1836 | -136 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1699 |  | 1836 | -137 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1691 |  | 1836 | -145 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 |  | 1836 | -152 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1462 |  | 1600 | -138 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1652 |  | 1836 | -184 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1374 |  | 1600 | -226 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1274 |  | 1600 | -326 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1239 |  | 1600 | -361 | 77 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1239 |  | 1600 | -361 | 77 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1233 |  | 1601 | -368 | 77 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1233 |  | 1601 | -368 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1193 |  | 1600 | -407 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1176 |  | 1600 | -424 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1176 |  | 1600 | -424 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1171 |  | 1601 | -430 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1171 |  | 1601 | -430 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -874 |  | -1248 | -374 | 70 | []

## 1330Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3475
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 | 1836 | 1836 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1827 | 1836 | 1836 | -9 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1827 | 1836 | 1836 | -9 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1822 | 1836 | 1836 | -14 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1540 | 1600 | 1600 | -60 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1744 | 1836 | 1836 | -92 | 95 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 | 1836 | 1836 | -106 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1724 | 1836 | 1836 | -112 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1720 | 1836 | 1836 | -116 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1713 | 1836 | 1836 | -123 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 | 1836 | 1836 | -151 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1460 | 1600 | 1600 | -140 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1460 | 1600 | 1600 | -140 | 91 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1455 | 1601 | 1601 | -146 | 91 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1455 | 1601 | 1601 | -146 | 91 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -905 | -999 | -999 | -94 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1447 | 1600 | 1600 | -153 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1388 | 1600 | 1600 | -212 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1318 | 1600 | 1600 | -282 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1318 | 1600 | 1600 | -282 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1312 | 1601 | 1601 | -289 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1312 | 1601 | 1601 | -289 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1310 | 1600 | 1600 | -290 | 82 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1229 | 1600 | 1600 | -371 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -924 | -1248 | -1248 | -324 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -921 | -1248 | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -920 | -1248 | -1248 | -329 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -910 | -1248 | -1248 | -338 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -910 | -1248 | -1248 | -339 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -904 | -1248 | -1248 | -345 | 72 | []

## 1330Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3475
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 |  | 1836 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1827 |  | 1836 | -9 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1827 |  | 1836 | -9 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1822 |  | 1836 | -14 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1540 |  | 1600 | -60 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1744 |  | 1836 | -92 | 95 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 |  | 1836 | -106 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1724 |  | 1836 | -112 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1720 |  | 1836 | -116 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1713 |  | 1836 | -123 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 |  | 1836 | -151 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1460 |  | 1600 | -140 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1460 |  | 1600 | -140 | 91 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1455 |  | 1601 | -146 | 91 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1455 |  | 1601 | -146 | 91 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -905 |  | -999 | -94 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1447 |  | 1600 | -153 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1388 |  | 1600 | -212 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1318 |  | 1600 | -282 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1318 |  | 1600 | -282 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1312 |  | 1601 | -289 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1312 |  | 1601 | -289 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1310 |  | 1600 | -290 | 82 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1229 |  | 1600 | -371 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -924 |  | -1248 | -324 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -921 |  | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -920 |  | -1248 | -329 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -910 |  | -1248 | -338 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -910 |  | -1248 | -339 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -904 |  | -1248 | -345 | 72 | []

## 1430Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3408
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1512 | 1600 | 1600 | -88 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1445 | 1600 | 1600 | -155 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1343 | 1600 | 1600 | -257 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1298 | 1600 | 1600 | -302 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1298 | 1600 | 1600 | -302 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1292 | 1601 | 1601 | -309 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1292 | 1601 | 1601 | -309 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 | 1836 | 1836 | -378 | 79 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 | 1836 | 1836 | -378 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1428 | 1836 | 1836 | -408 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 | 1836 | 1836 | -412 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -965 | -1248 | -1248 | -284 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -963 | -1248 | -1248 | -285 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -960 | -1248 | -1248 | -288 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -955 | -1248 | -1248 | -294 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -953 | -1248 | -1248 | -296 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -948 | -1248 | -1248 | -300 | 76 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1352 | 1836 | 1836 | -484 | 74 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1332 | 1836 | 1836 | -504 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -725 | -999 | -999 | -274 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1159 | 1600 | 1600 | -441 | 72 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1325 | 1836 | 1836 | -511 | 72 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1322 | 1836 | 1836 | -514 | 72 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1321 | 1836 | 1836 | -515 | 72 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1304 | 1836 | 1836 | -532 | 71 | []

## 1430Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3408
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 |  | 1600 | -5 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 |  | 1600 | -5 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1512 |  | 1600 | -88 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1445 |  | 1600 | -155 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1343 |  | 1600 | -257 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1298 |  | 1600 | -302 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1298 |  | 1600 | -302 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1292 |  | 1601 | -309 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1292 |  | 1601 | -309 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 |  | 1836 | -378 | 79 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 |  | 1836 | -378 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1428 |  | 1836 | -408 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 |  | 1836 | -412 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -965 |  | -1248 | -284 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -963 |  | -1248 | -285 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -960 |  | -1248 | -288 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1227 |  | 1600 | -373 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -955 |  | -1248 | -294 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -953 |  | -1248 | -296 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -948 |  | -1248 | -300 | 76 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1352 |  | 1836 | -484 | 74 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1332 |  | 1836 | -504 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -725 |  | -999 | -274 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1159 |  | 1600 | -441 | 72 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1325 |  | 1836 | -511 | 72 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1322 |  | 1836 | -514 | 72 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1321 |  | 1836 | -515 | 72 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1304 |  | 1836 | -532 | 71 | []

## 1530Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3186
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1591 | 1601 | 1601 | -10 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1591 | 1601 | 1601 | -10 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1525 | 1600 | 1600 | -75 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1486 | 1600 | 1600 | -114 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1329 | 1600 | 1600 | -271 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1203 | 1600 | 1600 | -397 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1203 | 1600 | 1600 | -397 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1197 | 1601 | 1601 | -404 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1197 | 1601 | 1601 | -404 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -916 | -1248 | -1248 | -333 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -915 | -1248 | -1248 | -333 | 73 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1173 | 1600 | 1600 | -427 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -911 | -1248 | -1248 | -337 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -909 | -1248 | -1248 | -339 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -905 | -1248 | -1248 | -343 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -903 | -1248 | -1248 | -345 | 72 | []

## 1530Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3186
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 |  | 1600 | -5 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 |  | 1600 | -5 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1591 |  | 1601 | -10 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1591 |  | 1601 | -10 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1525 |  | 1600 | -75 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1486 |  | 1600 | -114 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1329 |  | 1600 | -271 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1203 |  | 1600 | -397 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1203 |  | 1600 | -397 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1197 |  | 1601 | -404 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1197 |  | 1601 | -404 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -916 |  | -1248 | -333 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -915 |  | -1248 | -333 | 73 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1173 |  | 1600 | -427 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -911 |  | -1248 | -337 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -909 |  | -1248 | -339 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -905 |  | -1248 | -343 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -903 |  | -1248 | -345 | 72 | []

## 1630Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3128
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1552 | 1600 | 1600 | -48 | 97 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1512 | 1600 | 1600 | -88 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1353 | 1600 | 1600 | -247 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1204 | 1600 | 1600 | -396 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1204 | 1600 | 1600 | -396 | 75 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1200 | 1600 | 1600 | -400 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -935 | -1248 | -1248 | -313 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -935 | -1248 | -1248 | -313 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1198 | 1601 | 1601 | -403 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1198 | 1601 | 1601 | -403 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -931 | -1248 | -1248 | -317 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -928 | -1248 | -1248 | -320 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -925 | -1248 | -1248 | -324 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -922 | -1248 | -1248 | -326 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1382 | -1920 | -1920 | -538 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1133 | 1600 | 1600 | -467 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3128
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 |  | 1600 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 |  | 1600 | 0 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 |  | 1601 | -6 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 |  | 1601 | -6 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1552 |  | 1600 | -48 | 97 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1512 |  | 1600 | -88 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1353 |  | 1600 | -247 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1204 |  | 1600 | -396 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1204 |  | 1600 | -396 | 75 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1200 |  | 1600 | -400 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -935 |  | -1248 | -313 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -935 |  | -1248 | -313 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1198 |  | 1601 | -403 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1198 |  | 1601 | -403 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -931 |  | -1248 | -317 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -928 |  | -1248 | -320 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -925 |  | -1248 | -324 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -922 |  | -1248 | -326 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1382 |  | -1920 | -538 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1133 |  | 1600 | -467 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3035
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1457 | 1600 | 1600 | -143 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1372 | 1600 | 1600 | -228 | 86 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1310 | 1600 | 1600 | -290 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1203 | 1600 | 1600 | -397 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1196 | 1600 | 1600 | -404 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1196 | 1600 | 1600 | -404 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1190 | 1601 | 1601 | -411 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1190 | 1601 | 1601 | -411 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -921 | -1248 | -1248 | -328 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -921 | -1248 | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -916 | -1248 | -1248 | -332 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -914 | -1248 | -1248 | -335 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -910 | -1248 | -1248 | -338 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -908 | -1248 | -1248 | -341 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1153 | 1600 | 1600 | -447 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1371 | -1920 | -1920 | -549 | 71 | []

## 1730Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3035
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 |  | 1600 | -7 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 |  | 1600 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1457 |  | 1600 | -143 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1372 |  | 1600 | -228 | 86 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1310 |  | 1600 | -290 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1203 |  | 1600 | -397 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1196 |  | 1600 | -404 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1196 |  | 1600 | -404 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1190 |  | 1601 | -411 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1190 |  | 1601 | -411 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -921 |  | -1248 | -328 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -921 |  | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -916 |  | -1248 | -332 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -914 |  | -1248 | -335 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -910 |  | -1248 | -338 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -908 |  | -1248 | -341 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1153 |  | 1600 | -447 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1371 |  | -1920 | -549 | 71 | []

## 1830Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3121
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 | 1601 | 1601 | -8 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 | 1601 | 1601 | -8 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1446 | 1600 | 1600 | -154 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1346 | 1600 | 1600 | -254 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1313 | 1600 | 1600 | -287 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1226 | 1600 | 1600 | -374 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1203 | 1600 | 1600 | -397 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1203 | 1600 | 1600 | -397 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1198 | 1601 | 1601 | -403 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1198 | 1601 | 1601 | -403 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1177 | 1600 | 1600 | -423 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -889 | -1248 | -1248 | -360 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -889 | -1248 | -1248 | -360 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -885 | -1248 | -1248 | -364 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -883 | -1248 | -1248 | -366 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -879 | -1248 | -1248 | -370 | 70 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -877 | -1248 | -1248 | -372 | 70 | []

## 1830Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3121
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 |  | 1600 | -2 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 |  | 1600 | -2 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 |  | 1601 | -8 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 |  | 1601 | -8 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1446 |  | 1600 | -154 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1346 |  | 1600 | -254 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1313 |  | 1600 | -287 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1226 |  | 1600 | -374 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1203 |  | 1600 | -397 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1203 |  | 1600 | -397 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1198 |  | 1601 | -403 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1198 |  | 1601 | -403 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1177 |  | 1600 | -423 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -889 |  | -1248 | -360 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -889 |  | -1248 | -360 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -885 |  | -1248 | -364 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -883 |  | -1248 | -366 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -879 |  | -1248 | -370 | 70 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -877 |  | -1248 | -372 | 70 | []

## 1930Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2988
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1594 | 1601 | 1601 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1594 | 1601 | 1601 | -7 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1494 | 1600 | 1600 | -106 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1404 | 1600 | 1600 | -196 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1344 | 1600 | 1600 | -256 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1237 | 1600 | 1600 | -363 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1190 | 1600 | 1600 | -410 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1190 | 1600 | 1600 | -410 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1184 | 1601 | 1601 | -417 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1184 | 1601 | 1601 | -417 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1183 | 1600 | 1600 | -417 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -910 | -1248 | -1248 | -338 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -910 | -1248 | -1248 | -339 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -906 | -1248 | -1248 | -343 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -904 | -1248 | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -900 | -1248 | -1248 | -349 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -897 | -1248 | -1248 | -351 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1369 | -1920 | -1920 | -551 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2988
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1599 |  | 1600 | -1 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1599 |  | 1600 | -1 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1594 |  | 1601 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1594 |  | 1601 | -7 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1494 |  | 1600 | -106 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1404 |  | 1600 | -196 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1344 |  | 1600 | -256 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1237 |  | 1600 | -363 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1190 |  | 1600 | -410 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1190 |  | 1600 | -410 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1184 |  | 1601 | -417 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1184 |  | 1601 | -417 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1183 |  | 1600 | -417 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -910 |  | -1248 | -338 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -910 |  | -1248 | -339 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -906 |  | -1248 | -343 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -904 |  | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -900 |  | -1248 | -349 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -897 |  | -1248 | -351 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1369 |  | -1920 | -551 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2962
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1546 | 1600 | 1600 | -54 | 97 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1478 | 1600 | 1600 | -122 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1372 | 1600 | 1600 | -228 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1243 | 1600 | 1600 | -357 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1181 | 1600 | 1600 | -419 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1172 | 1601 | 1601 | -429 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1172 | 1601 | 1601 | -429 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1351 | -1920 | -1920 | -569 | 70 | []

## 2030Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2962
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1594 |  | 1600 | -6 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 |  | 1600 | -6 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1546 |  | 1600 | -54 | 97 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1478 |  | 1600 | -122 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1372 |  | 1600 | -228 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1243 |  | 1600 | -357 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1181 |  | 1600 | -419 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1178 |  | 1600 | -422 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1178 |  | 1600 | -422 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1172 |  | 1601 | -429 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1172 |  | 1601 | -429 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1351 |  | -1920 | -569 | 70 | []

## 2130Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2954
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1591 | 1601 | 1601 | -10 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1591 | 1601 | 1601 | -10 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1488 | 1600 | 1600 | -112 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1401 | 1600 | 1600 | -199 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1339 | 1600 | 1600 | -261 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1237 | 1600 | 1600 | -363 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1195 | 1600 | 1600 | -405 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1195 | 1600 | 1600 | -405 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1190 | 1601 | 1601 | -411 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1190 | 1601 | 1601 | -411 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1180 | 1600 | 1600 | -420 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1360 | -1920 | -1920 | -560 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2954
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1596 |  | 1600 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1596 |  | 1600 | -4 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1591 |  | 1601 | -10 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1591 |  | 1601 | -10 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1488 |  | 1600 | -112 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1401 |  | 1600 | -199 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1339 |  | 1600 | -261 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1237 |  | 1600 | -363 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1195 |  | 1600 | -405 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1195 |  | 1600 | -405 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1190 |  | 1601 | -411 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1190 |  | 1601 | -411 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1180 |  | 1600 | -420 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1360 |  | -1920 | -560 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3129
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1343 | 1600 | 1600 | -257 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1252 | 1600 | 1600 | -348 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1252 | 1600 | 1600 | -348 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1247 | 1601 | 1601 | -354 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1247 | 1601 | 1601 | -354 | 78 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1245 | 1600 | 1600 | -355 | 78 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1226 | 1600 | 1600 | -374 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1193 | 1600 | 1600 | -407 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -744 | -999 | -999 | -256 | 74 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1321 | -1836 | -1836 | -515 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1150 | 1600 | 1600 | -450 | 72 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1300 | -1836 | -1836 | -536 | 71 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1300 | -1836 | -1836 | -536 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -876 | -1248 | -1248 | -372 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -875 | -1248 | -1248 | -373 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3129
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 |  | 1600 | -7 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 |  | 1600 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1343 |  | 1600 | -257 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1252 |  | 1600 | -348 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1252 |  | 1600 | -348 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1247 |  | 1601 | -354 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1247 |  | 1601 | -354 | 78 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1245 |  | 1600 | -355 | 78 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1226 |  | 1600 | -374 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1193 |  | 1600 | -407 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -744 |  | -999 | -256 | 74 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1321 |  | -1836 | -515 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1150 |  | 1600 | -450 | 72 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1300 |  | -1836 | -536 | 71 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1300 |  | -1836 | -536 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -876 |  | -1248 | -372 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -875 |  | -1248 | -373 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3211
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1374 | 1600 | 1600 | -226 | 86 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1268 | 1600 | 1600 | -332 | 79 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1263 | 1600 | 1600 | -337 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1254 | 1601 | 1601 | -347 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1254 | 1601 | 1601 | -347 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -777 | -999 | -999 | -222 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1199 | 1600 | 1600 | -401 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1354 | -1836 | -1836 | -482 | 74 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1336 | -1836 | -1836 | -500 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1336 | -1836 | -1836 | -500 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1149 | 1600 | 1600 | -451 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -889 | -1248 | -1248 | -359 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -888 | -1248 | -1248 | -361 | 71 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1302 | -1836 | -1836 | -534 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -885 | -1248 | -1248 | -364 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -880 | -1248 | -1248 | -369 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -878 | -1248 | -1248 | -371 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2024-01-03 21:07
Business day: | 05.01.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3211
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 |  | 1600 | -7 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 |  | 1600 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1374 |  | 1600 | -226 | 86 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1268 |  | 1600 | -332 | 79 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1263 |  | 1600 | -337 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1258 |  | 1600 | -342 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1258 |  | 1600 | -342 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1254 |  | 1601 | -347 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1254 |  | 1601 | -347 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -777 |  | -999 | -222 | 78 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1199 |  | 1600 | -401 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1354 |  | -1836 | -482 | 74 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1336 |  | -1836 | -500 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1336 |  | -1836 | -500 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1149 |  | 1600 | -451 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -889 |  | -1248 | -359 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -888 |  | -1248 | -361 | 71 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1302 |  | -1836 | -534 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -885 |  | -1248 | -364 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -880 |  | -1248 | -369 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -878 |  | -1248 | -371 | 70 | []