## 1230Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3341
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1829 | 1836 | 1836 | -7 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1823 | 1836 | 1836 | -13 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1796 | 1836 | 1836 | -40 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1796 | 1836 | 1836 | -40 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1775 | 1836 | 1836 | -61 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1775 | 1836 | 1836 | -61 | 97 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1719 | 1836 | 1836 | -117 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1712 | 1836 | 1836 | -124 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1707 | 1836 | 1836 | -129 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 | 1836 | 1836 | -152 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1389 | 1600 | 1600 | -211 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1305 | 1600 | 1600 | -295 | 82 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1231 | 1600 | 1600 | -369 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -911 | -1248 | -1248 | -338 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -907 | -1248 | -1248 | -342 | 73 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -906 | -1248 | -1248 | -342 | 73 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1156 | 1601 | 1601 | -445 | 72 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1156 | 1601 | 1601 | -445 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -897 | -1248 | -1248 | -352 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -897 | -1248 | -1248 | -352 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -890 | -1248 | -1248 | -358 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1142 | 1601 | 1601 | -459 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1142 | 1601 | 1601 | -459 | 71 | []

## 1230Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3341
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1829 |  | 1836 | -7 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1823 |  | 1836 | -13 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1796 |  | 1836 | -40 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1796 |  | 1836 | -40 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1775 |  | 1836 | -61 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1775 |  | 1836 | -61 | 97 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1719 |  | 1836 | -117 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1712 |  | 1836 | -124 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1707 |  | 1836 | -129 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 |  | 1836 | -152 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1389 |  | 1600 | -211 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1305 |  | 1600 | -295 | 82 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1231 |  | 1600 | -369 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -911 |  | -1248 | -338 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -907 |  | -1248 | -342 | 73 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1161 |  | 1600 | -439 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1161 |  | 1600 | -439 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -906 |  | -1248 | -342 | 73 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1156 |  | 1601 | -445 | 72 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1156 |  | 1601 | -445 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -897 |  | -1248 | -352 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -897 |  | -1248 | -352 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1147 |  | 1600 | -453 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1147 |  | 1600 | -453 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -890 |  | -1248 | -358 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1142 |  | 1601 | -459 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1142 |  | 1601 | -459 | 71 | []

## 1330Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3345
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1832 | 1836 | 1836 | -4 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1827 | 1836 | 1836 | -9 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1802 | 1836 | 1836 | -34 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1802 | 1836 | 1836 | -34 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1785 | 1836 | 1836 | -51 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1782 | 1836 | 1836 | -54 | 97 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1726 | 1836 | 1836 | -110 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1717 | 1836 | 1836 | -119 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1714 | 1836 | 1836 | -122 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1690 | 1836 | 1836 | -146 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1380 | 1600 | 1600 | -220 | 86 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1296 | 1600 | 1600 | -304 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1225 | 1600 | 1600 | -375 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -920 | -1248 | -1248 | -329 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -916 | -1248 | -1248 | -332 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -915 | -1248 | -1248 | -333 | 73 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -906 | -1248 | -1248 | -343 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -906 | -1248 | -1248 | -343 | 73 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1160 | 1601 | 1601 | -441 | 72 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1160 | 1601 | 1601 | -441 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -900 | -1248 | -1248 | -349 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1151 | 1600 | 1600 | -449 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1151 | 1600 | 1600 | -449 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1146 | 1601 | 1601 | -455 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1146 | 1601 | 1601 | -455 | 72 | []

## 1330Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3345
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1832 |  | 1836 | -4 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1827 |  | 1836 | -9 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1802 |  | 1836 | -34 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1802 |  | 1836 | -34 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1785 |  | 1836 | -51 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1782 |  | 1836 | -54 | 97 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1726 |  | 1836 | -110 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1717 |  | 1836 | -119 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1714 |  | 1836 | -122 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1690 |  | 1836 | -146 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1380 |  | 1600 | -220 | 86 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1296 |  | 1600 | -304 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1225 |  | 1600 | -375 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -920 |  | -1248 | -329 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -916 |  | -1248 | -332 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -915 |  | -1248 | -333 | 73 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1166 |  | 1600 | -434 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1166 |  | 1600 | -434 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -906 |  | -1248 | -343 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -906 |  | -1248 | -343 | 73 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1160 |  | 1601 | -441 | 72 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1160 |  | 1601 | -441 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -900 |  | -1248 | -349 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1151 |  | 1600 | -449 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1151 |  | 1600 | -449 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1146 |  | 1601 | -455 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1146 |  | 1601 | -455 | 72 | []

## 1430Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3537
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1561 | 1600 | 1600 | -39 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 | 1836 | 1836 | -79 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 | 1836 | 1836 | -79 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1487 | 1600 | 1600 | -113 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1487 | 1600 | 1600 | -113 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 | 1836 | 1836 | -130 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 | 1836 | 1836 | -132 | 93 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1482 | 1601 | 1601 | -119 | 93 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1482 | 1601 | 1601 | -119 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1472 | 1600 | 1600 | -128 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 | 1836 | 1836 | -177 | 90 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1637 | 1836 | 1836 | -199 | 89 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1633 | 1836 | 1836 | -203 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1632 | 1836 | 1836 | -204 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1629 | 1836 | 1836 | -207 | 89 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1612 | 1836 | 1836 | -224 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1398 | 1600 | 1600 | -202 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1323 | 1600 | 1600 | -277 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1323 | 1600 | 1600 | -277 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1318 | 1601 | 1601 | -283 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1318 | 1601 | 1601 | -283 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1012 | -1248 | -1248 | -237 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1009 | -1248 | -1248 | -240 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1293 | 1600 | 1600 | -307 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1007 | -1248 | -1248 | -241 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -999 | -1248 | -1248 | -250 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -998 | -1248 | -1248 | -250 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -992 | -1248 | -1248 | -256 | 79 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1253 | 1600 | 1600 | -347 | 78 | []

## 1430Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3537
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1561 |  | 1600 | -39 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 |  | 1836 | -79 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 |  | 1836 | -79 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1487 |  | 1600 | -113 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1487 |  | 1600 | -113 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 |  | 1836 | -130 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 |  | 1836 | -132 | 93 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1482 |  | 1601 | -119 | 93 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1482 |  | 1601 | -119 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1472 |  | 1600 | -128 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 |  | 1836 | -177 | 90 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1637 |  | 1836 | -199 | 89 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1633 |  | 1836 | -203 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1632 |  | 1836 | -204 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1629 |  | 1836 | -207 | 89 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1612 |  | 1836 | -224 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1398 |  | 1600 | -202 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1323 |  | 1600 | -277 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1323 |  | 1600 | -277 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1318 |  | 1601 | -283 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1318 |  | 1601 | -283 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1012 |  | -1248 | -237 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1009 |  | -1248 | -240 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1293 |  | 1600 | -307 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1007 |  | -1248 | -241 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -999 |  | -1248 | -250 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -998 |  | -1248 | -250 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -992 |  | -1248 | -256 | 79 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1253 |  | 1600 | -347 | 78 | []

## 1530Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3508
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1574 | 1600 | 1600 | -26 | 98 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1494 | 1600 | 1600 | -106 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 | 1836 | 1836 | -140 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 | 1836 | 1836 | -140 | 92 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1653 | 1836 | 1836 | -183 | 90 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1652 | 1836 | 1836 | -184 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1436 | 1600 | 1600 | -164 | 90 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1436 | 1600 | 1600 | -164 | 90 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1431 | 1601 | 1601 | -170 | 89 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1431 | 1601 | 1601 | -170 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1404 | 1600 | 1600 | -196 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 | 1836 | 1836 | -233 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1581 | 1836 | 1836 | -255 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1578 | 1836 | 1836 | -258 | 86 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1575 | 1836 | 1836 | -261 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1570 | 1836 | 1836 | -266 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1555 | 1836 | 1836 | -281 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1012 | -1248 | -1248 | -236 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1294 | 1600 | 1600 | -306 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1009 | -1248 | -1248 | -239 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1007 | -1248 | -1248 | -241 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1000 | -1248 | -1248 | -249 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -999 | -1248 | -1248 | -250 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1278 | 1600 | 1600 | -322 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1278 | 1600 | 1600 | -322 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -993 | -1248 | -1248 | -255 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1273 | 1601 | 1601 | -328 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1273 | 1601 | 1601 | -328 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1252 | 1600 | 1600 | -348 | 78 | []

## 1530Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3508
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1574 |  | 1600 | -26 | 98 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1494 |  | 1600 | -106 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 |  | 1836 | -140 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 |  | 1836 | -140 | 92 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1653 |  | 1836 | -183 | 90 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1652 |  | 1836 | -184 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1436 |  | 1600 | -164 | 90 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1436 |  | 1600 | -164 | 90 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1431 |  | 1601 | -170 | 89 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1431 |  | 1601 | -170 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1404 |  | 1600 | -196 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 |  | 1836 | -233 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1581 |  | 1836 | -255 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1578 |  | 1836 | -258 | 86 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1575 |  | 1836 | -261 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1570 |  | 1836 | -266 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1555 |  | 1836 | -281 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1012 |  | -1248 | -236 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1294 |  | 1600 | -306 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1009 |  | -1248 | -239 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1007 |  | -1248 | -241 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1000 |  | -1248 | -249 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -999 |  | -1248 | -250 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1278 |  | 1600 | -322 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1278 |  | 1600 | -322 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -993 |  | -1248 | -255 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1273 |  | 1601 | -328 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1273 |  | 1601 | -328 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1252 |  | 1600 | -348 | 78 | []

## 1630Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2966
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1530 | 1600 | 1600 | -70 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1411 | 1600 | 1600 | -189 | 88 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1278 | 1600 | 1600 | -322 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1241 | 1600 | 1600 | -359 | 78 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -961 | -1248 | -1248 | -288 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -959 | -1248 | -1248 | -289 | 77 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1226 | 1601 | 1601 | -375 | 77 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1226 | 1601 | 1601 | -375 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -956 | -1248 | -1248 | -292 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -952 | -1248 | -1248 | -297 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -949 | -1248 | -1248 | -300 | 76 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1392 | 1836 | 1836 | -444 | 76 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1392 | 1836 | 1836 | -444 | 76 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1392 | 1836 | 1836 | -444 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -945 | -1248 | -1248 | -303 | 76 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1384 | 1836 | 1836 | -452 | 75 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1312 | 1836 | 1836 | -524 | 71 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1294 | 1836 | 1836 | -542 | 70 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1288 | 1836 | 1836 | -548 | 70 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1287 | 1836 | 1836 | -549 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2966
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1530 |  | 1600 | -70 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1411 |  | 1600 | -189 | 88 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1278 |  | 1600 | -322 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1241 |  | 1600 | -359 | 78 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1232 |  | 1600 | -368 | 77 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1232 |  | 1600 | -368 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -961 |  | -1248 | -288 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -959 |  | -1248 | -289 | 77 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1226 |  | 1601 | -375 | 77 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1226 |  | 1601 | -375 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -956 |  | -1248 | -292 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -952 |  | -1248 | -297 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -949 |  | -1248 | -300 | 76 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1392 |  | 1836 | -444 | 76 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1392 |  | 1836 | -444 | 76 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1392 |  | 1836 | -444 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -945 |  | -1248 | -303 | 76 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1384 |  | 1836 | -452 | 75 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1312 |  | 1836 | -524 | 71 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1294 |  | 1836 | -542 | 70 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1288 |  | 1836 | -548 | 70 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1287 |  | 1836 | -549 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2331
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1533 | 1600 | 1600 | -67 | 96 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1438 | 1600 | 1600 | -162 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1433 | 1601 | 1601 | -168 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1406 | 1600 | 1600 | -194 | 88 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1547 | 1836 | 1836 | -289 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1257 | 1600 | 1600 | -343 | 79 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1197 | 1600 | 1600 | -403 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1315 | 1836 | 1836 | -521 | 72 | []

## 1730Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2331
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1533 |  | 1600 | -67 | 96 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1438 |  | 1600 | -162 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1433 |  | 1601 | -168 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1406 |  | 1600 | -194 | 88 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1547 |  | 1836 | -289 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1257 |  | 1600 | -343 | 79 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1197 |  | 1600 | -403 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1315 |  | 1836 | -521 | 72 | []

## 1830Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2502
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1548 | 1600 | 1600 | -52 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1543 | 1601 | 1601 | -58 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1539 | 1600 | 1600 | -61 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1398 | 1600 | 1600 | -202 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1548 | 1836 | 1836 | -288 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1238 | 1600 | 1600 | -362 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1178 | 1600 | 1600 | -422 | 74 | []

## 1830Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2502
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1597 |  | 1600 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1548 |  | 1600 | -52 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1543 |  | 1601 | -58 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1539 |  | 1600 | -61 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1398 |  | 1600 | -202 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1548 |  | 1836 | -288 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1238 |  | 1600 | -362 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1178 |  | 1600 | -422 | 74 | []

## 1930Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2616
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1546 | 1600 | 1600 | -54 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1399 | 1600 | 1600 | -201 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1241 | 1600 | 1600 | -359 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1176 | 1600 | 1600 | -424 | 74 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1160 | 1601 | 1601 | -441 | 72 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1160 | 1601 | 1601 | -441 | 72 | []

## 1930Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2616
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1546 |  | 1600 | -54 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1399 |  | 1600 | -201 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1241 |  | 1600 | -359 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1176 |  | 1600 | -424 | 74 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1166 |  | 1600 | -434 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1166 |  | 1600 | -434 | 73 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1160 |  | 1601 | -441 | 72 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1160 |  | 1601 | -441 | 72 | []

## 2030Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2789
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1547 | 1600 | 1600 | -53 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1402 | 1600 | 1600 | -198 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1333 | 1600 | 1600 | -267 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1333 | 1600 | 1600 | -267 | 83 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1327 | 1601 | 1601 | -274 | 83 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1327 | 1601 | 1601 | -274 | 83 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1250 | 1600 | 1600 | -350 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1186 | 1600 | 1600 | -414 | 74 | []

## 2030Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2789
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1547 |  | 1600 | -53 | 97 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1402 |  | 1600 | -198 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1333 |  | 1600 | -267 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1333 |  | 1600 | -267 | 83 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1327 |  | 1601 | -274 | 83 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1327 |  | 1601 | -274 | 83 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1250 |  | 1600 | -350 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1186 |  | 1600 | -414 | 74 | []

## 2130Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3291
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1554 | 1600 | 1600 | -46 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1489 | 1600 | 1600 | -111 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1489 | 1600 | 1600 | -111 | 93 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1484 | 1601 | 1601 | -117 | 93 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1484 | 1601 | 1601 | -117 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1371 | 1600 | 1600 | -229 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1243 | 1600 | 1600 | -357 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1415 | -1836 | -1836 | -421 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1206 | 1601 | 1601 | -395 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1206 | 1601 | 1601 | -395 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1195 | 1600 | 1600 | -405 | 75 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1361 | -1836 | -1836 | -475 | 74 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1361 | -1836 | -1836 | -475 | 74 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1361 | -1836 | -1836 | -475 | 74 | []

## 2130Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3291
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1554 |  | 1600 | -46 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1489 |  | 1600 | -111 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1489 |  | 1600 | -111 | 93 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1484 |  | 1601 | -117 | 93 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1484 |  | 1601 | -117 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1371 |  | 1600 | -229 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1243 |  | 1600 | -357 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1415 |  | -1836 | -421 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1211 |  | 1600 | -389 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1211 |  | 1600 | -389 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1206 |  | 1601 | -395 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1206 |  | 1601 | -395 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1195 |  | 1600 | -405 | 75 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1361 |  | -1836 | -475 | 74 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1361 |  | -1836 | -475 | 74 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1361 |  | -1836 | -475 | 74 | []

## 2230Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3254
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1592 | 1600 | 1600 | -8 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1592 | 1600 | 1600 | -8 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1505 | 1600 | 1600 | -95 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1439 | 1600 | 1600 | -161 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1337 | 1600 | 1600 | -263 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1224 | 1600 | 1600 | -376 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1224 | 1600 | 1600 | -376 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1219 | 1601 | 1601 | -382 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1219 | 1601 | 1601 | -382 | 76 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1210 | 1600 | 1600 | -390 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1152 | 1600 | 1600 | -448 | 72 | []

## 2230Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3254
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1592 |  | 1600 | -8 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1592 |  | 1600 | -8 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1505 |  | 1600 | -95 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1439 |  | 1600 | -161 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1337 |  | 1600 | -263 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1224 |  | 1600 | -376 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1224 |  | 1600 | -376 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1219 |  | 1601 | -382 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1219 |  | 1601 | -382 | 76 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1210 |  | 1600 | -390 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1152 |  | 1600 | -448 | 72 | []

## 2330Preventive
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3329
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1591 | 1601 | 1601 | -10 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1591 | 1601 | 1601 | -10 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1468 | 1600 | 1600 | -132 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1399 | 1600 | 1600 | -201 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1305 | 1600 | 1600 | -295 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1234 | 1601 | 1601 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1234 | 1601 | 1601 | -367 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1186 | 1600 | 1600 | -414 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -887 | -1248 | -1248 | -362 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -886 | -1248 | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -883 | -1248 | -1248 | -366 | 71 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1127 | 1600 | 1600 | -473 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -880 | -1248 | -1248 | -369 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -876 | -1248 | -1248 | -372 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2024-01-10 08:14
Business day: | 10.01.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3329
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 |  | 1600 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1597 |  | 1600 | -3 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1591 |  | 1601 | -10 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1591 |  | 1601 | -10 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1468 |  | 1600 | -132 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1399 |  | 1600 | -201 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1305 |  | 1600 | -295 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1240 |  | 1600 | -360 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1240 |  | 1600 | -360 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1234 |  | 1601 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1234 |  | 1601 | -367 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1186 |  | 1600 | -414 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -887 |  | -1248 | -362 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -886 |  | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -883 |  | -1248 | -366 | 71 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1127 |  | 1600 | -473 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -880 |  | -1248 | -369 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -876 |  | -1248 | -372 | 70 | []