## 1230Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2868
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1525 | 1600 | 1600 | -75 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1520 | 1600 | 1600 | -80 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1487 | 1600 | 1600 | -113 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1461 | 1600 | 1600 | -139 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1460 | 1600 | 1600 | -140 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1360 | 1600 | 1600 | -240 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1358 | 1600 | 1600 | -242 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 | 1600 | 1600 | -276 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1306 | 1600 | 1600 | -294 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1297 | 1600 | 1600 | -303 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1280 | 1600 | 1600 | -320 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 | 1600 | 1600 | -328 | 80 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 | 1600 | 1600 | -338 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1250 | 1600 | 1600 | -350 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1217 | 1600 | 1600 | -383 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1123 | 1600 | 1600 | -477 | 70 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1123 | 1600 | 1600 | -477 | 70 | []

## 1230Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2868
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 |  | 1600 | -3 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1525 |  | 1600 | -75 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1520 |  | 1600 | -80 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1487 |  | 1600 | -113 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1461 |  | 1600 | -139 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1460 |  | 1600 | -140 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1360 |  | 1600 | -240 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1358 |  | 1600 | -242 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1324 |  | 1600 | -276 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1306 |  | 1600 | -294 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1297 |  | 1600 | -303 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1280 |  | 1600 | -320 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 |  | 1600 | -328 | 80 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 |  | 1600 | -338 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 |  | 1600 | -349 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 |  | 1600 | -349 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1250 |  | 1600 | -350 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1217 |  | 1600 | -383 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1183 |  | 1600 | -417 | 74 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1123 |  | 1600 | -477 | 70 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1123 |  | 1600 | -477 | 70 | []

## 1330Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2882
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1590 | 1600 | 1600 | -10 | 99 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1524 | 1600 | 1600 | -76 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1517 | 1600 | 1600 | -83 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1475 | 1600 | 1600 | -125 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1458 | 1600 | 1600 | -142 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1456 | 1600 | 1600 | -144 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 | 1600 | 1600 | -247 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 | 1600 | 1600 | -247 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1315 | 1600 | 1600 | -285 | 82 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1273 | 1600 | 1600 | -327 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 | 1600 | 1600 | -393 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1169 | 1600 | 1600 | -431 | 73 | []

## 1330Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2882
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1590 |  | 1600 | -10 | 99 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1524 |  | 1600 | -76 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1517 |  | 1600 | -83 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1475 |  | 1600 | -125 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1458 |  | 1600 | -142 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1456 |  | 1600 | -144 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 |  | 1600 | -247 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 |  | 1600 | -247 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1315 |  | 1600 | -285 | 82 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 |  | 1600 | -298 | 81 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1273 |  | 1600 | -327 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1253 |  | 1600 | -347 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 |  | 1600 | -393 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1169 |  | 1600 | -431 | 73 | []

## 1430Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2827
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1521 | 1600 | 1600 | -79 | 95 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1503 | 1600 | 1600 | -97 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1476 | 1600 | 1600 | -124 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1438 | 1600 | 1600 | -162 | 90 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1433 | 1600 | 1600 | -167 | 90 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1349 | 1600 | 1600 | -251 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 | 1600 | 1600 | -270 | 83 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1288 | 1600 | 1600 | -312 | 80 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1279 | 1600 | 1600 | -321 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 | 1600 | 1600 | -393 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1203 | 1600 | 1600 | -397 | 75 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1196 | 1600 | 1600 | -404 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1152 | 1600 | 1600 | -448 | 72 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1121 | 1600 | 1600 | -479 | 70 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1120 | 1600 | 1600 | -480 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2827
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 |  | 1600 | -3 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1521 |  | 1600 | -79 | 95 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1503 |  | 1600 | -97 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1476 |  | 1600 | -124 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1438 |  | 1600 | -162 | 90 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1433 |  | 1600 | -167 | 90 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1349 |  | 1600 | -251 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1330 |  | 1600 | -270 | 83 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1288 |  | 1600 | -312 | 80 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1279 |  | 1600 | -321 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 |  | 1600 | -393 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1203 |  | 1600 | -397 | 75 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1196 |  | 1600 | -404 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1152 |  | 1600 | -448 | 72 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1121 |  | 1600 | -479 | 70 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1120 |  | 1600 | -480 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2779
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1522 | 1600 | 1600 | -78 | 95 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1455 | 1600 | 1600 | -145 | 91 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1445 | 1600 | 1600 | -155 | 90 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1396 | 1600 | 1600 | -204 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1380 | 1600 | 1600 | -220 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1317 | 1600 | 1600 | -283 | 82 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1202 | 1600 | 1600 | -398 | 75 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1200 | 1600 | 1600 | -400 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1198 | 1600 | 1600 | -402 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1172 | 1600 | 1600 | -428 | 73 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1171 | 1600 | 1600 | -429 | 73 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1169 | 1600 | 1600 | -431 | 73 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []

## 1530Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2779
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1522 |  | 1600 | -78 | 95 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1455 |  | 1600 | -145 | 91 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1445 |  | 1600 | -155 | 90 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1396 |  | 1600 | -204 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1380 |  | 1600 | -220 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1317 |  | 1600 | -283 | 82 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1290 |  | 1600 | -310 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 |  | 1600 | -349 | 78 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1202 |  | 1600 | -398 | 75 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1200 |  | 1600 | -400 | 75 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1199 |  | 1600 | -401 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1199 |  | 1600 | -401 | 75 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1198 |  | 1600 | -402 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1172 |  | 1600 | -428 | 73 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1171 |  | 1600 | -429 | 73 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1169 |  | 1600 | -431 | 73 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1165 |  | 1600 | -435 | 73 | []

## 1630Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2740
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1517 | 1600 | 1600 | -83 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1469 | 1600 | 1600 | -131 | 92 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1456 | 1600 | 1600 | -144 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1412 | 1600 | 1600 | -188 | 88 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1387 | 1600 | 1600 | -213 | 87 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1325 | 1600 | 1600 | -275 | 83 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 | 1600 | 1600 | -296 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1196 | 1600 | 1600 | -404 | 75 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1195 | 1600 | 1600 | -405 | 75 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1192 | 1600 | 1600 | -408 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1146 | 1600 | 1600 | -454 | 72 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1135 | 1600 | 1600 | -465 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2740
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1594 |  | 1600 | -6 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1517 |  | 1600 | -83 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1469 |  | 1600 | -131 | 92 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1456 |  | 1600 | -144 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1412 |  | 1600 | -188 | 88 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1387 |  | 1600 | -213 | 87 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1325 |  | 1600 | -275 | 83 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1304 |  | 1600 | -296 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1269 |  | 1600 | -331 | 79 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1260 |  | 1600 | -340 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1196 |  | 1600 | -404 | 75 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1195 |  | 1600 | -405 | 75 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1193 |  | 1600 | -407 | 75 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1192 |  | 1600 | -408 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1147 |  | 1600 | -453 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1146 |  | 1600 | -454 | 72 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1135 |  | 1600 | -465 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2821
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1528 | 1600 | 1600 | -72 | 95 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1505 | 1600 | 1600 | -95 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1503 | 1600 | 1600 | -97 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1454 | 1600 | 1600 | -146 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1447 | 1600 | 1600 | -153 | 90 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 | 1600 | 1600 | -247 | 85 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1350 | 1600 | 1600 | -250 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1313 | 1600 | 1600 | -287 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 | 1600 | 1600 | -293 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1279 | 1600 | 1600 | -321 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1275 | 1600 | 1600 | -325 | 80 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 | 1600 | 1600 | -336 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 | 1600 | 1600 | -336 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 | 1600 | 1600 | -338 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 | 1600 | 1600 | -338 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 | 1600 | 1600 | -338 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 | 1600 | 1600 | -341 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1197 | 1600 | 1600 | -403 | 75 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1155 | 1600 | 1600 | -445 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1149 | 1600 | 1600 | -451 | 72 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1142 | 1600 | 1600 | -458 | 71 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1127 | 1600 | 1600 | -473 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2821
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1528 |  | 1600 | -72 | 95 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1505 |  | 1600 | -95 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1503 |  | 1600 | -97 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1454 |  | 1600 | -146 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1447 |  | 1600 | -153 | 90 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 |  | 1600 | -247 | 85 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1350 |  | 1600 | -250 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1313 |  | 1600 | -287 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1307 |  | 1600 | -293 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 |  | 1600 | -298 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1279 |  | 1600 | -321 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1275 |  | 1600 | -325 | 80 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1269 |  | 1600 | -331 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 |  | 1600 | -336 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 |  | 1600 | -336 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 |  | 1600 | -338 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 |  | 1600 | -338 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 |  | 1600 | -338 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 |  | 1600 | -341 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1253 |  | 1600 | -347 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1253 |  | 1600 | -347 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1197 |  | 1600 | -403 | 75 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1155 |  | 1600 | -445 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1149 |  | 1600 | -451 | 72 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1142 |  | 1600 | -458 | 71 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1127 |  | 1600 | -473 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2820
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1522 | 1600 | 1600 | -78 | 95 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1510 | 1600 | 1600 | -90 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1508 | 1600 | 1600 | -92 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1463 | 1600 | 1600 | -137 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1453 | 1600 | 1600 | -147 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 | 1600 | 1600 | -247 | 85 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1319 | 1600 | 1600 | -281 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 | 1600 | 1600 | -288 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1308 | 1600 | 1600 | -292 | 82 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1282 | 1600 | 1600 | -318 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1280 | 1600 | 1600 | -320 | 80 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1274 | 1600 | 1600 | -326 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 | 1600 | 1600 | -328 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1266 | 1600 | 1600 | -334 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 | 1600 | 1600 | -336 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1263 | 1600 | 1600 | -337 | 79 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 | 1600 | 1600 | -341 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 | 1600 | 1600 | -341 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 | 1600 | 1600 | -393 | 75 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1176 | 1600 | 1600 | -424 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1154 | 1600 | 1600 | -446 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1153 | 1600 | 1600 | -447 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1135 | 1600 | 1600 | -465 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2820
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1594 |  | 1600 | -6 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1522 |  | 1600 | -78 | 95 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1510 |  | 1600 | -90 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1508 |  | 1600 | -92 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1463 |  | 1600 | -137 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1453 |  | 1600 | -147 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 |  | 1600 | -243 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1353 |  | 1600 | -247 | 85 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1319 |  | 1600 | -281 | 82 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 |  | 1600 | -288 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1308 |  | 1600 | -292 | 82 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1282 |  | 1600 | -318 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1280 |  | 1600 | -320 | 80 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1274 |  | 1600 | -326 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 |  | 1600 | -328 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1269 |  | 1600 | -331 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1269 |  | 1600 | -331 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1266 |  | 1600 | -334 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1264 |  | 1600 | -336 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1263 |  | 1600 | -337 | 79 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1260 |  | 1600 | -340 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1260 |  | 1600 | -340 | 79 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 |  | 1600 | -341 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 |  | 1600 | -341 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1207 |  | 1600 | -393 | 75 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1176 |  | 1600 | -424 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1165 |  | 1600 | -435 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1154 |  | 1600 | -446 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1153 |  | 1600 | -447 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1135 |  | 1600 | -465 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2706
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1519 | 1600 | 1600 | -81 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1485 | 1600 | 1600 | -115 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1463 | 1600 | 1600 | -137 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1416 | 1600 | 1600 | -184 | 89 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1408 | 1600 | 1600 | -192 | 88 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1337 | 1600 | 1600 | -263 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1320 | 1600 | 1600 | -280 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1285 | 1600 | 1600 | -315 | 80 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1279 | 1600 | 1600 | -321 | 80 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1275 | 1600 | 1600 | -325 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 | 1600 | 1600 | -338 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1167 | 1600 | 1600 | -433 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1154 | 1600 | 1600 | -446 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1121 | 1600 | 1600 | -479 | 70 | []

## 1930Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2706
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1597 |  | 1600 | -3 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1519 |  | 1600 | -81 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1485 |  | 1600 | -115 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1463 |  | 1600 | -137 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1416 |  | 1600 | -184 | 89 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1408 |  | 1600 | -192 | 88 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1337 |  | 1600 | -263 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1320 |  | 1600 | -280 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1285 |  | 1600 | -315 | 80 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1279 |  | 1600 | -321 | 80 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1275 |  | 1600 | -325 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 |  | 1600 | -338 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 |  | 1600 | -349 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1167 |  | 1600 | -433 | 73 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1158 |  | 1600 | -442 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1154 |  | 1600 | -446 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1121 |  | 1600 | -479 | 70 | []

## 2030Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2794
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1518 | 1600 | 1600 | -82 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1492 | 1600 | 1600 | -108 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1477 | 1600 | 1600 | -123 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1461 | 1600 | 1600 | -139 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1430 | 1600 | 1600 | -170 | 89 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1348 | 1600 | 1600 | -252 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1342 | 1600 | 1600 | -258 | 84 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1299 | 1600 | 1600 | -301 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1268 | 1600 | 1600 | -332 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1263 | 1600 | 1600 | -337 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 | 1600 | 1600 | -341 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1250 | 1600 | 1600 | -350 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1186 | 1600 | 1600 | -414 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1156 | 1600 | 1600 | -444 | 72 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1131 | 1600 | 1600 | -469 | 71 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1123 | 1600 | 1600 | -477 | 70 | []

## 2030Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2794
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1596 |  | 1600 | -4 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1518 |  | 1600 | -82 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1492 |  | 1600 | -108 | 93 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1477 |  | 1600 | -123 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1461 |  | 1600 | -139 | 91 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1430 |  | 1600 | -170 | 89 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1348 |  | 1600 | -252 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1342 |  | 1600 | -258 | 84 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 |  | 1600 | -298 | 81 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1302 |  | 1600 | -298 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1299 |  | 1600 | -301 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1268 |  | 1600 | -332 | 79 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1263 |  | 1600 | -337 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 |  | 1600 | -341 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 78 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 78 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1250 |  | 1600 | -350 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1186 |  | 1600 | -414 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1166 |  | 1600 | -434 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1156 |  | 1600 | -444 | 72 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1140 |  | 1600 | -460 | 71 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1131 |  | 1600 | -469 | 71 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1123 |  | 1600 | -477 | 70 | []

## 2130Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2915
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1531 | 1600 | 1600 | -69 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1521 | 1600 | 1600 | -79 | 95 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1509 | 1600 | 1600 | -91 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1503 | 1600 | 1600 | -97 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1478 | 1600 | 1600 | -122 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1394 | 1600 | 1600 | -206 | 87 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1355 | 1600 | 1600 | -245 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1341 | 1600 | 1600 | -259 | 84 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1328 | 1600 | 1600 | -272 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1328 | 1600 | 1600 | -272 | 83 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1286 | 1600 | 1600 | -314 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1284 | 1600 | 1600 | -316 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1282 | 1600 | 1600 | -318 | 80 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1282 | 1600 | 1600 | -318 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1279 | 1600 | 1600 | -321 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1278 | 1600 | 1600 | -322 | 80 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1278 | 1600 | 1600 | -322 | 80 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1278 | 1600 | 1600 | -322 | 80 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1277 | 1600 | 1600 | -323 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1275 | 1600 | 1600 | -325 | 80 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 | 1600 | 1600 | -328 | 80 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 | 1600 | 1600 | -338 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2915
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1598 |  | 1600 | -2 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1531 |  | 1600 | -69 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1521 |  | 1600 | -79 | 95 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1509 |  | 1600 | -91 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1503 |  | 1600 | -97 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1478 |  | 1600 | -122 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1394 |  | 1600 | -206 | 87 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1355 |  | 1600 | -245 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1341 |  | 1600 | -259 | 84 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1328 |  | 1600 | -272 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1328 |  | 1600 | -272 | 83 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1286 |  | 1600 | -314 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1284 |  | 1600 | -316 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1282 |  | 1600 | -318 | 80 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1282 |  | 1600 | -318 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1279 |  | 1600 | -321 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1278 |  | 1600 | -322 | 80 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1278 |  | 1600 | -322 | 80 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1278 |  | 1600 | -322 | 80 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1277 |  | 1600 | -323 | 80 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1275 |  | 1600 | -325 | 80 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 |  | 1600 | -328 | 80 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1269 |  | 1600 | -331 | 79 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 |  | 1600 | -338 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1253 |  | 1600 | -347 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 |  | 1600 | -349 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1183 |  | 1600 | -417 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1165 |  | 1600 | -435 | 73 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1163 |  | 1600 | -437 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1140 |  | 1600 | -460 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3001
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1556 | 1600 | 1600 | -44 | 97 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1527 | 1600 | 1600 | -73 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1512 | 1600 | 1600 | -88 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1493 | 1600 | 1600 | -107 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1473 | 1600 | 1600 | -127 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1398 | 1600 | 1600 | -202 | 87 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1346 | 1600 | 1600 | -254 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1345 | 1600 | 1600 | -255 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1318 | 1600 | 1600 | -282 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 | 1600 | 1600 | -288 | 82 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1274 | 1600 | 1600 | -326 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 | 1600 | 1600 | -328 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 | 1600 | 1600 | -338 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 | 1600 | 1600 | -341 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1139 | 1600 | 1600 | -461 | 71 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1133 | 1600 | 1600 | -467 | 71 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1126 | 1600 | 1600 | -474 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3001
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1556 |  | 1600 | -44 | 97 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1527 |  | 1600 | -73 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1512 |  | 1600 | -88 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1493 |  | 1600 | -107 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1473 |  | 1600 | -127 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1398 |  | 1600 | -202 | 87 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1346 |  | 1600 | -254 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1345 |  | 1600 | -255 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1318 |  | 1600 | -282 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1312 |  | 1600 | -288 | 82 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1274 |  | 1600 | -326 | 80 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1272 |  | 1600 | -328 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 |  | 1600 | -338 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1260 |  | 1600 | -340 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 |  | 1600 | -341 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG_CO_00007 | N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1199 |  | 1600 | -401 | 75 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1139 |  | 1600 | -461 | 71 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1133 |  | 1600 | -467 | 71 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1126 |  | 1600 | -474 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3037
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1561 | 1600 | 1600 | -39 | 98 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1545 | 1600 | 1600 | -55 | 97 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1503 | 1600 | 1600 | -97 | 94 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1497 | 1600 | 1600 | -103 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1463 | 1600 | 1600 | -137 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1408 | 1600 | 1600 | -192 | 88 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1336 | 1600 | 1600 | -264 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1325 | 1600 | 1600 | -275 | 83 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1319 | 1600 | 1600 | -281 | 82 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1274 | 1600 | 1600 | -326 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1266 | 1600 | 1600 | -334 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 | 1600 | 1600 | -338 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 | 1600 | 1600 | -341 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 | 1600 | 1600 | -341 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1217 | 1600 | 1600 | -383 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1196 | 1600 | 1600 | -404 | 75 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1299 | 1760 | 1760 | -461 | 74 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1136 | 1600 | 1600 | -464 | 71 | []

## 2330Curative
Detailed results
Generated at: | 2024-01-15 08:17
Business day: | 15.01.2024
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3037
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1561 |  | 1600 | -39 | 98 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1545 |  | 1600 | -55 | 97 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1503 |  | 1600 | -97 | 94 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1497 |  | 1600 | -103 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1463 |  | 1600 | -137 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1408 |  | 1600 | -192 | 88 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1357 |  | 1600 | -243 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1336 |  | 1600 | -264 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1325 |  | 1600 | -275 | 83 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1319 |  | 1600 | -281 | 82 | []
BG_CO_00002 | N-1 400kV Sofia Zapad - Chervena Mogila ck. 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1274 |  | 1600 | -326 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1271 |  | 1600 | -329 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1266 |  | 1600 | -334 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1262 |  | 1600 | -338 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
BG_CO_00012 | Â N-1 400kV Varna - Burgas | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1260 |  | 1600 | -340 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 |  | 1600 | -341 | 79 | []
BG_CO_00010 | N-1 400kV Maritsa Iztok â Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1259 |  | 1600 | -341 | 79 | []
BG_CO_00016 | N-1 400kV Kozloduy - Sofia Zapad ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
BG_CO_00013 | N-1 400kV Burgas â Maritsa Iztok 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 78 | []
BG_CO_00011 | N-1 400kV Maritsa Iztok - Plovdiv | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1251 |  | 1600 | -349 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
KS_ME_CO_00001 | N-1 400 kV Pec 3-Ribarevina | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1217 |  | 1600 | -383 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1196 |  | 1600 | -404 | 75 | []
BG_CO_00001 | N-1 400kV Chervena Mogila - Blagoevgrad ck. 1 | [BG-MK] 400kV Chervena Mogila - Stip [DIR] [BG] | VCMOGL11_XCM_ST11_1:line | 1299 |  | 1760 | -461 | 74 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1159 |  | 1600 | -441 | 72 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | 1136 |  | 1600 | -464 | 71 | []