## 0030Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3261
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1579 | 1600 | 1600 | -21 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1443 | 1600 | 1600 | -157 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1443 | 1600 | 1600 | -157 | 90 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1437 | 1601 | 1601 | -164 | 90 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1437 | 1601 | 1601 | -164 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1377 | 1600 | 1600 | -223 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1203 | 1600 | 1600 | -397 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1373 | -1836 | -1836 | -463 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1171 | 1601 | 1601 | -430 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1171 | 1601 | 1601 | -430 | 73 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1325 | -1836 | -1836 | -511 | 72 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1318 | -1836 | -1836 | -518 | 72 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1318 | -1836 | -1836 | -518 | 72 | []

## 0030Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3261
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1579 |  | 1600 | -21 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1443 |  | 1600 | -157 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1443 |  | 1600 | -157 | 90 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1437 |  | 1601 | -164 | 90 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1437 |  | 1601 | -164 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1377 |  | 1600 | -223 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1203 |  | 1600 | -397 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1373 |  | -1836 | -463 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1178 |  | 1600 | -422 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1178 |  | 1600 | -422 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1171 |  | 1601 | -430 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1171 |  | 1601 | -430 | 73 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1325 |  | -1836 | -511 | 72 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1318 |  | -1836 | -518 | 72 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1318 |  | -1836 | -518 | 72 | []

## 0130Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2823
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1577 | 1600 | 1600 | -23 | 99 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1372 | 1600 | 1600 | -228 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1236 | 1601 | 1601 | -365 | 77 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1236 | 1601 | 1601 | -365 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1186 | 1600 | 1600 | -414 | 74 | []

## 0130Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2823
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1597 |  | 1600 | -3 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1577 |  | 1600 | -23 | 99 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1372 |  | 1600 | -228 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1239 |  | 1600 | -361 | 77 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1239 |  | 1600 | -361 | 77 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1236 |  | 1601 | -365 | 77 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1236 |  | 1601 | -365 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1186 |  | 1600 | -414 | 74 | []

## 0230Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3559
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1565 | 1600 | 1600 | -35 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1540 | 1600 | 1600 | -60 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1540 | 1600 | 1600 | -60 | 96 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1537 | 1601 | 1601 | -64 | 96 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1537 | 1601 | 1601 | -64 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1585 | -1836 | -1836 | -251 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1568 | -1836 | -1836 | -268 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1568 | -1836 | -1836 | -268 | 85 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1363 | 1600 | 1600 | -237 | 85 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1544 | -1836 | -1836 | -292 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1297 | 1600 | 1600 | -303 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1297 | 1600 | 1600 | -303 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1293 | 1601 | 1601 | -308 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1293 | 1601 | 1601 | -308 | 81 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1463 | -1836 | -1836 | -373 | 80 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1433 | -1836 | -1836 | -403 | 78 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1432 | -1836 | -1836 | -404 | 78 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1427 | -1836 | -1836 | -409 | 78 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1419 | -1836 | -1836 | -417 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1232 | 1600 | 1600 | -368 | 77 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1398 | -1836 | -1836 | -438 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1171 | 1600 | 1600 | -429 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -705 | -999 | -999 | -294 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -877 | -1248 | -1248 | -371 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -875 | -1248 | -1248 | -373 | 70 | []

## 0230Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3559
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1565 |  | 1600 | -35 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1540 |  | 1600 | -60 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1540 |  | 1600 | -60 | 96 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1537 |  | 1601 | -64 | 96 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1537 |  | 1601 | -64 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1585 |  | -1836 | -251 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1568 |  | -1836 | -268 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1568 |  | -1836 | -268 | 85 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1363 |  | 1600 | -237 | 85 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1544 |  | -1836 | -292 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1297 |  | 1600 | -303 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1297 |  | 1600 | -303 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1293 |  | 1601 | -308 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1293 |  | 1601 | -308 | 81 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1463 |  | -1836 | -373 | 80 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1433 |  | -1836 | -403 | 78 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1432 |  | -1836 | -404 | 78 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1427 |  | -1836 | -409 | 78 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1419 |  | -1836 | -417 | 77 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1232 |  | 1600 | -368 | 77 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1398 |  | -1836 | -438 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1171 |  | 1600 | -429 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -705 |  | -999 | -294 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -877 |  | -1248 | -371 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -875 |  | -1248 | -373 | 70 | []

## 0330Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3657
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1561 | 1600 | 1600 | -39 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1547 | 1600 | 1600 | -53 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1547 | 1600 | 1600 | -53 | 97 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1544 | 1601 | 1601 | -57 | 96 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1544 | 1601 | 1601 | -57 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1702 | 1836 | 1836 | -134 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 | 1836 | 1836 | -138 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 | 1836 | 1836 | -138 | 92 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1664 | 1836 | 1836 | -172 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1590 | 1836 | 1836 | -246 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1367 | 1600 | 1600 | -233 | 85 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 | 1836 | 1836 | -276 | 85 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1559 | 1836 | 1836 | -277 | 85 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1556 | 1836 | 1836 | -280 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1547 | 1836 | 1836 | -289 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1336 | 1600 | 1600 | -264 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1336 | 1600 | 1600 | -264 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1528 | 1836 | 1836 | -308 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1333 | 1601 | 1601 | -268 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1333 | 1601 | 1601 | -268 | 83 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1245 | 1600 | 1600 | -355 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1184 | 1600 | 1600 | -416 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -724 | -999 | -999 | -275 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -905 | -1248 | -1248 | -344 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -902 | -1248 | -1248 | -347 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -900 | -1248 | -1248 | -348 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -892 | -1248 | -1248 | -356 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -892 | -1248 | -1248 | -357 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -886 | -1248 | -1248 | -362 | 71 | []

## 0330Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3657
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1561 |  | 1600 | -39 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1547 |  | 1600 | -53 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1547 |  | 1600 | -53 | 97 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1544 |  | 1601 | -57 | 96 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1544 |  | 1601 | -57 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1702 |  | 1836 | -134 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 |  | 1836 | -138 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 |  | 1836 | -138 | 92 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1664 |  | 1836 | -172 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1590 |  | 1836 | -246 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1367 |  | 1600 | -233 | 85 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 |  | 1836 | -276 | 85 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1559 |  | 1836 | -277 | 85 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1556 |  | 1836 | -280 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1547 |  | 1836 | -289 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1336 |  | 1600 | -264 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1336 |  | 1600 | -264 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1528 |  | 1836 | -308 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1333 |  | 1601 | -268 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1333 |  | 1601 | -268 | 83 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1245 |  | 1600 | -355 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1184 |  | 1600 | -416 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -724 |  | -999 | -275 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -905 |  | -1248 | -344 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -902 |  | -1248 | -347 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -900 |  | -1248 | -348 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -892 |  | -1248 | -356 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -892 |  | -1248 | -357 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -886 |  | -1248 | -362 | 71 | []

## 0430Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3723
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1559 | 1600 | 1600 | -41 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1682 | 1836 | 1836 | -154 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1682 | 1836 | 1836 | -154 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 | 1836 | 1836 | -162 | 91 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 | 1836 | 1836 | -202 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1368 | 1600 | 1600 | -232 | 85 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 | 1836 | 1836 | -270 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1354 | 1601 | 1601 | -247 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1354 | 1601 | 1601 | -247 | 85 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 | 1836 | 1836 | -301 | 84 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1533 | 1836 | 1836 | -303 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1531 | 1836 | 1836 | -305 | 83 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 | 1836 | 1836 | -309 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1502 | 1836 | 1836 | -334 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1248 | 1600 | 1600 | -352 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1189 | 1600 | 1600 | -411 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -916 | -1248 | -1248 | -333 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -913 | -1248 | -1248 | -335 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -911 | -1248 | -1248 | -337 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -904 | -1248 | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -346 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -897 | -1248 | -1248 | -351 | 72 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-RO] Stupina - Varna [DIR] [RO] | RSTUP41 _XVA_ST11_1:line | 1434 | 2000 | 2000 | -566 | 72 | []
RO-BG_CO_00004 | N-1 Stupina-Varna | [RO-RO] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1405 | -2000 | -2000 | -595 | 70 | []

## 0430Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3723
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1591 |  | 1600 | -9 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1591 |  | 1600 | -9 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1559 |  | 1600 | -41 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1682 |  | 1836 | -154 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1682 |  | 1836 | -154 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 |  | 1836 | -162 | 91 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 |  | 1836 | -202 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1368 |  | 1600 | -232 | 85 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1836 | -270 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1357 |  | 1600 | -243 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1357 |  | 1600 | -243 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1354 |  | 1601 | -247 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1354 |  | 1601 | -247 | 85 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 |  | 1836 | -301 | 84 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1533 |  | 1836 | -303 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1531 |  | 1836 | -305 | 83 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 |  | 1836 | -309 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1502 |  | 1836 | -334 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1248 |  | 1600 | -352 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1189 |  | 1600 | -411 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -916 |  | -1248 | -333 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -913 |  | -1248 | -335 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -911 |  | -1248 | -337 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -904 |  | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -346 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -897 |  | -1248 | -351 | 72 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-RO] Stupina - Varna [DIR] [RO] | RSTUP41 _XVA_ST11_1:line | 1434 |  | 2000 | -566 | 72 | []
RO-BG_CO_00004 | N-1 Stupina-Varna | [RO-RO] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1405 |  | -2000 | -595 | 70 | []

## 0530Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3630
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1572 | 1600 | 1600 | -28 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1749 | 1836 | 1836 | -87 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 | 1836 | 1836 | -93 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 | 1836 | 1836 | -93 | 95 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1707 | 1836 | 1836 | -129 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1464 | 1600 | 1600 | -136 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1464 | 1600 | 1600 | -136 | 91 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1461 | 1601 | 1601 | -140 | 91 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1461 | 1601 | 1601 | -140 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1636 | 1836 | 1836 | -200 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1607 | 1836 | 1836 | -229 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 | 1836 | 1836 | -230 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1604 | 1836 | 1836 | -232 | 87 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1599 | 1836 | 1836 | -237 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1571 | 1836 | 1836 | -265 | 86 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1357 | 1600 | 1600 | -243 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1301 | 1600 | 1600 | -299 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1301 | 1600 | 1600 | -299 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1298 | 1601 | 1601 | -303 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1298 | 1601 | 1601 | -303 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1221 | 1600 | 1600 | -379 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -909 | -1248 | -1248 | -339 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -906 | -1248 | -1248 | -342 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1161 | 1600 | 1600 | -439 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -905 | -1248 | -1248 | -344 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -896 | -1248 | -1248 | -352 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -896 | -1248 | -1248 | -352 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -890 | -1248 | -1248 | -358 | 71 | []

## 0530Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3630
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1572 |  | 1600 | -28 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1749 |  | 1836 | -87 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 |  | 1836 | -93 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 |  | 1836 | -93 | 95 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1707 |  | 1836 | -129 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1464 |  | 1600 | -136 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1464 |  | 1600 | -136 | 91 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1461 |  | 1601 | -140 | 91 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1461 |  | 1601 | -140 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1636 |  | 1836 | -200 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1607 |  | 1836 | -229 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 |  | 1836 | -230 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1604 |  | 1836 | -232 | 87 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1599 |  | 1836 | -237 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1571 |  | 1836 | -265 | 86 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1357 |  | 1600 | -243 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1301 |  | 1600 | -299 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1301 |  | 1600 | -299 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1298 |  | 1601 | -303 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1298 |  | 1601 | -303 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1221 |  | 1600 | -379 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -909 |  | -1248 | -339 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -906 |  | -1248 | -342 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1161 |  | 1600 | -439 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -905 |  | -1248 | -344 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -896 |  | -1248 | -352 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -896 |  | -1248 | -352 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -890 |  | -1248 | -358 | 71 | []

## 0630Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3264
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1524 | 1600 | 1600 | -76 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1422 | 1600 | 1600 | -178 | 89 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1380 | 1600 | 1600 | -220 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1380 | 1600 | 1600 | -220 | 86 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1376 | 1601 | 1601 | -225 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1376 | 1601 | 1601 | -225 | 86 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 | 1836 | 1836 | -309 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1496 | 1836 | 1836 | -340 | 81 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1496 | 1836 | 1836 | -340 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1303 | 1600 | 1600 | -297 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1478 | 1836 | 1836 | -358 | 80 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1410 | 1836 | 1836 | -426 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1226 | 1600 | 1600 | -374 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1377 | 1836 | 1836 | -459 | 75 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1372 | 1836 | 1836 | -464 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -746 | -999 | -999 | -253 | 75 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1369 | 1836 | 1836 | -467 | 75 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1360 | 1836 | 1836 | -476 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1184 | 1600 | 1600 | -416 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1184 | 1600 | 1600 | -416 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1181 | 1601 | 1601 | -420 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1181 | 1601 | 1601 | -420 | 74 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1350 | 1836 | 1836 | -486 | 74 | []

## 0630Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3264
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1524 |  | 1600 | -76 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1422 |  | 1600 | -178 | 89 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1380 |  | 1600 | -220 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1380 |  | 1600 | -220 | 86 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1376 |  | 1601 | -225 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1376 |  | 1601 | -225 | 86 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 |  | 1836 | -309 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1496 |  | 1836 | -340 | 81 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1496 |  | 1836 | -340 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1303 |  | 1600 | -297 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1478 |  | 1836 | -358 | 80 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1410 |  | 1836 | -426 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1226 |  | 1600 | -374 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1377 |  | 1836 | -459 | 75 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1372 |  | 1836 | -464 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -746 |  | -999 | -253 | 75 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1369 |  | 1836 | -467 | 75 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1360 |  | 1836 | -476 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1184 |  | 1600 | -416 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1184 |  | 1600 | -416 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1181 |  | 1601 | -420 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1181 |  | 1601 | -420 | 74 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1350 |  | 1836 | -486 | 74 | []

## 0730Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3010
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1516 | 1600 | 1600 | -84 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1429 | 1600 | 1600 | -171 | 89 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1323 | 1600 | 1600 | -277 | 83 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1323 | 1600 | 1600 | -277 | 83 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1317 | 1601 | 1601 | -284 | 82 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1317 | 1601 | 1601 | -284 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1310 | 1600 | 1600 | -290 | 82 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1241 | 1600 | 1600 | -359 | 78 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1357 | 1836 | 1836 | -479 | 74 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1323 | 1836 | 1836 | -513 | 72 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1323 | 1836 | 1836 | -513 | 72 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1307 | 1836 | 1836 | -529 | 71 | []

## 0730Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3010
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1600 |  | 1600 | 0 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1516 |  | 1600 | -84 | 95 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1429 |  | 1600 | -171 | 89 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1323 |  | 1600 | -277 | 83 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1323 |  | 1600 | -277 | 83 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1317 |  | 1601 | -284 | 82 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1317 |  | 1601 | -284 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1310 |  | 1600 | -290 | 82 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1241 |  | 1600 | -359 | 78 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1357 |  | 1836 | -479 | 74 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1323 |  | 1836 | -513 | 72 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1323 |  | 1836 | -513 | 72 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1307 |  | 1836 | -529 | 71 | []

## 0830Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3353
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1519 | 1600 | 1600 | -81 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1491 | 1600 | 1600 | -109 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1491 | 1600 | 1600 | -109 | 93 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1486 | 1601 | 1601 | -115 | 93 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1486 | 1601 | 1601 | -115 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1427 | 1600 | 1600 | -173 | 89 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1312 | 1600 | 1600 | -288 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1491 | 1836 | 1836 | -345 | 81 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1491 | 1836 | 1836 | -345 | 81 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1486 | 1836 | 1836 | -350 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1260 | 1601 | 1601 | -341 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1260 | 1601 | 1601 | -341 | 79 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1440 | 1836 | 1836 | -396 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1382 | 1836 | 1836 | -454 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1373 | 1836 | 1836 | -463 | 75 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1362 | 1836 | 1836 | -474 | 74 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1343 | 1836 | 1836 | -493 | 73 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1328 | 1836 | 1836 | -508 | 72 | []

## 0830Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3353
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1519 |  | 1600 | -81 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1491 |  | 1600 | -109 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1491 |  | 1600 | -109 | 93 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1486 |  | 1601 | -115 | 93 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1486 |  | 1601 | -115 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1427 |  | 1600 | -173 | 89 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1312 |  | 1600 | -288 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1491 |  | 1836 | -345 | 81 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1491 |  | 1836 | -345 | 81 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1486 |  | 1836 | -350 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1265 |  | 1600 | -335 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1265 |  | 1600 | -335 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1260 |  | 1601 | -341 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1260 |  | 1601 | -341 | 79 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1440 |  | 1836 | -396 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1239 |  | 1600 | -361 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1382 |  | 1836 | -454 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1373 |  | 1836 | -463 | 75 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1362 |  | 1836 | -474 | 74 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1343 |  | 1836 | -493 | 73 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1328 |  | 1836 | -508 | 72 | []

## 0930Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3541
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1564 | 1600 | 1600 | -36 | 98 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1474 | 1600 | 1600 | -126 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1405 | 1600 | 1600 | -195 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 | 1836 | 1836 | -276 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 | 1836 | 1836 | -276 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1342 | 1600 | 1600 | -258 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1342 | 1600 | 1600 | -258 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1538 | 1836 | 1836 | -298 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1337 | 1601 | 1601 | -264 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1337 | 1601 | 1601 | -264 | 84 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1493 | 1836 | 1836 | -343 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1300 | 1600 | 1600 | -300 | 81 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 | 1836 | 1836 | -371 | 80 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1433 | 1836 | 1836 | -403 | 78 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1428 | 1836 | 1836 | -408 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1236 | 1600 | 1600 | -364 | 77 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1401 | 1836 | 1836 | -435 | 76 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1388 | 1836 | 1836 | -448 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -902 | -1248 | -1248 | -347 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -900 | -1248 | -1248 | -349 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -897 | -1248 | -1248 | -351 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -891 | -1248 | -1248 | -358 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -889 | -1248 | -1248 | -359 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -885 | -1248 | -1248 | -364 | 71 | []

## 0930Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3541
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 |  | 1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 |  | 1600 | -5 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1564 |  | 1600 | -36 | 98 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1474 |  | 1600 | -126 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1405 |  | 1600 | -195 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 |  | 1836 | -276 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 |  | 1836 | -276 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1342 |  | 1600 | -258 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1342 |  | 1600 | -258 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1538 |  | 1836 | -298 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1337 |  | 1601 | -264 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1337 |  | 1601 | -264 | 84 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1493 |  | 1836 | -343 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1300 |  | 1600 | -300 | 81 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 |  | 1836 | -371 | 80 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1433 |  | 1836 | -403 | 78 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1428 |  | 1836 | -408 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1236 |  | 1600 | -364 | 77 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1401 |  | 1836 | -435 | 76 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1388 |  | 1836 | -448 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -902 |  | -1248 | -347 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -900 |  | -1248 | -349 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -897 |  | -1248 | -351 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -891 |  | -1248 | -358 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -889 |  | -1248 | -359 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -885 |  | -1248 | -364 | 71 | []

## 1030Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3408
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1511 | 1600 | 1600 | -89 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1411 | 1600 | 1600 | -189 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1367 | 1600 | 1600 | -233 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1327 | 1600 | 1600 | -273 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1327 | 1600 | 1600 | -273 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1322 | 1601 | 1601 | -279 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1322 | 1601 | 1601 | -279 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1509 | 1836 | 1836 | -327 | 82 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1509 | 1836 | 1836 | -327 | 82 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1487 | 1836 | 1836 | -349 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1270 | 1600 | 1600 | -330 | 79 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1443 | 1836 | 1836 | -393 | 79 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1427 | 1836 | 1836 | -409 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1218 | 1600 | 1600 | -382 | 76 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1384 | 1836 | 1836 | -452 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1384 | 1836 | 1836 | -452 | 75 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1351 | 1836 | 1836 | -485 | 74 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1349 | 1836 | 1836 | -487 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -909 | -1248 | -1248 | -340 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -907 | -1248 | -1248 | -342 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -904 | -1248 | -1248 | -344 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -898 | -1248 | -1248 | -350 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -897 | -1248 | -1248 | -352 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -892 | -1248 | -1248 | -356 | 71 | []

## 1030Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3408
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 |  | 1600 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 |  | 1600 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1511 |  | 1600 | -89 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1411 |  | 1600 | -189 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1367 |  | 1600 | -233 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1327 |  | 1600 | -273 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1327 |  | 1600 | -273 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1322 |  | 1601 | -279 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1322 |  | 1601 | -279 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1509 |  | 1836 | -327 | 82 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1509 |  | 1836 | -327 | 82 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1487 |  | 1836 | -349 | 81 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1270 |  | 1600 | -330 | 79 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1443 |  | 1836 | -393 | 79 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1836 | -409 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1218 |  | 1600 | -382 | 76 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1384 |  | 1836 | -452 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1384 |  | 1836 | -452 | 75 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1351 |  | 1836 | -485 | 74 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1349 |  | 1836 | -487 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -909 |  | -1248 | -340 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -907 |  | -1248 | -342 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -904 |  | -1248 | -344 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -898 |  | -1248 | -350 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -897 |  | -1248 | -352 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -892 |  | -1248 | -356 | 71 | []

## 1130Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3631
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1821 | 1836 | 1836 | -15 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1821 | 1836 | 1836 | -15 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1803 | 1836 | 1836 | -33 | 98 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1798 | 1836 | 1836 | -38 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1756 | 1836 | 1836 | -80 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1503 | 1600 | 1600 | -97 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1710 | 1836 | 1836 | -126 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1701 | 1836 | 1836 | -135 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 | 1836 | 1836 | -149 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 | 1836 | 1836 | -173 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1435 | 1600 | 1600 | -165 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1410 | 1600 | 1600 | -190 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1410 | 1600 | 1600 | -190 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1405 | 1601 | 1601 | -196 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1405 | 1601 | 1601 | -196 | 88 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1333 | 1600 | 1600 | -267 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -799 | -999 | -999 | -200 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1263 | 1600 | 1600 | -337 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -912 | -1248 | -1248 | -336 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -909 | -1248 | -1248 | -340 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -908 | -1248 | -1248 | -341 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -898 | -1248 | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -898 | -1248 | -1248 | -350 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -892 | -1248 | -1248 | -356 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1345 | -1920 | -1920 | -575 | 70 | []

## 1130Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3631
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1595 |  | 1600 | -5 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1594 |  | 1600 | -6 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 |  | 1600 | -6 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 |  | 1601 | -12 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1821 |  | 1836 | -15 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1821 |  | 1836 | -15 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1803 |  | 1836 | -33 | 98 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1798 |  | 1836 | -38 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1756 |  | 1836 | -80 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1503 |  | 1600 | -97 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1710 |  | 1836 | -126 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1701 |  | 1836 | -135 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 |  | 1836 | -149 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 |  | 1836 | -173 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1435 |  | 1600 | -165 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1410 |  | 1600 | -190 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1410 |  | 1600 | -190 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1405 |  | 1601 | -196 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1405 |  | 1601 | -196 | 88 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1333 |  | 1600 | -267 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -799 |  | -999 | -200 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1263 |  | 1600 | -337 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -912 |  | -1248 | -336 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -909 |  | -1248 | -340 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -908 |  | -1248 | -341 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -898 |  | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -898 |  | -1248 | -350 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -892 |  | -1248 | -356 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1345 |  | -1920 | -575 | 70 | []

## 1230Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3394
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 | 1836 | 1836 | -11 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1822 | 1836 | 1836 | -14 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1816 | 1836 | 1836 | -20 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1816 | 1836 | 1836 | -20 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1547 | 1600 | 1600 | -53 | 97 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1771 | 1836 | 1836 | -65 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 | 1836 | 1836 | -111 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1716 | 1836 | 1836 | -120 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1708 | 1836 | 1836 | -128 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 | 1836 | 1836 | -162 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1447 | 1600 | 1600 | -153 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1435 | 1600 | 1600 | -165 | 90 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1435 | 1600 | 1600 | -165 | 90 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1430 | 1601 | 1601 | -171 | 89 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1430 | 1601 | 1601 | -171 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1399 | 1600 | 1600 | -201 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -839 | -999 | -999 | -160 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1318 | 1600 | 1600 | -282 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1318 | 1600 | 1600 | -282 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1313 | 1601 | 1601 | -288 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1313 | 1601 | 1601 | -288 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1309 | 1600 | 1600 | -291 | 82 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1241 | 1600 | 1600 | -359 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -904 | -1248 | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -900 | -1248 | -1248 | -348 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -899 | -1248 | -1248 | -349 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -890 | -1248 | -1248 | -359 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -890 | -1248 | -1248 | -359 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -883 | -1248 | -1248 | -365 | 71 | []

## 1230Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3394
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 |  | 1836 | -11 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1822 |  | 1836 | -14 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1816 |  | 1836 | -20 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1816 |  | 1836 | -20 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1547 |  | 1600 | -53 | 97 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1771 |  | 1836 | -65 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 |  | 1836 | -111 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1716 |  | 1836 | -120 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1708 |  | 1836 | -128 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 |  | 1836 | -162 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1447 |  | 1600 | -153 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1435 |  | 1600 | -165 | 90 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1435 |  | 1600 | -165 | 90 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1430 |  | 1601 | -171 | 89 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1430 |  | 1601 | -171 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1399 |  | 1600 | -201 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -839 |  | -999 | -160 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1318 |  | 1600 | -282 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1318 |  | 1600 | -282 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1313 |  | 1601 | -288 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1313 |  | 1601 | -288 | 82 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1309 |  | 1600 | -291 | 82 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1241 |  | 1600 | -359 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -904 |  | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -900 |  | -1248 | -348 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -899 |  | -1248 | -349 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -890 |  | -1248 | -359 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -890 |  | -1248 | -359 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -883 |  | -1248 | -365 | 71 | []

## 1330Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3466
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1826 | -1836 | -1836 | -10 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1815 | -1836 | -1836 | -21 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1808 | -1836 | -1836 | -28 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1808 | -1836 | -1836 | -28 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1761 | -1836 | -1836 | -75 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1501 | 1600 | 1600 | -99 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1717 | -1836 | -1836 | -119 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1707 | -1836 | -1836 | -129 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1706 | -1836 | -1836 | -130 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1482 | 1600 | 1600 | -118 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1482 | 1600 | 1600 | -118 | 93 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1477 | 1601 | 1601 | -124 | 92 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1477 | 1601 | 1601 | -124 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1663 | -1836 | -1836 | -173 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1444 | 1600 | 1600 | -156 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -873 | -999 | -999 | -127 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1353 | 1600 | 1600 | -247 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1341 | 1600 | 1600 | -259 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1341 | 1600 | 1600 | -259 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1336 | 1601 | 1601 | -265 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1336 | 1601 | 1601 | -265 | 83 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1277 | 1600 | 1600 | -323 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -902 | -1248 | -1248 | -346 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -899 | -1248 | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -898 | -1248 | -1248 | -350 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -889 | -1248 | -1248 | -360 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -889 | -1248 | -1248 | -360 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -882 | -1248 | -1248 | -366 | 71 | []

## 1330Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3466
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1826 |  | -1836 | -10 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1815 |  | -1836 | -21 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1808 |  | -1836 | -28 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1808 |  | -1836 | -28 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1761 |  | -1836 | -75 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1501 |  | 1600 | -99 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1717 |  | -1836 | -119 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1707 |  | -1836 | -129 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1706 |  | -1836 | -130 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1482 |  | 1600 | -118 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1482 |  | 1600 | -118 | 93 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1477 |  | 1601 | -124 | 92 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1477 |  | 1601 | -124 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1663 |  | -1836 | -173 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1444 |  | 1600 | -156 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -873 |  | -999 | -127 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1353 |  | 1600 | -247 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1341 |  | 1600 | -259 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1341 |  | 1600 | -259 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1336 |  | 1601 | -265 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1336 |  | 1601 | -265 | 83 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1277 |  | 1600 | -323 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -902 |  | -1248 | -346 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -899 |  | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -898 |  | -1248 | -350 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -889 |  | -1248 | -360 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -889 |  | -1248 | -360 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -882 |  | -1248 | -366 | 71 | []

## 1430Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3280
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1503 | 1600 | 1600 | -97 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1485 | 1600 | 1600 | -115 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1485 | 1600 | 1600 | -115 | 93 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1480 | 1601 | 1601 | -121 | 92 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1480 | 1601 | 1601 | -121 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1439 | 1600 | 1600 | -161 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1554 | -1836 | -1836 | -282 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1545 | -1836 | -1836 | -291 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1545 | -1836 | -1836 | -291 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1341 | 1600 | 1600 | -259 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1524 | -1836 | -1836 | -312 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1502 | -1836 | -1836 | -334 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -793 | -999 | -999 | -206 | 79 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1269 | 1600 | 1600 | -331 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1265 | 1601 | 1601 | -336 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1265 | 1601 | 1601 | -336 | 79 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1449 | -1836 | -1836 | -387 | 79 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1436 | -1836 | -1836 | -400 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1431 | -1836 | -1836 | -405 | 78 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1399 | -1836 | -1836 | -437 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -881 | -1248 | -1248 | -367 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -879 | -1248 | -1248 | -370 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -877 | -1248 | -1248 | -372 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3280
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1503 |  | 1600 | -97 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1485 |  | 1600 | -115 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1485 |  | 1600 | -115 | 93 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1480 |  | 1601 | -121 | 92 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1480 |  | 1601 | -121 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1439 |  | 1600 | -161 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1554 |  | -1836 | -282 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1545 |  | -1836 | -291 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1545 |  | -1836 | -291 | 84 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1341 |  | 1600 | -259 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1524 |  | -1836 | -312 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1502 |  | -1836 | -334 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1271 |  | 1600 | -329 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1271 |  | 1600 | -329 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -793 |  | -999 | -206 | 79 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1269 |  | 1600 | -331 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1265 |  | 1601 | -336 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1265 |  | 1601 | -336 | 79 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1449 |  | -1836 | -387 | 79 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1436 |  | -1836 | -400 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1431 |  | -1836 | -405 | 78 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1399 |  | -1836 | -437 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -881 |  | -1248 | -367 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -879 |  | -1248 | -370 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -877 |  | -1248 | -372 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2921
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1512 | 1600 | 1600 | -88 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1428 | 1600 | 1600 | -172 | 89 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1393 | 1600 | 1600 | -207 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1393 | 1600 | 1600 | -207 | 87 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1388 | 1601 | 1601 | -213 | 87 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1388 | 1601 | 1601 | -213 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1312 | 1600 | 1600 | -288 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -800 | -999 | -999 | -199 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1244 | 1600 | 1600 | -356 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1122 | 1600 | 1600 | -478 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1122 | 1600 | 1600 | -478 | 70 | []

## 1530Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2921
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1512 |  | 1600 | -88 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1428 |  | 1600 | -172 | 89 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1393 |  | 1600 | -207 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1393 |  | 1600 | -207 | 87 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1388 |  | 1601 | -213 | 87 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1388 |  | 1601 | -213 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1312 |  | 1600 | -288 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -800 |  | -999 | -199 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1244 |  | 1600 | -356 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1122 |  | 1600 | -478 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1122 |  | 1600 | -478 | 70 | []

## 1630Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1760
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1509 | 1600 | 1600 | -91 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1422 | 1600 | 1600 | -178 | 89 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1285 | 1600 | 1600 | -315 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1233 | 1600 | 1600 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1203 | 1601 | 1601 | -398 | 75 | []

## 1630Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1760
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1597 |  | 1600 | -3 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1509 |  | 1600 | -91 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1422 |  | 1600 | -178 | 89 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1285 |  | 1600 | -315 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1233 |  | 1600 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1209 |  | 1600 | -391 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1203 |  | 1601 | -398 | 75 | []

## 1730Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2811
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1492 | 1600 | 1600 | -108 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1448 | 1600 | 1600 | -152 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -888 | -999 | -999 | -111 | 89 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1355 | 1600 | 1600 | -245 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1297 | 1601 | 1601 | -304 | 81 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1297 | 1601 | 1601 | -304 | 81 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1287 | 1600 | 1600 | -313 | 80 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1383 | -1836 | -1836 | -453 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1316 | -1836 | -1836 | -520 | 72 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1292 | -1836 | -1836 | -544 | 70 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1292 | -1836 | -1836 | -544 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2811
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1492 |  | 1600 | -108 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1448 |  | 1600 | -152 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -888 |  | -999 | -111 | 89 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1355 |  | 1600 | -245 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1302 |  | 1600 | -298 | 81 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1302 |  | 1600 | -298 | 81 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1297 |  | 1601 | -304 | 81 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1297 |  | 1601 | -304 | 81 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1287 |  | 1600 | -313 | 80 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1383 |  | -1836 | -453 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1316 |  | -1836 | -520 | 72 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1292 |  | -1836 | -544 | 70 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1292 |  | -1836 | -544 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2064
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1500 | 1600 | 1600 | -100 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1432 | 1600 | 1600 | -168 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1417 | 1600 | 1600 | -183 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1412 | 1601 | 1601 | -189 | 88 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1310 | 1600 | 1600 | -290 | 82 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1256 | 1600 | 1600 | -344 | 78 | []

## 1830Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2064
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1500 |  | 1600 | -100 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1432 |  | 1600 | -168 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1417 |  | 1600 | -183 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1412 |  | 1601 | -189 | 88 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1310 |  | 1600 | -290 | 82 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1256 |  | 1600 | -344 | 78 | []

## 1930Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2736
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1493 | 1600 | 1600 | -107 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1446 | 1600 | 1600 | -154 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1403 | 1600 | 1600 | -197 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1403 | 1600 | 1600 | -197 | 88 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1398 | 1601 | 1601 | -203 | 87 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1398 | 1601 | 1601 | -203 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1347 | 1600 | 1600 | -253 | 84 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1284 | 1600 | 1600 | -316 | 80 | []

## 1930Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2736
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1598 |  | 1600 | -2 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1493 |  | 1600 | -107 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1446 |  | 1600 | -154 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1403 |  | 1600 | -197 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1403 |  | 1600 | -197 | 88 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1398 |  | 1601 | -203 | 87 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1398 |  | 1601 | -203 | 87 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1347 |  | 1600 | -253 | 84 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1284 |  | 1600 | -316 | 80 | []

## 2030Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2639
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 | 1600 | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1488 | 1600 | 1600 | -112 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1445 | 1600 | 1600 | -155 | 90 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1379 | 1600 | 1600 | -221 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1379 | 1600 | 1600 | -221 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1374 | 1601 | 1601 | -227 | 86 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1374 | 1601 | 1601 | -227 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1345 | 1600 | 1600 | -255 | 84 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1285 | 1600 | 1600 | -315 | 80 | []

## 2030Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2639
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1599 |  | 1600 | -1 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1488 |  | 1600 | -112 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1445 |  | 1600 | -155 | 90 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1379 |  | 1600 | -221 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1379 |  | 1600 | -221 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1374 |  | 1601 | -227 | 86 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1374 |  | 1601 | -227 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1345 |  | 1600 | -255 | 84 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1285 |  | 1600 | -315 | 80 | []

## 2130Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3181
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 | 1601 | 1601 | -8 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 | 1601 | 1601 | -8 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1565 | 1600 | 1600 | -35 | 98 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1477 | 1600 | 1600 | -123 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1402 | 1600 | 1600 | -198 | 88 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1292 | 1600 | 1600 | -308 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1225 | 1600 | 1600 | -375 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1222 | 1601 | 1601 | -379 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1222 | 1601 | 1601 | -379 | 76 | []

## 2130Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3181
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 |  | 1600 | -2 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 |  | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 |  | 1601 | -8 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 |  | 1601 | -8 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1565 |  | 1600 | -35 | 98 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1477 |  | 1600 | -123 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1402 |  | 1600 | -198 | 88 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1292 |  | 1600 | -308 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1227 |  | 1600 | -373 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1227 |  | 1600 | -373 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [OPP] [RO] | RGIAL11 _RLACS41 _1:line | 1225 |  | 1600 | -375 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1222 |  | 1601 | -379 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1222 |  | 1601 | -379 | 76 | []

## 2230Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3235
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1519 | 1600 | 1600 | -81 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1420 | 1600 | 1600 | -180 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1372 | 1600 | 1600 | -228 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1282 | 1600 | 1600 | -318 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1248 | 1601 | 1601 | -353 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1248 | 1601 | 1601 | -353 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1217 | 1600 | 1600 | -383 | 76 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1343 | -1836 | -1836 | -493 | 73 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1298 | -1836 | -1836 | -538 | 71 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1298 | -1836 | -1836 | -538 | 71 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1296 | -1836 | -1836 | -540 | 71 | []

## 2230Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3235
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 |  | 1600 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 |  | 1600 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1519 |  | 1600 | -81 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [OPP] [RO] | RTULC41 _RIS1A41 _1:line | 1420 |  | 1600 | -180 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1372 |  | 1600 | -228 | 86 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1282 |  | 1600 | -318 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1253 |  | 1600 | -347 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1253 |  | 1600 | -347 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1248 |  | 1601 | -353 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1248 |  | 1601 | -353 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1217 |  | 1600 | -383 | 76 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1343 |  | -1836 | -493 | 73 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1298 |  | -1836 | -538 | 71 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1298 |  | -1836 | -538 | 71 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1296 |  | -1836 | -540 | 71 | []

## 2330Preventive
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3341
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1597 | 1601 | 1601 | -4 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1597 | 1601 | 1601 | -4 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1555 | 1600 | 1600 | -45 | 97 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1479 | 1600 | 1600 | -121 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1385 | 1600 | 1600 | -215 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1282 | 1600 | 1600 | -318 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1282 | 1600 | 1600 | -318 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1279 | 1601 | 1601 | -322 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1279 | 1601 | 1601 | -322 | 80 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1272 | 1600 | 1600 | -328 | 79 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1442 | -1836 | -1836 | -394 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1397 | -1836 | -1836 | -439 | 76 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1395 | -1836 | -1836 | -441 | 76 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1395 | -1836 | -1836 | -441 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1198 | 1600 | 1600 | -402 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -743 | -999 | -999 | -256 | 74 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1294 | -1836 | -1836 | -542 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2024-01-16 21:14
Business day: | 18.01.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3341
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | helpful
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 |  | 1600 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 |  | 1600 | 0 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1597 |  | 1601 | -4 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1597 |  | 1601 | -4 | 100 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1555 |  | 1600 | -45 | 97 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Isaccea - Tulcea Vest [DIR] [RO] | RTULC41 _RIS1A41 _1:line | 1479 |  | 1600 | -121 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1385 |  | 1600 | -215 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1282 |  | 1600 | -318 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1282 |  | 1600 | -318 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1279 |  | 1601 | -322 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1279 |  | 1601 | -322 | 80 | []
RO_CO_00016 | N-1 Tariverde - Constanta Nord | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1272 |  | 1600 | -328 | 79 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1442 |  | -1836 | -394 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1397 |  | -1836 | -439 | 76 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1395 |  | -1836 | -441 | 76 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1395 |  | -1836 | -441 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Lacu Sarat - Gura Ialomitei [DIR] [RO] | RGIAL11 _RLACS41 _1:line | 1198 |  | 1600 | -402 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -743 |  | -999 | -256 | 74 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1294 |  | -1836 | -542 | 70 | []