## 0030Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3837
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1994 | -2000 | -2000 | -6 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1919 | -2000 | -2000 | -81 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1760 | -1836 | -1836 | -76 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1760 | -1836 | -1836 | -76 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1697 | -1836 | -1836 | -139 | 92 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1682 | -1836 | -1836 | -154 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1643 | -1836 | -1836 | -193 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1641 | -1836 | -1836 | -195 | 89 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1635 | -1836 | -1836 | -201 | 89 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1632 | -1836 | -1836 | -204 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1608 | -1836 | -1836 | -228 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1601 | -1836 | -1836 | -235 | 87 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1081 | -1248 | -1248 | -168 | 87 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1077 | -1248 | -1248 | -172 | 86 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1076 | -1248 | -1248 | -172 | 86 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1066 | -1248 | -1248 | -183 | 85 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1065 | -1248 | -1248 | -183 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1364 | 1600 | 1600 | -236 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1364 | 1600 | 1600 | -236 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1361 | 1601 | 1601 | -240 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1361 | 1601 | 1601 | -240 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1058 | -1248 | -1248 | -190 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1230 | 1601 | 1601 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1230 | 1601 | 1601 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1474 | -1920 | -1920 | -446 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1524 | 2000 | 2000 | -476 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1510 | -2000 | -2000 | -490 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1507 | -2000 | -2000 | -493 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1500 | -2000 | -2000 | -500 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1498 | -2000 | -2000 | -502 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1491 | -2000 | -2000 | -509 | 75 | []

## 0030Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3837
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1994 |  | -2000 | -6 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1919 |  | -2000 | -81 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1760 |  | -1836 | -76 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1760 |  | -1836 | -76 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1697 |  | -1836 | -139 | 92 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1682 |  | -1836 | -154 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1643 |  | -1836 | -193 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1641 |  | -1836 | -195 | 89 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1635 |  | -1836 | -201 | 89 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1632 |  | -1836 | -204 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1608 |  | -1836 | -228 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1601 |  | -1836 | -235 | 87 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1081 |  | -1248 | -168 | 87 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1077 |  | -1248 | -172 | 86 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1076 |  | -1248 | -172 | 86 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1066 |  | -1248 | -183 | 85 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1065 |  | -1248 | -183 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1364 |  | 1600 | -236 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1364 |  | 1600 | -236 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1361 |  | 1601 | -240 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1361 |  | 1601 | -240 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1058 |  | -1248 | -190 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1233 |  | 1600 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1233 |  | 1600 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1230 |  | 1601 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1230 |  | 1601 | -371 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1474 |  | -1920 | -446 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1524 |  | 2000 | -476 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1510 |  | -2000 | -490 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1507 |  | -2000 | -493 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1500 |  | -2000 | -500 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1498 |  | -2000 | -502 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1491 |  | -2000 | -509 | 75 | []

## 0130Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3833
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1950 | -2000 | -2000 | -50 | 98 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1893 | -2000 | -2000 | -107 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1720 | -1836 | -1836 | -116 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1720 | -1836 | -1836 | -116 | 94 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1700 | -1836 | -1836 | -136 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1684 | -1836 | -1836 | -152 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1631 | -1836 | -1836 | -205 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1606 | -1836 | -1836 | -230 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1596 | -1836 | -1836 | -240 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1592 | -1836 | -1836 | -244 | 87 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1591 | -1836 | -1836 | -245 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1367 | 1600 | 1600 | -233 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1367 | 1600 | 1600 | -233 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1364 | 1601 | 1601 | -237 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1364 | 1601 | 1601 | -237 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1564 | -1836 | -1836 | -272 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1002 | -1248 | -1248 | -246 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -998 | -1248 | -1248 | -250 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -998 | -1248 | -1248 | -250 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -988 | -1248 | -1248 | -261 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -987 | -1248 | -1248 | -262 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -980 | -1248 | -1248 | -268 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1224 | 1601 | 1601 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1224 | 1601 | 1601 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1434 | -1920 | -1920 | -486 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1484 | 2000 | 2000 | -516 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1483 | -2000 | -2000 | -517 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1476 | -2000 | -2000 | -524 | 74 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1469 | -2000 | -2000 | -531 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1466 | -2000 | -2000 | -534 | 73 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1459 | -2000 | -2000 | -541 | 73 | []

## 0130Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3833
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1950 |  | -2000 | -50 | 98 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1893 |  | -2000 | -107 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1720 |  | -1836 | -116 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1720 |  | -1836 | -116 | 94 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1700 |  | -1836 | -136 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1684 |  | -1836 | -152 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1631 |  | -1836 | -205 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1606 |  | -1836 | -230 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1596 |  | -1836 | -240 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1592 |  | -1836 | -244 | 87 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1591 |  | -1836 | -245 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1367 |  | 1600 | -233 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1367 |  | 1600 | -233 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1364 |  | 1601 | -237 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1364 |  | 1601 | -237 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1564 |  | -1836 | -272 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1002 |  | -1248 | -246 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -998 |  | -1248 | -250 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -998 |  | -1248 | -250 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -988 |  | -1248 | -261 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -987 |  | -1248 | -262 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -980 |  | -1248 | -268 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1227 |  | 1600 | -373 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1227 |  | 1600 | -373 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1224 |  | 1601 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1224 |  | 1601 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1434 |  | -1920 | -486 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1484 |  | 2000 | -516 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1483 |  | -2000 | -517 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1476 |  | -2000 | -524 | 74 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1469 |  | -2000 | -531 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1466 |  | -2000 | -534 | 73 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1459 |  | -2000 | -541 | 73 | []

## 0230Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3801
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1906 | -2000 | -2000 | -94 | 95 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1860 | -2000 | -2000 | -140 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1691 | 1836 | 1836 | -145 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1691 | 1836 | 1836 | -145 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1657 | 1836 | 1836 | -179 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1641 | 1836 | 1836 | -195 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1602 | 1836 | 1836 | -234 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1578 | 1836 | 1836 | -258 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 | 1836 | 1836 | -268 | 85 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 | 1836 | 1836 | -271 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1562 | 1836 | 1836 | -274 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1359 | 1600 | 1600 | -241 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1359 | 1600 | 1600 | -241 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1356 | 1601 | 1601 | -245 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1356 | 1601 | 1601 | -245 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1534 | 1836 | 1836 | -302 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1027 | -1248 | -1248 | -221 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1024 | -1248 | -1248 | -224 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1023 | -1248 | -1248 | -226 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1013 | -1248 | -1248 | -235 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1013 | -1248 | -1248 | -235 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1007 | -1248 | -1248 | -242 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1216 | 1600 | 1600 | -384 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1216 | 1600 | 1600 | -384 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1212 | 1601 | 1601 | -389 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1212 | 1601 | 1601 | -389 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1460 | -2000 | -2000 | -540 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1445 | 2000 | 2000 | -555 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1444 | -2000 | -2000 | -556 | 72 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1441 | -2000 | -2000 | -559 | 72 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1434 | -2000 | -2000 | -566 | 72 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1428 | -2000 | -2000 | -572 | 71 | []

## 0230Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3801
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1906 |  | -2000 | -94 | 95 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1860 |  | -2000 | -140 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1691 |  | 1836 | -145 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1691 |  | 1836 | -145 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1657 |  | 1836 | -179 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1641 |  | 1836 | -195 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1602 |  | 1836 | -234 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1578 |  | 1836 | -258 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1836 | -268 | 85 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1836 | -271 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1562 |  | 1836 | -274 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1359 |  | 1600 | -241 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1359 |  | 1600 | -241 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1356 |  | 1601 | -245 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1356 |  | 1601 | -245 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1534 |  | 1836 | -302 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1027 |  | -1248 | -221 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1024 |  | -1248 | -224 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1023 |  | -1248 | -226 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1013 |  | -1248 | -235 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1013 |  | -1248 | -235 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1007 |  | -1248 | -242 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1216 |  | 1600 | -384 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1216 |  | 1600 | -384 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1212 |  | 1601 | -389 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1212 |  | 1601 | -389 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1460 |  | -2000 | -540 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1445 |  | 2000 | -555 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1444 |  | -2000 | -556 | 72 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1441 |  | -2000 | -559 | 72 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1434 |  | -2000 | -566 | 72 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1428 |  | -2000 | -572 | 71 | []

## 0330Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3771
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1860 | -2000 | -2000 | -140 | 93 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1822 | -2000 | -2000 | -178 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1644 | 1836 | 1836 | -192 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1644 | 1836 | 1836 | -192 | 90 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1597 | 1836 | 1836 | -239 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1391 | 1600 | 1600 | -209 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1391 | 1600 | 1600 | -209 | 87 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1388 | 1601 | 1601 | -213 | 87 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1388 | 1601 | 1601 | -213 | 87 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1581 | 1836 | 1836 | -255 | 86 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1550 | 1836 | 1836 | -286 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1044 | -1248 | -1248 | -205 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1041 | -1248 | -1248 | -207 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1039 | -1248 | -1248 | -209 | 83 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 | 1836 | 1836 | -309 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1517 | 1836 | 1836 | -319 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1031 | -1248 | -1248 | -217 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1030 | -1248 | -1248 | -218 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1515 | 1836 | 1836 | -321 | 83 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1512 | 1836 | 1836 | -324 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1024 | -1248 | -1248 | -224 | 82 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1485 | 1836 | 1836 | -351 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1220 | 1601 | 1601 | -381 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1220 | 1601 | 1601 | -381 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1431 | -2000 | -2000 | -569 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1412 | -2000 | -2000 | -588 | 71 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1410 | -2000 | -2000 | -590 | 70 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1405 | 2000 | 2000 | -595 | 70 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1402 | -2000 | -2000 | -598 | 70 | []

## 0330Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3771
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1860 |  | -2000 | -140 | 93 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1822 |  | -2000 | -178 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1644 |  | 1836 | -192 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1644 |  | 1836 | -192 | 90 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1597 |  | 1836 | -239 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1391 |  | 1600 | -209 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1391 |  | 1600 | -209 | 87 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1388 |  | 1601 | -213 | 87 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1388 |  | 1601 | -213 | 87 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1581 |  | 1836 | -255 | 86 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1550 |  | 1836 | -286 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1044 |  | -1248 | -205 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1041 |  | -1248 | -207 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1039 |  | -1248 | -209 | 83 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 |  | 1836 | -309 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1517 |  | 1836 | -319 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1031 |  | -1248 | -217 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1030 |  | -1248 | -218 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1515 |  | 1836 | -321 | 83 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1512 |  | 1836 | -324 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1024 |  | -1248 | -224 | 82 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1485 |  | 1836 | -351 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1223 |  | 1600 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1223 |  | 1600 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1220 |  | 1601 | -381 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1220 |  | 1601 | -381 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1431 |  | -2000 | -569 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1412 |  | -2000 | -588 | 71 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1410 |  | -2000 | -590 | 70 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1405 |  | 2000 | -595 | 70 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1402 |  | -2000 | -598 | 70 | []

## 0430Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3755
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1461 | 1600 | 1600 | -139 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1461 | 1600 | 1600 | -139 | 91 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1824 | -2000 | -2000 | -176 | 91 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1458 | 1601 | 1601 | -143 | 91 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1458 | 1601 | 1601 | -143 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1792 | -2000 | -2000 | -208 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 | 1836 | 1836 | -245 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 | 1836 | 1836 | -245 | 87 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1057 | -1248 | -1248 | -192 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1054 | -1248 | -1248 | -194 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1052 | -1248 | -1248 | -197 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1045 | -1248 | -1248 | -204 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1043 | -1248 | -1248 | -205 | 84 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1531 | 1836 | 1836 | -305 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1038 | -1248 | -1248 | -211 | 83 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1512 | 1836 | 1836 | -324 | 82 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1487 | 1836 | 1836 | -349 | 81 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1463 | 1836 | 1836 | -373 | 80 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1453 | 1836 | 1836 | -383 | 79 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 | 1836 | 1836 | -384 | 79 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1449 | 1836 | 1836 | -387 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1246 | 1601 | 1601 | -355 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1246 | 1601 | 1601 | -355 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1418 | 1836 | 1836 | -418 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1402 | -2000 | -2000 | -598 | 70 | []

## 0430Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3755
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1461 |  | 1600 | -139 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1461 |  | 1600 | -139 | 91 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1824 |  | -2000 | -176 | 91 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1458 |  | 1601 | -143 | 91 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1458 |  | 1601 | -143 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1792 |  | -2000 | -208 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 |  | 1836 | -245 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 |  | 1836 | -245 | 87 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1057 |  | -1248 | -192 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1054 |  | -1248 | -194 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1052 |  | -1248 | -197 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1045 |  | -1248 | -204 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1043 |  | -1248 | -205 | 84 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1531 |  | 1836 | -305 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1038 |  | -1248 | -211 | 83 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1512 |  | 1836 | -324 | 82 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1487 |  | 1836 | -349 | 81 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1463 |  | 1836 | -373 | 80 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1453 |  | 1836 | -383 | 79 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1836 | -384 | 79 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1449 |  | 1836 | -387 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1249 |  | 1600 | -351 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1249 |  | 1600 | -351 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1246 |  | 1601 | -355 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1246 |  | 1601 | -355 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1418 |  | 1836 | -418 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1402 |  | -2000 | -598 | 70 | []

## 0530Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3755
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1515 | 1600 | 1600 | -85 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1515 | 1600 | 1600 | -85 | 95 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1511 | 1601 | 1601 | -90 | 94 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1511 | 1601 | 1601 | -90 | 94 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1882 | -2000 | -2000 | -118 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1850 | -2000 | -2000 | -150 | 93 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1078 | -1248 | -1248 | -171 | 86 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1076 | -1248 | -1248 | -172 | 86 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1073 | -1248 | -1248 | -176 | 86 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1067 | -1248 | -1248 | -181 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1065 | -1248 | -1248 | -184 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1060 | -1248 | -1248 | -188 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1470 | 1836 | 1836 | -366 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1470 | 1836 | 1836 | -366 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1249 | 1601 | 1601 | -352 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1249 | 1601 | 1601 | -352 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1391 | 1836 | 1836 | -445 | 76 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1373 | 1836 | 1836 | -463 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1350 | 1836 | 1836 | -486 | 74 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1327 | 1836 | 1836 | -509 | 72 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1326 | 1836 | 1836 | -510 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1435 | 2000 | 2000 | -565 | 72 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1314 | 1836 | 1836 | -522 | 72 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1428 | -2000 | -2000 | -572 | 71 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1311 | 1836 | 1836 | -525 | 71 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1421 | -2000 | -2000 | -579 | 71 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1417 | -2000 | -2000 | -583 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1409 | -2000 | -2000 | -591 | 70 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1404 | -2000 | -2000 | -596 | 70 | []

## 0530Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3755
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1515 |  | 1600 | -85 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1515 |  | 1600 | -85 | 95 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1511 |  | 1601 | -90 | 94 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1511 |  | 1601 | -90 | 94 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1882 |  | -2000 | -118 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1850 |  | -2000 | -150 | 93 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1078 |  | -1248 | -171 | 86 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1076 |  | -1248 | -172 | 86 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1073 |  | -1248 | -176 | 86 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1067 |  | -1248 | -181 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1065 |  | -1248 | -184 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1060 |  | -1248 | -188 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1470 |  | 1836 | -366 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1470 |  | 1836 | -366 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1254 |  | 1600 | -346 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1254 |  | 1600 | -346 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1249 |  | 1601 | -352 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1249 |  | 1601 | -352 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1391 |  | 1836 | -445 | 76 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1373 |  | 1836 | -463 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1350 |  | 1836 | -486 | 74 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1327 |  | 1836 | -509 | 72 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1326 |  | 1836 | -510 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1435 |  | 2000 | -565 | 72 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1314 |  | 1836 | -522 | 72 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1428 |  | -2000 | -572 | 71 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1311 |  | 1836 | -525 | 71 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1421 |  | -2000 | -579 | 71 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1417 |  | -2000 | -583 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1409 |  | -2000 | -591 | 70 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1404 |  | -2000 | -596 | 70 | []

## 0630Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3726
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 | 1601 | 1601 | -8 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 | 1601 | 1601 | -8 | 99 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1968 | -2000 | -2000 | -32 | 98 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1937 | -2000 | -2000 | -63 | 97 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 | -1248 | -1248 | -245 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 | -1248 | -1248 | -246 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -999 | -1248 | -1248 | -250 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -996 | -1248 | -1248 | -253 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -992 | -1248 | -1248 | -256 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -989 | -1248 | -1248 | -259 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1236 | 1601 | 1601 | -365 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1236 | 1601 | 1601 | -365 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1513 | -2000 | -2000 | -487 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1494 | 2000 | 2000 | -506 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1489 | -2000 | -2000 | -511 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1477 | -2000 | -2000 | -523 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1474 | -2000 | -2000 | -526 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1466 | -2000 | -2000 | -534 | 73 | []

## 0630Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3726
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1595 |  | 1600 | -5 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 |  | 1600 | -5 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 |  | 1601 | -8 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 |  | 1601 | -8 | 99 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1968 |  | -2000 | -32 | 98 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1937 |  | -2000 | -63 | 97 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 |  | -1248 | -245 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 |  | -1248 | -246 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -999 |  | -1248 | -250 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -996 |  | -1248 | -253 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -992 |  | -1248 | -256 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -989 |  | -1248 | -259 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1239 |  | 1600 | -361 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1239 |  | 1600 | -361 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1236 |  | 1601 | -365 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1236 |  | 1601 | -365 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1513 |  | -2000 | -487 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1494 |  | 2000 | -506 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1489 |  | -2000 | -511 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1477 |  | -2000 | -523 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1474 |  | -2000 | -526 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1466 |  | -2000 | -534 | 73 | []

## 0730Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2547
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1586 | 1601 | 1601 | -15 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1586 | 1601 | 1601 | -15 | 99 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -951 | -1248 | -1248 | -298 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -949 | -1248 | -1248 | -299 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -946 | -1248 | -1248 | -302 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -945 | -1248 | -1248 | -304 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -940 | -1248 | -1248 | -308 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -940 | -1248 | -1248 | -308 | 75 | []

## 0730Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2547
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1591 |  | 1600 | -9 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1591 |  | 1600 | -9 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1586 |  | 1601 | -15 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1586 |  | 1601 | -15 | 99 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -951 |  | -1248 | -298 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -949 |  | -1248 | -299 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -946 |  | -1248 | -302 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -945 |  | -1248 | -304 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -940 |  | -1248 | -308 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -940 |  | -1248 | -308 | 75 | []

## 0830Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2888
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1586 | 1601 | 1601 | -15 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1586 | 1601 | 1601 | -15 | 99 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 | -1248 | -1248 | -246 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1002 | -1248 | -1248 | -247 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -998 | -1248 | -1248 | -250 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -995 | -1248 | -1248 | -254 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -991 | -1248 | -1248 | -257 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -988 | -1248 | -1248 | -260 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1263 | 1600 | 1600 | -337 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1263 | 1600 | 1600 | -337 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1258 | 1601 | 1601 | -343 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1258 | 1601 | 1601 | -343 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1437 | -1920 | -1920 | -483 | 75 | []

## 0830Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2888
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1591 |  | 1600 | -9 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1591 |  | 1600 | -9 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1586 |  | 1601 | -15 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1586 |  | 1601 | -15 | 99 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 |  | -1248 | -246 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1002 |  | -1248 | -247 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -998 |  | -1248 | -250 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -995 |  | -1248 | -254 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -991 |  | -1248 | -257 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -988 |  | -1248 | -260 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1263 |  | 1600 | -337 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1263 |  | 1600 | -337 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1258 |  | 1601 | -343 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1258 |  | 1601 | -343 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1437 |  | -1920 | -483 | 75 | []

## 0930Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3175
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 | 1601 | 1601 | -11 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1577 | 1836 | 1836 | -259 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1577 | 1836 | 1836 | -259 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1371 | 1600 | 1600 | -229 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1371 | 1600 | 1600 | -229 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1365 | 1601 | 1601 | -236 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1365 | 1601 | 1601 | -236 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1039 | -1248 | -1248 | -210 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1036 | -1248 | -1248 | -212 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1034 | -1248 | -1248 | -214 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1027 | -1248 | -1248 | -222 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1025 | -1248 | -1248 | -223 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1020 | -1248 | -1248 | -228 | 82 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1484 | 1836 | 1836 | -352 | 81 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1478 | 1836 | 1836 | -358 | 81 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1421 | 1836 | 1836 | -415 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1479 | -1920 | -1920 | -441 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1414 | 1836 | 1836 | -422 | 77 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1410 | 1836 | 1836 | -426 | 77 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1408 | 1836 | 1836 | -428 | 77 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1405 | 1836 | 1836 | -431 | 77 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1400 | 1836 | 1836 | -436 | 76 | []

## 0930Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3175
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1596 |  | 1600 | -4 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1596 |  | 1600 | -4 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1590 |  | 1601 | -11 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1590 |  | 1601 | -11 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1577 |  | 1836 | -259 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1577 |  | 1836 | -259 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1371 |  | 1600 | -229 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1371 |  | 1600 | -229 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1365 |  | 1601 | -236 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1365 |  | 1601 | -236 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1039 |  | -1248 | -210 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1036 |  | -1248 | -212 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1034 |  | -1248 | -214 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1027 |  | -1248 | -222 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1025 |  | -1248 | -223 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1020 |  | -1248 | -228 | 82 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1484 |  | 1836 | -352 | 81 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1478 |  | 1836 | -358 | 81 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1421 |  | 1836 | -415 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1479 |  | -1920 | -441 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1414 |  | 1836 | -422 | 77 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1410 |  | 1836 | -426 | 77 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1408 |  | 1836 | -428 | 77 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1405 |  | 1836 | -431 | 77 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1400 |  | 1836 | -436 | 76 | []

## 1030Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3207
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1592 | 1600 | 1600 | -8 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1592 | 1600 | 1600 | -8 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1587 | 1601 | 1601 | -14 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1587 | 1601 | 1601 | -14 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1576 | 1836 | 1836 | -260 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1576 | 1836 | 1836 | -260 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1371 | 1600 | 1600 | -229 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1371 | 1600 | 1600 | -229 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1366 | 1601 | 1601 | -235 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1366 | 1601 | 1601 | -235 | 85 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 | 1836 | 1836 | -391 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1435 | 1836 | 1836 | -401 | 78 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1418 | 1836 | 1836 | -418 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1410 | 1836 | 1836 | -426 | 77 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1409 | 1836 | 1836 | -427 | 77 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1405 | 1836 | 1836 | -431 | 77 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1400 | 1836 | 1836 | -436 | 76 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1397 | 1836 | 1836 | -439 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1354 | -1920 | -1920 | -566 | 71 | []

## 1030Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3207
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1592 |  | 1600 | -8 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1592 |  | 1600 | -8 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1587 |  | 1601 | -14 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1587 |  | 1601 | -14 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1576 |  | 1836 | -260 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1576 |  | 1836 | -260 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1371 |  | 1600 | -229 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1371 |  | 1600 | -229 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1366 |  | 1601 | -235 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1366 |  | 1601 | -235 | 85 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1836 | -391 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1836 | -401 | 78 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1418 |  | 1836 | -418 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1410 |  | 1836 | -426 | 77 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1409 |  | 1836 | -427 | 77 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1405 |  | 1836 | -431 | 77 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1400 |  | 1836 | -436 | 76 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1397 |  | 1836 | -439 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1354 |  | -1920 | -566 | 71 | []

## 1130Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3289
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 | 1601 | 1601 | -6 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1679 | 1836 | 1836 | -157 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1679 | 1836 | 1836 | -157 | 91 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1406 | 1600 | 1600 | -194 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1406 | 1600 | 1600 | -194 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1401 | 1601 | 1601 | -200 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1401 | 1601 | 1601 | -200 | 88 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1544 | 1836 | 1836 | -292 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1537 | 1836 | 1836 | -299 | 84 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1523 | 1836 | 1836 | -313 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1514 | 1836 | 1836 | -322 | 82 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1510 | 1836 | 1836 | -326 | 82 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1510 | 1836 | 1836 | -326 | 82 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1509 | 1836 | 1836 | -327 | 82 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1500 | 1836 | 1836 | -336 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1369 | -1920 | -1920 | -551 | 71 | []

## 1130Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3289
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1600 |  | 1600 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1600 |  | 1600 | 0 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1595 |  | 1601 | -6 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1595 |  | 1601 | -6 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1679 |  | 1836 | -157 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1679 |  | 1836 | -157 | 91 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1406 |  | 1600 | -194 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1406 |  | 1600 | -194 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1401 |  | 1601 | -200 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1401 |  | 1601 | -200 | 88 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1544 |  | 1836 | -292 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1537 |  | 1836 | -299 | 84 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1523 |  | 1836 | -313 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1514 |  | 1836 | -322 | 82 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1510 |  | 1836 | -326 | 82 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1510 |  | 1836 | -326 | 82 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1509 |  | 1836 | -327 | 82 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1500 |  | 1836 | -336 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1369 |  | -1920 | -551 | 71 | []

## 1230Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3182
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1594 | 1601 | 1601 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1594 | 1601 | 1601 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1528 | 1836 | 1836 | -308 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1528 | 1836 | 1836 | -308 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1327 | 1600 | 1600 | -273 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1327 | 1600 | 1600 | -273 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1323 | 1601 | 1601 | -278 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1323 | 1601 | 1601 | -278 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1415 | 1836 | 1836 | -421 | 77 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1408 | 1836 | 1836 | -428 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1389 | 1836 | 1836 | -447 | 76 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1377 | 1836 | 1836 | -459 | 75 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1371 | 1836 | 1836 | -465 | 75 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1367 | 1836 | 1836 | -469 | 74 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1362 | 1836 | 1836 | -474 | 74 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1359 | 1836 | 1836 | -477 | 74 | []

## 1230Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3182
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 |  | 1600 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 |  | 1600 | -2 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1594 |  | 1601 | -7 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1594 |  | 1601 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1528 |  | 1836 | -308 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1528 |  | 1836 | -308 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1327 |  | 1600 | -273 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1327 |  | 1600 | -273 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1323 |  | 1601 | -278 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1323 |  | 1601 | -278 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1415 |  | 1836 | -421 | 77 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1408 |  | 1836 | -428 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1389 |  | 1836 | -447 | 76 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1377 |  | 1836 | -459 | 75 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1371 |  | 1836 | -465 | 75 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1367 |  | 1836 | -469 | 74 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1362 |  | 1836 | -474 | 74 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1359 |  | 1836 | -477 | 74 | []

## 1330Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3137
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 | 1601 | 1601 | -8 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 | 1601 | 1601 | -8 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1541 | 1836 | 1836 | -295 | 84 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1541 | 1836 | 1836 | -295 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1035 | -1248 | -1248 | -213 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1326 | 1600 | 1600 | -274 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1326 | 1600 | 1600 | -274 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1033 | -1248 | -1248 | -216 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1030 | -1248 | -1248 | -218 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1321 | 1601 | 1601 | -280 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1321 | 1601 | 1601 | -280 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1023 | -1248 | -1248 | -225 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1022 | -1248 | -1248 | -227 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1017 | -1248 | -1248 | -232 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1467 | 1836 | 1836 | -369 | 80 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 | 1836 | 1836 | -378 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1465 | -1920 | -1920 | -455 | 76 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1398 | 1836 | 1836 | -438 | 76 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1385 | 1836 | 1836 | -451 | 75 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1382 | 1836 | 1836 | -454 | 75 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1380 | 1836 | 1836 | -456 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1376 | 1836 | 1836 | -460 | 75 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1372 | 1836 | 1836 | -464 | 75 | []

## 1330Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3137
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 |  | 1600 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1598 |  | 1600 | -2 | 100 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1593 |  | 1601 | -8 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 |  | 1601 | -8 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1541 |  | 1836 | -295 | 84 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1541 |  | 1836 | -295 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1035 |  | -1248 | -213 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1326 |  | 1600 | -274 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1326 |  | 1600 | -274 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1033 |  | -1248 | -216 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1030 |  | -1248 | -218 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1321 |  | 1601 | -280 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1321 |  | 1601 | -280 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1023 |  | -1248 | -225 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1022 |  | -1248 | -227 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1017 |  | -1248 | -232 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1467 |  | 1836 | -369 | 80 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 |  | 1836 | -378 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1465 |  | -1920 | -455 | 76 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1398 |  | 1836 | -438 | 76 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1385 |  | 1836 | -451 | 75 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1382 |  | 1836 | -454 | 75 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1380 |  | 1836 | -456 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1376 |  | 1836 | -460 | 75 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1372 |  | 1836 | -464 | 75 | []

## 1430Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3026
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1592 | 1601 | 1601 | -9 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1592 | 1601 | 1601 | -9 | 99 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1023 | -1248 | -1248 | -226 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1021 | -1248 | -1248 | -227 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1018 | -1248 | -1248 | -230 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1013 | -1248 | -1248 | -236 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1010 | -1248 | -1248 | -238 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1006 | -1248 | -1248 | -242 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1283 | 1600 | 1600 | -317 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1283 | 1600 | 1600 | -317 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1278 | 1601 | 1601 | -323 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1278 | 1601 | 1601 | -323 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1386 | 1836 | 1836 | -450 | 75 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1386 | 1836 | 1836 | -450 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1439 | -1920 | -1920 | -481 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1317 | 1836 | 1836 | -519 | 72 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1304 | 1836 | 1836 | -532 | 71 | []

## 1430Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3026
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 |  | 1600 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1597 |  | 1600 | -3 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1592 |  | 1601 | -9 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1592 |  | 1601 | -9 | 99 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1023 |  | -1248 | -226 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1021 |  | -1248 | -227 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1018 |  | -1248 | -230 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1013 |  | -1248 | -236 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1010 |  | -1248 | -238 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1006 |  | -1248 | -242 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1283 |  | 1600 | -317 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1283 |  | 1600 | -317 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1278 |  | 1601 | -323 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1278 |  | 1601 | -323 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1386 |  | 1836 | -450 | 75 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1386 |  | 1836 | -450 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1439 |  | -1920 | -481 | 75 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1317 |  | 1836 | -519 | 72 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1304 |  | 1836 | -532 | 71 | []

## 1530Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2799
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -984 | -1248 | -1248 | -265 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -984 | -1248 | -1248 | -265 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -979 | -1248 | -1248 | -269 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -978 | -1248 | -1248 | -271 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -973 | -1248 | -1248 | -275 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -971 | -1248 | -1248 | -277 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1177 | 1601 | 1601 | -424 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1177 | 1601 | 1601 | -424 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1384 | -1920 | -1920 | -536 | 72 | []

## 1530Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2799
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 |  | 1600 | -7 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 |  | 1600 | -7 | 100 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 |  | 1601 | -13 | 99 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -984 |  | -1248 | -265 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -984 |  | -1248 | -265 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -979 |  | -1248 | -269 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -978 |  | -1248 | -271 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -973 |  | -1248 | -275 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -971 |  | -1248 | -277 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1182 |  | 1600 | -418 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1182 |  | 1600 | -418 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1177 |  | 1601 | -424 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1177 |  | 1601 | -424 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1384 |  | -1920 | -536 | 72 | []

## 1630Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2936
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1587 | 1601 | 1601 | -14 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1587 | 1601 | 1601 | -14 | 99 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -999 | -1248 | -1248 | -249 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -998 | -1248 | -1248 | -250 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -995 | -1248 | -1248 | -254 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -991 | -1248 | -1248 | -258 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -988 | -1248 | -1248 | -261 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -985 | -1248 | -1248 | -264 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1234 | 1601 | 1601 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1234 | 1601 | 1601 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1438 | -1920 | -1920 | -482 | 75 | []

## 1630Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2936
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1591 |  | 1600 | -9 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1591 |  | 1600 | -9 | 99 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1587 |  | 1601 | -14 | 99 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1587 |  | 1601 | -14 | 99 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -999 |  | -1248 | -249 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -998 |  | -1248 | -250 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -995 |  | -1248 | -254 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -991 |  | -1248 | -258 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -988 |  | -1248 | -261 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -985 |  | -1248 | -264 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1239 |  | 1600 | -361 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1239 |  | 1600 | -361 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1234 |  | 1601 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1234 |  | 1601 | -367 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1438 |  | -1920 | -482 | 75 | []

## 1730Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2978
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1817 | -2000 | -2000 | -183 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1748 | -2000 | -2000 | -252 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1535 | -1836 | -1836 | -301 | 84 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1449 | -2000 | -2000 | -551 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -902 | -1248 | -1248 | -347 | 72 | []
BC | Base Case | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1156 | 1601 | 1601 | -445 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -899 | -1248 | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -894 | -1248 | -1248 | -354 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -892 | -1248 | -1248 | -357 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -888 | -1248 | -1248 | -360 | 71 | []

## 1730Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2978
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1593 |  | 1600 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1588 |  | 1601 | -13 | 99 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1817 |  | -2000 | -183 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1748 |  | -2000 | -252 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1535 |  | -1836 | -301 | 84 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1161 |  | 1600 | -439 | 73 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1449 |  | -2000 | -551 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -902 |  | -1248 | -347 | 72 | []
BC | Base Case | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1156 |  | 1601 | -445 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -899 |  | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -894 |  | -1248 | -354 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -892 |  | -1248 | -357 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -888 |  | -1248 | -360 | 71 | []

## 1830Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3529
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 | -2000 | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1908 | -2000 | -2000 | -92 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1360 | 1600 | 1600 | -240 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1360 | 1600 | 1600 | -240 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1355 | 1601 | 1601 | -246 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1355 | 1601 | 1601 | -246 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -991 | -1248 | -1248 | -258 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -989 | -1248 | -1248 | -260 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -986 | -1248 | -1248 | -262 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -980 | -1248 | -1248 | -269 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -978 | -1248 | -1248 | -270 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -973 | -1248 | -1248 | -275 | 78 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1556 | -2000 | -2000 | -444 | 78 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1521 | -2000 | -2000 | -479 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1513 | -2000 | -2000 | -487 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1512 | -2000 | -2000 | -488 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1443 | -1920 | -1920 | -477 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1502 | -2000 | -2000 | -498 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1496 | 2000 | 2000 | -504 | 75 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1368 | -1836 | -1836 | -468 | 75 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1368 | -1836 | -1836 | -468 | 75 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1347 | -1836 | -1836 | -489 | 73 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1346 | -1836 | -1836 | -490 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1134 | 1600 | 1600 | -466 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1134 | 1600 | 1600 | -466 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1129 | 1601 | 1601 | -472 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1129 | 1601 | 1601 | -472 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3529
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 |  | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1908 |  | -2000 | -92 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1360 |  | 1600 | -240 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1360 |  | 1600 | -240 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1355 |  | 1601 | -246 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1355 |  | 1601 | -246 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -991 |  | -1248 | -258 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -989 |  | -1248 | -260 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -986 |  | -1248 | -262 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -980 |  | -1248 | -269 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -978 |  | -1248 | -270 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -973 |  | -1248 | -275 | 78 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1556 |  | -2000 | -444 | 78 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1521 |  | -2000 | -479 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1513 |  | -2000 | -487 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1512 |  | -2000 | -488 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1443 |  | -1920 | -477 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1502 |  | -2000 | -498 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1496 |  | 2000 | -504 | 75 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1368 |  | -1836 | -468 | 75 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1368 |  | -1836 | -468 | 75 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1347 |  | -1836 | -489 | 73 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1346 |  | -1836 | -490 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1134 |  | 1600 | -466 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1134 |  | 1600 | -466 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1129 |  | 1601 | -472 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1129 |  | 1601 | -472 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3585
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 | -2000 | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1891 | -2000 | -2000 | -109 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1350 | 1600 | 1600 | -250 | 84 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1350 | 1600 | 1600 | -250 | 84 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1345 | 1601 | 1601 | -256 | 84 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1345 | 1601 | 1601 | -256 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1446 | -1836 | -1836 | -390 | 79 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1446 | -1836 | -1836 | -390 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1446 | -1836 | -1836 | -390 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -979 | -1248 | -1248 | -270 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 | -1248 | -1248 | -272 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1433 | -1836 | -1836 | -403 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -974 | -1248 | -1248 | -274 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -966 | -1248 | -1248 | -282 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -966 | -1248 | -1248 | -283 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1545 | -2000 | -2000 | -455 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -960 | -1248 | -1248 | -289 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1521 | -2000 | -2000 | -479 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1517 | -2000 | -2000 | -483 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1516 | -2000 | -2000 | -484 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1454 | -1920 | -1920 | -466 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1511 | -2000 | -2000 | -489 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1501 | 2000 | 2000 | -499 | 75 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1373 | -1836 | -1836 | -463 | 75 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1353 | -1836 | -1836 | -483 | 74 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1344 | -1836 | -1836 | -492 | 73 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1344 | -1836 | -1836 | -492 | 73 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1319 | -1836 | -1836 | -517 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1149 | 1600 | 1600 | -451 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1149 | 1600 | 1600 | -451 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1144 | 1601 | 1601 | -457 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1144 | 1601 | 1601 | -457 | 71 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1303 | -1836 | -1836 | -533 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3585
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 |  | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1891 |  | -2000 | -109 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1350 |  | 1600 | -250 | 84 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1350 |  | 1600 | -250 | 84 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1345 |  | 1601 | -256 | 84 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1345 |  | 1601 | -256 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1446 |  | -1836 | -390 | 79 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1446 |  | -1836 | -390 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1446 |  | -1836 | -390 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -979 |  | -1248 | -270 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 |  | -1248 | -272 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1433 |  | -1836 | -403 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -974 |  | -1248 | -274 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -966 |  | -1248 | -282 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -966 |  | -1248 | -283 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1545 |  | -2000 | -455 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -960 |  | -1248 | -289 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1521 |  | -2000 | -479 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1517 |  | -2000 | -483 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1516 |  | -2000 | -484 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1454 |  | -1920 | -466 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1511 |  | -2000 | -489 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1501 |  | 2000 | -499 | 75 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1373 |  | -1836 | -463 | 75 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1353 |  | -1836 | -483 | 74 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1344 |  | -1836 | -492 | 73 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1344 |  | -1836 | -492 | 73 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1319 |  | -1836 | -517 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1149 |  | 1600 | -451 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1149 |  | 1600 | -451 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1144 |  | 1601 | -457 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1144 |  | 1601 | -457 | 71 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1303 |  | -1836 | -533 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3652
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1996 | -2000 | -2000 | -4 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1879 | -2000 | -2000 | -121 | 94 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1383 | 1600 | 1600 | -217 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1383 | 1600 | 1600 | -217 | 86 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1378 | 1601 | 1601 | -223 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1378 | 1601 | 1601 | -223 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 | 1836 | 1836 | -329 | 82 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 | 1836 | 1836 | -329 | 82 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1490 | 1836 | 1836 | -346 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1481 | 1836 | 1836 | -355 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -993 | -1248 | -1248 | -256 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -990 | -1248 | -1248 | -258 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -988 | -1248 | -1248 | -260 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -980 | -1248 | -1248 | -268 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -980 | -1248 | -1248 | -269 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -974 | -1248 | -1248 | -275 | 78 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1426 | 1836 | 1836 | -410 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1471 | -1920 | -1920 | -449 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1403 | 1836 | 1836 | -433 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1529 | -2000 | -2000 | -471 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1527 | -2000 | -2000 | -473 | 76 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1398 | 1836 | 1836 | -438 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1517 | -2000 | -2000 | -483 | 76 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1393 | 1836 | 1836 | -443 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1517 | -2000 | -2000 | -483 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1512 | -2000 | -2000 | -488 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1512 | 2000 | 2000 | -488 | 76 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1376 | 1836 | 1836 | -460 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1353 | 1836 | 1836 | -483 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1178 | 1601 | 1601 | -423 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1178 | 1601 | 1601 | -423 | 74 | []

## 2030Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3652
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1996 |  | -2000 | -4 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1879 |  | -2000 | -121 | 94 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1383 |  | 1600 | -217 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1383 |  | 1600 | -217 | 86 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1378 |  | 1601 | -223 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1378 |  | 1601 | -223 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 |  | 1836 | -329 | 82 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 |  | 1836 | -329 | 82 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1490 |  | 1836 | -346 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1481 |  | 1836 | -355 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -993 |  | -1248 | -256 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -990 |  | -1248 | -258 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -988 |  | -1248 | -260 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -980 |  | -1248 | -268 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -980 |  | -1248 | -269 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -974 |  | -1248 | -275 | 78 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1426 |  | 1836 | -410 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1471 |  | -1920 | -449 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1403 |  | 1836 | -433 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1529 |  | -2000 | -471 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1527 |  | -2000 | -473 | 76 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1398 |  | 1836 | -438 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1517 |  | -2000 | -483 | 76 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1393 |  | 1836 | -443 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1517 |  | -2000 | -483 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1512 |  | -2000 | -488 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1512 |  | 2000 | -488 | 76 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1376 |  | 1836 | -460 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1183 |  | 1600 | -417 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1183 |  | 1600 | -417 | 74 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1353 |  | 1836 | -483 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1178 |  | 1601 | -423 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1178 |  | 1601 | -423 | 74 | []

## 2130Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3479
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1997 | -2000 | -2000 | -3 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1864 | -2000 | -2000 | -136 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1341 | 1600 | 1600 | -259 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1341 | 1600 | 1600 | -259 | 84 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1336 | 1601 | 1601 | -265 | 83 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1336 | 1601 | 1601 | -265 | 83 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1529 | -2000 | -2000 | -471 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1523 | 2000 | 2000 | -477 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1518 | -2000 | -2000 | -482 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1514 | -2000 | -2000 | -486 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1509 | -2000 | -2000 | -491 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1503 | -2000 | -2000 | -497 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -913 | -1248 | -1248 | -335 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -912 | -1248 | -1248 | -336 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -909 | -1248 | -1248 | -339 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -904 | -1248 | -1248 | -344 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -902 | -1248 | -1248 | -347 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -898 | -1248 | -1248 | -350 | 72 | []

## 2130Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3479
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1997 |  | -2000 | -3 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1864 |  | -2000 | -136 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1341 |  | 1600 | -259 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1341 |  | 1600 | -259 | 84 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1336 |  | 1601 | -265 | 83 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1336 |  | 1601 | -265 | 83 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1529 |  | -2000 | -471 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1523 |  | 2000 | -477 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1518 |  | -2000 | -482 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1514 |  | -2000 | -486 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1509 |  | -2000 | -491 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1503 |  | -2000 | -497 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -913 |  | -1248 | -335 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -912 |  | -1248 | -336 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -909 |  | -1248 | -339 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -904 |  | -1248 | -344 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -902 |  | -1248 | -347 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -898 |  | -1248 | -350 | 72 | []

## 2230Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3438
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 | -2000 | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1850 | -2000 | -2000 | -150 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1309 | 1600 | 1600 | -291 | 82 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1309 | 1600 | 1600 | -291 | 82 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1304 | 1601 | 1601 | -297 | 81 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1304 | 1601 | 1601 | -297 | 81 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1529 | -2000 | -2000 | -471 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1525 | 2000 | 2000 | -475 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1519 | -2000 | -2000 | -481 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1509 | -2000 | -2000 | -491 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1496 | -2000 | -2000 | -504 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1495 | -2000 | -2000 | -505 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -884 | -1248 | -1248 | -365 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -883 | -1248 | -1248 | -366 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -880 | -1248 | -1248 | -369 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -875 | -1248 | -1248 | -373 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3438
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 |  | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1850 |  | -2000 | -150 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1309 |  | 1600 | -291 | 82 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1309 |  | 1600 | -291 | 82 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1304 |  | 1601 | -297 | 81 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1304 |  | 1601 | -297 | 81 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1529 |  | -2000 | -471 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1525 |  | 2000 | -475 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1519 |  | -2000 | -481 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1509 |  | -2000 | -491 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1496 |  | -2000 | -504 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1495 |  | -2000 | -505 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -884 |  | -1248 | -365 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -883 |  | -1248 | -366 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -880 |  | -1248 | -369 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -875 |  | -1248 | -373 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3476
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 | -2000 | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1847 | -2000 | -2000 | -153 | 92 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -970 | -1248 | -1248 | -279 | 78 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -967 | -1248 | -1248 | -281 | 77 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1238 | 1601 | 1601 | -363 | 77 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1238 | 1601 | 1601 | -363 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -965 | -1248 | -1248 | -283 | 77 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1415 | -1836 | -1836 | -421 | 77 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1410 | -1836 | -1836 | -426 | 77 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1410 | -1836 | -1836 | -426 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -958 | -1248 | -1248 | -291 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -957 | -1248 | -1248 | -292 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1533 | -2000 | -2000 | -467 | 77 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1405 | -1836 | -1836 | -431 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -951 | -1248 | -1248 | -297 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1523 | 2000 | 2000 | -477 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1522 | -2000 | -2000 | -478 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1507 | -2000 | -2000 | -493 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1498 | -2000 | -2000 | -502 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1495 | -2000 | -2000 | -505 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1407 | -1920 | -1920 | -513 | 73 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1337 | -1836 | -1836 | -499 | 73 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1317 | -1836 | -1836 | -519 | 72 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1312 | -1836 | -1836 | -524 | 71 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1301 | -1836 | -1836 | -535 | 71 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1294 | -1836 | -1836 | -542 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2024-02-12 19:09
Business day: | 13.02.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3476
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 |  | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1847 |  | -2000 | -153 | 92 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -970 |  | -1248 | -279 | 78 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1242 |  | 1600 | -358 | 78 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1242 |  | 1600 | -358 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -967 |  | -1248 | -281 | 77 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1238 |  | 1601 | -363 | 77 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1238 |  | 1601 | -363 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -965 |  | -1248 | -283 | 77 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1415 |  | -1836 | -421 | 77 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1410 |  | -1836 | -426 | 77 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1410 |  | -1836 | -426 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -958 |  | -1248 | -291 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -957 |  | -1248 | -292 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1533 |  | -2000 | -467 | 77 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1405 |  | -1836 | -431 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -951 |  | -1248 | -297 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1523 |  | 2000 | -477 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1522 |  | -2000 | -478 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1507 |  | -2000 | -493 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1498 |  | -2000 | -502 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1495 |  | -2000 | -505 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [OPP] [RO] | RTINTA1 _RURE241 _1:line | -1407 |  | -1920 | -513 | 73 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1337 |  | -1836 | -499 | 73 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1317 |  | -1836 | -519 | 72 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1312 |  | -1836 | -524 | 71 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1301 |  | -1836 | -535 | 71 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1294 |  | -1836 | -542 | 70 | []