## 0030Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3644
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1883 | -2000 | -2000 | -117 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1863 | -2000 | -2000 | -137 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 | 1836 | 1836 | -170 | 91 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 | 1836 | 1836 | -170 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1625 | 1836 | 1836 | -211 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1608 | 1836 | 1836 | -228 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1578 | 1836 | 1836 | -258 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1571 | 1836 | 1836 | -265 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1836 | 1836 | -267 | 85 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1554 | 1836 | 1836 | -282 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1550 | 1836 | 1836 | -286 | 84 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1545 | 1836 | 1836 | -291 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1019 | -1248 | -1248 | -230 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1016 | -1248 | -1248 | -232 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1014 | -1248 | -1248 | -234 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1007 | -1248 | -1248 | -242 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1006 | -1248 | -1248 | -243 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1000 | -1248 | -1248 | -248 | 80 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1277 | 1600 | 1600 | -323 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1277 | 1600 | 1600 | -323 | 80 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1274 | 1601 | 1601 | -327 | 80 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1274 | 1601 | 1601 | -327 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1471 | -2000 | -2000 | -529 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1157 | 1601 | 1601 | -444 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1157 | 1601 | 1601 | -444 | 72 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1436 | -2000 | -2000 | -564 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1423 | -2000 | -2000 | -577 | 71 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1418 | -2000 | -2000 | -582 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1415 | 2000 | 2000 | -585 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1414 | -2000 | -2000 | -586 | 71 | []

## 0030Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3644
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1883 |  | -2000 | -117 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1863 |  | -2000 | -137 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 |  | 1836 | -170 | 91 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 |  | 1836 | -170 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1625 |  | 1836 | -211 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1608 |  | 1836 | -228 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1578 |  | 1836 | -258 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1571 |  | 1836 | -265 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1836 | -267 | 85 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1554 |  | 1836 | -282 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1550 |  | 1836 | -286 | 84 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1545 |  | 1836 | -291 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1019 |  | -1248 | -230 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1016 |  | -1248 | -232 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1014 |  | -1248 | -234 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1007 |  | -1248 | -242 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1006 |  | -1248 | -243 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1000 |  | -1248 | -248 | 80 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1277 |  | 1600 | -323 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1277 |  | 1600 | -323 | 80 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1274 |  | 1601 | -327 | 80 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1274 |  | 1601 | -327 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1471 |  | -2000 | -529 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1161 |  | 1600 | -439 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1161 |  | 1600 | -439 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1157 |  | 1601 | -444 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1157 |  | 1601 | -444 | 72 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1436 |  | -2000 | -564 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1423 |  | -2000 | -577 | 71 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1418 |  | -2000 | -582 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1415 |  | 2000 | -585 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1414 |  | -2000 | -586 | 71 | []

## 0130Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3616
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1852 | -2000 | -2000 | -148 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 | 1836 | 1836 | -151 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 | 1836 | 1836 | -151 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1833 | -2000 | -2000 | -167 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1642 | 1836 | 1836 | -194 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1625 | 1836 | 1836 | -211 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1598 | 1836 | 1836 | -238 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 | 1836 | 1836 | -245 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1589 | 1836 | 1836 | -247 | 87 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1575 | 1836 | 1836 | -261 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1567 | 1836 | 1836 | -269 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 | 1836 | 1836 | -270 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1031 | -1248 | -1248 | -218 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1029 | -1248 | -1248 | -220 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1026 | -1248 | -1248 | -222 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1020 | -1248 | -1248 | -229 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1018 | -1248 | -1248 | -230 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1013 | -1248 | -1248 | -236 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1233 | 1601 | 1601 | -368 | 77 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1233 | 1601 | 1601 | -368 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1450 | -2000 | -2000 | -550 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1141 | 1600 | 1600 | -459 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1141 | 1600 | 1600 | -459 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1137 | 1601 | 1601 | -464 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1137 | 1601 | 1601 | -464 | 71 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1414 | -2000 | -2000 | -586 | 71 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1402 | -2000 | -2000 | -598 | 70 | []

## 0130Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3616
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1852 |  | -2000 | -148 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 |  | 1836 | -151 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 |  | 1836 | -151 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1833 |  | -2000 | -167 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1642 |  | 1836 | -194 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1625 |  | 1836 | -211 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1598 |  | 1836 | -238 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 |  | 1836 | -245 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1589 |  | 1836 | -247 | 87 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1575 |  | 1836 | -261 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1836 | -269 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1836 | -270 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1031 |  | -1248 | -218 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1029 |  | -1248 | -220 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1026 |  | -1248 | -222 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1020 |  | -1248 | -229 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1018 |  | -1248 | -230 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1013 |  | -1248 | -236 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1236 |  | 1600 | -364 | 77 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1236 |  | 1600 | -364 | 77 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1233 |  | 1601 | -368 | 77 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1233 |  | 1601 | -368 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1450 |  | -2000 | -550 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1141 |  | 1600 | -459 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1141 |  | 1600 | -459 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1137 |  | 1601 | -464 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1137 |  | 1601 | -464 | 71 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1414 |  | -2000 | -586 | 71 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1402 |  | -2000 | -598 | 70 | []

## 0230Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3551
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1703 | 1836 | 1836 | -133 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1703 | 1836 | 1836 | -133 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 | 1836 | 1836 | -166 | 91 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1814 | -2000 | -2000 | -186 | 91 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1653 | 1836 | 1836 | -183 | 90 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1795 | -2000 | -2000 | -205 | 90 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1624 | 1836 | 1836 | -212 | 88 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1617 | 1836 | 1836 | -219 | 88 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1614 | 1836 | 1836 | -222 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 | 1836 | 1836 | -236 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1596 | 1836 | 1836 | -240 | 87 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1590 | 1836 | 1836 | -246 | 87 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1024 | -1248 | -1248 | -225 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1022 | -1248 | -1248 | -227 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1019 | -1248 | -1248 | -229 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1012 | -1248 | -1248 | -236 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1011 | -1248 | -1248 | -238 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1005 | -1248 | -1248 | -243 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1177 | 1600 | 1600 | -423 | 74 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1177 | 1600 | 1600 | -423 | 74 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1174 | 1601 | 1601 | -427 | 73 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1174 | 1601 | 1601 | -427 | 73 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1429 | -2000 | -2000 | -571 | 71 | []

## 0230Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3551
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1703 |  | 1836 | -133 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1703 |  | 1836 | -133 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 |  | 1836 | -166 | 91 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1814 |  | -2000 | -186 | 91 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1653 |  | 1836 | -183 | 90 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1795 |  | -2000 | -205 | 90 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1624 |  | 1836 | -212 | 88 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1617 |  | 1836 | -219 | 88 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1614 |  | 1836 | -222 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 |  | 1836 | -236 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1596 |  | 1836 | -240 | 87 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1590 |  | 1836 | -246 | 87 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1024 |  | -1248 | -225 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1022 |  | -1248 | -227 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1019 |  | -1248 | -229 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1012 |  | -1248 | -236 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1011 |  | -1248 | -238 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1005 |  | -1248 | -243 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1177 |  | 1600 | -423 | 74 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1177 |  | 1600 | -423 | 74 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1174 |  | 1601 | -427 | 73 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1174 |  | 1601 | -427 | 73 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1429 |  | -2000 | -571 | 71 | []

## 0330Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3549
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1681 | 1836 | 1836 | -155 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1681 | 1836 | 1836 | -155 | 92 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1830 | -2000 | -2000 | -170 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1804 | -2000 | -2000 | -196 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1646 | 1836 | 1836 | -190 | 90 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1642 | 1836 | 1836 | -194 | 89 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 | 1836 | 1836 | -233 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1595 | 1836 | 1836 | -241 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 | 1836 | 1836 | -245 | 87 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1581 | 1836 | 1836 | -255 | 86 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1580 | 1836 | 1836 | -256 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1567 | 1836 | 1836 | -269 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1034 | -1248 | -1248 | -215 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1032 | -1248 | -1248 | -217 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1029 | -1248 | -1248 | -219 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1022 | -1248 | -1248 | -226 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1021 | -1248 | -1248 | -227 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1016 | -1248 | -1248 | -233 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1182 | 1601 | 1601 | -419 | 74 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1182 | 1601 | 1601 | -419 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1441 | -2000 | -2000 | -559 | 72 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1402 | -2000 | -2000 | -598 | 70 | []

## 0330Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3549
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1681 |  | 1836 | -155 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1681 |  | 1836 | -155 | 92 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1830 |  | -2000 | -170 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1804 |  | -2000 | -196 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1646 |  | 1836 | -190 | 90 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1642 |  | 1836 | -194 | 89 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 |  | 1836 | -233 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1595 |  | 1836 | -241 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 |  | 1836 | -245 | 87 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1581 |  | 1836 | -255 | 86 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1580 |  | 1836 | -256 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1836 | -269 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1034 |  | -1248 | -215 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1032 |  | -1248 | -217 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1029 |  | -1248 | -219 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1022 |  | -1248 | -226 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1021 |  | -1248 | -227 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1016 |  | -1248 | -233 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1185 |  | 1600 | -415 | 74 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1185 |  | 1600 | -415 | 74 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1182 |  | 1601 | -419 | 74 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1182 |  | 1601 | -419 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1441 |  | -2000 | -559 | 72 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1402 |  | -2000 | -598 | 70 | []

## 0430Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3571
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1883 | -2000 | -2000 | -117 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1857 | -2000 | -2000 | -143 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1615 | 1836 | 1836 | -221 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1615 | 1836 | 1836 | -221 | 88 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1573 | 1836 | 1836 | -263 | 86 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1571 | 1836 | 1836 | -265 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1529 | 1836 | 1836 | -307 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1037 | -1248 | -1248 | -211 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1036 | -1248 | -1248 | -213 | 83 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1520 | 1836 | 1836 | -316 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1033 | -1248 | -1248 | -216 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1519 | 1836 | 1836 | -317 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1027 | -1248 | -1248 | -222 | 82 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1509 | 1836 | 1836 | -327 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1025 | -1248 | -1248 | -223 | 82 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1506 | 1836 | 1836 | -330 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1020 | -1248 | -1248 | -228 | 82 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1500 | 1836 | 1836 | -336 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1212 | 1601 | 1601 | -389 | 76 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1212 | 1601 | 1601 | -389 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1470 | -2000 | -2000 | -530 | 73 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1436 | -2000 | -2000 | -564 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1425 | -2000 | -2000 | -575 | 71 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1419 | -2000 | -2000 | -581 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1416 | -2000 | -2000 | -584 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1414 | 2000 | 2000 | -586 | 71 | []

## 0430Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3571
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1883 |  | -2000 | -117 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1857 |  | -2000 | -143 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1615 |  | 1836 | -221 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1615 |  | 1836 | -221 | 88 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1573 |  | 1836 | -263 | 86 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1571 |  | 1836 | -265 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1529 |  | 1836 | -307 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1037 |  | -1248 | -211 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1036 |  | -1248 | -213 | 83 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1520 |  | 1836 | -316 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1033 |  | -1248 | -216 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1519 |  | 1836 | -317 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1027 |  | -1248 | -222 | 82 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1509 |  | 1836 | -327 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1025 |  | -1248 | -223 | 82 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1506 |  | 1836 | -330 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1020 |  | -1248 | -228 | 82 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1500 |  | 1836 | -336 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1215 |  | 1600 | -385 | 76 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1215 |  | 1600 | -385 | 76 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1212 |  | 1601 | -389 | 76 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1212 |  | 1601 | -389 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1470 |  | -2000 | -530 | 73 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1436 |  | -2000 | -564 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1425 |  | -2000 | -575 | 71 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1419 |  | -2000 | -581 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1416 |  | -2000 | -584 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1414 |  | 2000 | -586 | 71 | []

## 0530Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3601
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1952 | -2000 | -2000 | -48 | 98 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1918 | -2000 | -2000 | -82 | 96 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1097 | -1248 | -1248 | -151 | 88 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1096 | -1248 | -1248 | -153 | 88 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1092 | -1248 | -1248 | -156 | 88 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1087 | -1248 | -1248 | -162 | 87 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1084 | -1248 | -1248 | -164 | 87 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1080 | -1248 | -1248 | -169 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 | 1836 | 1836 | -276 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 | 1836 | 1836 | -276 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1298 | 1600 | 1600 | -302 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1298 | 1600 | 1600 | -302 | 81 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1295 | 1601 | 1601 | -306 | 81 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1295 | 1601 | 1601 | -306 | 81 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1478 | 1836 | 1836 | -358 | 80 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1478 | 1836 | 1836 | -358 | 80 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1462 | 1836 | 1836 | -374 | 80 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1448 | 1836 | 1836 | -388 | 79 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1442 | 1836 | 1836 | -394 | 79 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1436 | 1836 | 1836 | -400 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1427 | 1836 | 1836 | -409 | 78 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1396 | 1836 | 1836 | -440 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1504 | -2000 | -2000 | -496 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1478 | -2000 | -2000 | -522 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1477 | 2000 | 2000 | -523 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1469 | -2000 | -2000 | -531 | 73 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1463 | -2000 | -2000 | -537 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1459 | -2000 | -2000 | -541 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1144 | 1600 | 1600 | -456 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1144 | 1600 | 1600 | -456 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1141 | 1601 | 1601 | -460 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1141 | 1601 | 1601 | -460 | 71 | []

## 0530Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3601
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1952 |  | -2000 | -48 | 98 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1918 |  | -2000 | -82 | 96 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1097 |  | -1248 | -151 | 88 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1096 |  | -1248 | -153 | 88 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1092 |  | -1248 | -156 | 88 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1087 |  | -1248 | -162 | 87 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1084 |  | -1248 | -164 | 87 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1080 |  | -1248 | -169 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 |  | 1836 | -276 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 |  | 1836 | -276 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1298 |  | 1600 | -302 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1298 |  | 1600 | -302 | 81 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1295 |  | 1601 | -306 | 81 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1295 |  | 1601 | -306 | 81 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1478 |  | 1836 | -358 | 80 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1478 |  | 1836 | -358 | 80 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1462 |  | 1836 | -374 | 80 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1448 |  | 1836 | -388 | 79 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1442 |  | 1836 | -394 | 79 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1436 |  | 1836 | -400 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1836 | -409 | 78 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1396 |  | 1836 | -440 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1504 |  | -2000 | -496 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1478 |  | -2000 | -522 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1477 |  | 2000 | -523 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1469 |  | -2000 | -531 | 73 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1463 |  | -2000 | -537 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1459 |  | -2000 | -541 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1144 |  | 1600 | -456 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1144 |  | 1600 | -456 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1141 |  | 1601 | -460 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1141 |  | 1601 | -460 | 71 | []

## 0630Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3569
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1922 | -2000 | -2000 | -78 | 96 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1896 | -2000 | -2000 | -104 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1367 | 1600 | 1600 | -233 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1367 | 1600 | 1600 | -233 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1364 | 1601 | 1601 | -237 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1364 | 1601 | 1601 | -237 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1057 | -1248 | -1248 | -191 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1057 | -1248 | -1248 | -192 | 85 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1053 | -1248 | -1248 | -196 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1048 | -1248 | -1248 | -200 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1046 | -1248 | -1248 | -203 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1042 | -1248 | -1248 | -207 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1475 | 1836 | 1836 | -361 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1475 | 1836 | 1836 | -361 | 80 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1408 | 1836 | 1836 | -428 | 77 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1403 | 1836 | 1836 | -433 | 76 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1395 | 1836 | 1836 | -441 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1510 | -2000 | -2000 | -490 | 75 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1372 | 1836 | 1836 | -464 | 75 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1368 | 1836 | 1836 | -468 | 74 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1360 | 1836 | 1836 | -476 | 74 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1469 | -2000 | -2000 | -531 | 73 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1345 | 1836 | 1836 | -491 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1163 | 1601 | 1601 | -438 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1163 | 1601 | 1601 | -438 | 73 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1451 | -2000 | -2000 | -549 | 73 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1450 | -2000 | -2000 | -550 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1440 | 2000 | 2000 | -560 | 72 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1440 | -2000 | -2000 | -560 | 72 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1313 | 1836 | 1836 | -523 | 72 | []

## 0630Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3569
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1922 |  | -2000 | -78 | 96 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1896 |  | -2000 | -104 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1367 |  | 1600 | -233 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1367 |  | 1600 | -233 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1364 |  | 1601 | -237 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1364 |  | 1601 | -237 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1057 |  | -1248 | -191 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1057 |  | -1248 | -192 | 85 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1053 |  | -1248 | -196 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1048 |  | -1248 | -200 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1046 |  | -1248 | -203 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1042 |  | -1248 | -207 | 83 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1475 |  | 1836 | -361 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1475 |  | 1836 | -361 | 80 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1408 |  | 1836 | -428 | 77 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1403 |  | 1836 | -433 | 76 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1395 |  | 1836 | -441 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1510 |  | -2000 | -490 | 75 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1372 |  | 1836 | -464 | 75 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1368 |  | 1836 | -468 | 74 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1360 |  | 1836 | -476 | 74 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1469 |  | -2000 | -531 | 73 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1345 |  | 1836 | -491 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1166 |  | 1600 | -434 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1166 |  | 1600 | -434 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1163 |  | 1601 | -438 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1163 |  | 1601 | -438 | 73 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1451 |  | -2000 | -549 | 73 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1450 |  | -2000 | -550 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1440 |  | 2000 | -560 | 72 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1440 |  | -2000 | -560 | 72 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1313 |  | 1836 | -523 | 72 | []

## 0730Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3095
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 | 1601 | 1601 | -13 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1756 | 1836 | 1836 | -80 | 96 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1821 | -2000 | -2000 | -179 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1777 | -2000 | -2000 | -223 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1435 | 1836 | 1836 | -401 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 | 1836 | 1836 | -405 | 78 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 | 1836 | 1836 | -412 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -951 | -1248 | -1248 | -298 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -950 | -1248 | -1248 | -299 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -946 | -1248 | -1248 | -302 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -942 | -1248 | -1248 | -307 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -939 | -1248 | -1248 | -309 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -936 | -1248 | -1248 | -313 | 75 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1355 | 1836 | 1836 | -481 | 74 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1347 | 1836 | 1836 | -489 | 73 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1327 | 1836 | 1836 | -509 | 72 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1446 | -2000 | -2000 | -554 | 72 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1327 | 1836 | 1836 | -509 | 72 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1314 | 1836 | 1836 | -522 | 72 | []

## 0730Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3095
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 |  | 1600 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1588 |  | 1601 | -13 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1756 |  | 1836 | -80 | 96 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1821 |  | -2000 | -179 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1777 |  | -2000 | -223 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1836 | -401 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 |  | 1836 | -405 | 78 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 |  | 1836 | -412 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -951 |  | -1248 | -298 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -950 |  | -1248 | -299 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -946 |  | -1248 | -302 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -942 |  | -1248 | -307 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -939 |  | -1248 | -309 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -936 |  | -1248 | -313 | 75 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1355 |  | 1836 | -481 | 74 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1347 |  | 1836 | -489 | 73 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1327 |  | 1836 | -509 | 72 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1446 |  | -2000 | -554 | 72 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1327 |  | 1836 | -509 | 72 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1314 |  | 1836 | -522 | 72 | []

## 0830Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2965
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 | 1836 | 1836 | -2 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -952 | -999 | -999 | -47 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 | 1836 | 1836 | -111 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 | 1836 | 1836 | -166 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1661 | 1836 | 1836 | -175 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1408 | 1600 | 1600 | -192 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1404 | 1601 | 1601 | -197 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1585 | 1836 | 1836 | -251 | 86 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1574 | 1836 | 1836 | -262 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1557 | 1836 | 1836 | -279 | 85 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 | 1836 | 1836 | -309 | 83 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1652 | -2000 | -2000 | -348 | 83 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1508 | 1836 | 1836 | -328 | 82 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1593 | -2000 | -2000 | -407 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -885 | -1248 | -1248 | -363 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -883 | -1248 | -1248 | -365 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -881 | -1248 | -1248 | -368 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -875 | -1248 | -1248 | -374 | 70 | []

## 0830Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2965
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 |  | 1836 | -2 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -952 |  | -999 | -47 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 |  | 1836 | -111 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 |  | 1836 | -166 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1661 |  | 1836 | -175 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1408 |  | 1600 | -192 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1404 |  | 1601 | -197 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1585 |  | 1836 | -251 | 86 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1574 |  | 1836 | -262 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1557 |  | 1836 | -279 | 85 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 |  | 1836 | -309 | 83 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1652 |  | -2000 | -348 | 83 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1508 |  | 1836 | -328 | 82 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1593 |  | -2000 | -407 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -885 |  | -1248 | -363 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -883 |  | -1248 | -365 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -881 |  | -1248 | -368 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -875 |  | -1248 | -374 | 70 | []

## 0930Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2836
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -997 | -999 | -999 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1790 | 1836 | 1836 | -46 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 | 1836 | 1836 | -101 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1701 | 1836 | 1836 | -135 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1693 | 1836 | 1836 | -143 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1597 | 1836 | 1836 | -239 | 87 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1587 | 1836 | 1836 | -249 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 | 1836 | 1836 | -276 | 85 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1530 | 1836 | 1836 | -306 | 83 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1516 | 1836 | 1836 | -320 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1285 | 1601 | 1601 | -316 | 80 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1591 | -2000 | -2000 | -409 | 80 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1534 | -2000 | -2000 | -466 | 77 | []

## 0930Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2836
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -997 |  | -999 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1790 |  | 1836 | -46 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 |  | 1836 | -101 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1701 |  | 1836 | -135 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1693 |  | 1836 | -143 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1597 |  | 1836 | -239 | 87 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1587 |  | 1836 | -249 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 |  | 1836 | -276 | 85 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1530 |  | 1836 | -306 | 83 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1516 |  | 1836 | -320 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1290 |  | 1600 | -310 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1285 |  | 1601 | -316 | 80 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1591 |  | -2000 | -409 | 80 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1534 |  | -2000 | -466 | 77 | []

## 1030Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2825
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 | 1836 | 1836 | -1 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -995 | -999 | -999 | -5 | 100 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1778 | 1836 | 1836 | -58 | 97 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 | 1836 | 1836 | -79 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1750 | 1836 | 1836 | -86 | 95 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1647 | 1836 | 1836 | -189 | 90 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1641 | 1836 | 1836 | -195 | 89 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1612 | 1836 | 1836 | -224 | 88 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1584 | 1836 | 1836 | -252 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1572 | 1836 | 1836 | -264 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1285 | 1601 | 1601 | -316 | 80 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1552 | -2000 | -2000 | -448 | 78 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1494 | -2000 | -2000 | -506 | 75 | []

## 1030Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2825
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 |  | 1836 | -1 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -995 |  | -999 | -5 | 100 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1778 |  | 1836 | -58 | 97 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 |  | 1836 | -79 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1750 |  | 1836 | -86 | 95 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1647 |  | 1836 | -189 | 90 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1641 |  | 1836 | -195 | 89 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1612 |  | 1836 | -224 | 88 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1584 |  | 1836 | -252 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1572 |  | 1836 | -264 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1290 |  | 1600 | -310 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1285 |  | 1601 | -316 | 80 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1552 |  | -2000 | -448 | 78 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1494 |  | -2000 | -506 | 75 | []

## 1130Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2781
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 | 1836 | 1836 | -11 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1776 | 1836 | 1836 | -60 | 97 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1775 | 1836 | 1836 | -61 | 97 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1761 | 1836 | 1836 | -75 | 96 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -946 | -999 | -999 | -54 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1652 | 1836 | 1836 | -184 | 90 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1648 | 1836 | 1836 | -188 | 90 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1625 | 1836 | 1836 | -211 | 89 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 | 1836 | 1836 | -236 | 87 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1587 | 1836 | 1836 | -249 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1231 | 1601 | 1601 | -370 | 77 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1522 | -2000 | -2000 | -478 | 76 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1459 | 2000 | 2000 | -541 | 73 | []

## 1130Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2781
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 |  | 1836 | -11 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1776 |  | 1836 | -60 | 97 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1775 |  | 1836 | -61 | 97 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1761 |  | 1836 | -75 | 96 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -946 |  | -999 | -54 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1652 |  | 1836 | -184 | 90 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1648 |  | 1836 | -188 | 90 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1625 |  | 1836 | -211 | 89 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 |  | 1836 | -236 | 87 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1587 |  | 1836 | -249 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1236 |  | 1600 | -364 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1231 |  | 1601 | -370 | 77 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1522 |  | -2000 | -478 | 76 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1459 |  | 2000 | -541 | 73 | []

## 1230Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2852
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 | 1836 | 1836 | -11 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1752 | 1836 | 1836 | -84 | 95 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1747 | 1836 | 1836 | -89 | 95 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 | 1836 | 1836 | -101 | 94 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -936 | -999 | -999 | -64 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1633 | 1836 | 1836 | -203 | 89 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 | 1836 | 1836 | -209 | 89 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1605 | 1836 | 1836 | -231 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1582 | 1836 | 1836 | -254 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1836 | 1836 | -267 | 85 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1592 | -2000 | -2000 | -408 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1266 | 1601 | 1601 | -335 | 79 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1524 | -2000 | -2000 | -476 | 76 | []

## 1230Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2852
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 |  | 1836 | -11 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1752 |  | 1836 | -84 | 95 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1747 |  | 1836 | -89 | 95 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 |  | 1836 | -101 | 94 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -936 |  | -999 | -64 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1633 |  | 1836 | -203 | 89 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 |  | 1836 | -209 | 89 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1605 |  | 1836 | -231 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1582 |  | 1836 | -254 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1836 | -267 | 85 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1592 |  | -2000 | -408 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1271 |  | 1600 | -329 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1266 |  | 1601 | -335 | 79 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1524 |  | -2000 | -476 | 76 | []

## 1330Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2907
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 | 1836 | 1836 | -11 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1712 | 1836 | 1836 | -124 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1712 | 1836 | 1836 | -124 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1699 | 1836 | 1836 | -137 | 93 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -907 | -999 | -999 | -92 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 | 1836 | 1836 | -233 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1597 | 1836 | 1836 | -239 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1575 | 1836 | 1836 | -261 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1553 | 1836 | 1836 | -283 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1541 | 1836 | 1836 | -295 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1325 | 1600 | 1600 | -275 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1320 | 1601 | 1601 | -281 | 82 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1627 | -2000 | -2000 | -373 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1559 | -2000 | -2000 | -441 | 78 | []

## 1330Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2907
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 |  | 1836 | -11 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1712 |  | 1836 | -124 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1712 |  | 1836 | -124 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1699 |  | 1836 | -137 | 93 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -907 |  | -999 | -92 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 |  | 1836 | -233 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1597 |  | 1836 | -239 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1575 |  | 1836 | -261 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1553 |  | 1836 | -283 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1541 |  | 1836 | -295 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1325 |  | 1600 | -275 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1320 |  | 1601 | -281 | 82 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1627 |  | -2000 | -373 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1559 |  | -2000 | -441 | 78 | []

## 1430Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3097
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 | 1836 | 1836 | -2 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1471 | 1600 | 1600 | -129 | 92 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1467 | 1601 | 1601 | -134 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1631 | 1836 | 1836 | -205 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 | 1836 | 1836 | -209 | 89 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1770 | -2000 | -2000 | -230 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1619 | 1836 | 1836 | -217 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -852 | -999 | -999 | -147 | 85 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1689 | -2000 | -2000 | -311 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1530 | 1836 | 1836 | -306 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 | 1836 | 1836 | -309 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1505 | 1836 | 1836 | -331 | 82 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1482 | 1836 | 1836 | -354 | 81 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1473 | 1836 | 1836 | -363 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -881 | -1248 | -1248 | -367 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -880 | -1248 | -1248 | -369 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -877 | -1248 | -1248 | -371 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3097
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 |  | 1836 | -2 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1471 |  | 1600 | -129 | 92 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1467 |  | 1601 | -134 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1631 |  | 1836 | -205 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 |  | 1836 | -209 | 89 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1770 |  | -2000 | -230 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1619 |  | 1836 | -217 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -852 |  | -999 | -147 | 85 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1689 |  | -2000 | -311 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1530 |  | 1836 | -306 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 |  | 1836 | -309 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1505 |  | 1836 | -331 | 82 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1482 |  | 1836 | -354 | 81 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1473 |  | 1836 | -363 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -881 |  | -1248 | -367 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -880 |  | -1248 | -369 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -877 |  | -1248 | -371 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3246
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1594 | 1601 | 1601 | -7 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1816 | 1836 | 1836 | -20 | 99 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1901 | -2000 | -2000 | -99 | 95 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1820 | -2000 | -2000 | -180 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1518 | 1836 | 1836 | -318 | 83 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1510 | 1836 | 1836 | -326 | 82 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1506 | 1836 | 1836 | -330 | 82 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1433 | 1836 | 1836 | -403 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 | 1836 | 1836 | -405 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -776 | -999 | -999 | -223 | 78 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1411 | 1836 | 1836 | -425 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1391 | 1836 | 1836 | -445 | 76 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1383 | 1836 | 1836 | -453 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1488 | -2000 | -2000 | -512 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -912 | -1248 | -1248 | -336 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -911 | -1248 | -1248 | -337 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -908 | -1248 | -1248 | -340 | 73 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1449 | -2000 | -2000 | -551 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -904 | -1248 | -1248 | -345 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1447 | -2000 | -2000 | -553 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -901 | -1248 | -1248 | -347 | 72 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1442 | -2000 | -2000 | -558 | 72 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1438 | -2000 | -2000 | -562 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1438 | 2000 | 2000 | -562 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -897 | -1248 | -1248 | -351 | 72 | []

## 1530Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3246
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1598 |  | 1600 | -2 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1594 |  | 1601 | -7 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1816 |  | 1836 | -20 | 99 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1901 |  | -2000 | -99 | 95 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1820 |  | -2000 | -180 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1518 |  | 1836 | -318 | 83 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1510 |  | 1836 | -326 | 82 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1506 |  | 1836 | -330 | 82 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1433 |  | 1836 | -403 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 |  | 1836 | -405 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -776 |  | -999 | -223 | 78 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1411 |  | 1836 | -425 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1391 |  | 1836 | -445 | 76 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1383 |  | 1836 | -453 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1488 |  | -2000 | -512 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -912 |  | -1248 | -336 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -911 |  | -1248 | -337 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -908 |  | -1248 | -340 | 73 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1449 |  | -2000 | -551 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -904 |  | -1248 | -345 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1447 |  | -2000 | -553 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -901 |  | -1248 | -347 | 72 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1442 |  | -2000 | -558 | 72 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1438 |  | -2000 | -562 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1438 |  | 2000 | -562 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -897 |  | -1248 | -351 | 72 | []

## 1630Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3143
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 | 1601 | 1601 | -8 | 100 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1981 | -2000 | -2000 | -19 | 99 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1897 | -2000 | -2000 | -103 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 | 1836 | 1836 | -233 | 87 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1536 | -2000 | -2000 | -464 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1507 | 2000 | 2000 | -493 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1502 | -2000 | -2000 | -498 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1498 | -2000 | -2000 | -502 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -933 | -1248 | -1248 | -315 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -933 | -1248 | -1248 | -315 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1495 | -2000 | -2000 | -505 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -929 | -1248 | -1248 | -319 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1488 | -2000 | -2000 | -512 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -927 | -1248 | -1248 | -322 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -923 | -1248 | -1248 | -326 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -920 | -1248 | -1248 | -328 | 74 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1128 | 1600 | 1600 | -472 | 70 | []
BC | Base Case | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1123 | 1601 | 1601 | -478 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3143
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 |  | 1600 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1593 |  | 1601 | -8 | 100 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1981 |  | -2000 | -19 | 99 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1897 |  | -2000 | -103 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 |  | 1836 | -233 | 87 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1536 |  | -2000 | -464 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1507 |  | 2000 | -493 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1502 |  | -2000 | -498 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1498 |  | -2000 | -502 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -933 |  | -1248 | -315 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -933 |  | -1248 | -315 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1495 |  | -2000 | -505 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -929 |  | -1248 | -319 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1488 |  | -2000 | -512 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -927 |  | -1248 | -322 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -923 |  | -1248 | -326 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -920 |  | -1248 | -328 | 74 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1128 |  | 1600 | -472 | 70 | []
BC | Base Case | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1123 |  | 1601 | -478 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3058
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1987 | -2000 | -2000 | -13 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 | 1601 | 1601 | -12 | 99 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1903 | -2000 | -2000 | -97 | 95 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1403 | 1836 | 1836 | -433 | 76 | []
BC | Base Case | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1224 | 1601 | 1601 | -377 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1523 | 2000 | 2000 | -477 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1523 | -2000 | -2000 | -477 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1497 | -2000 | -2000 | -503 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1495 | -2000 | -2000 | -505 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1493 | -2000 | -2000 | -507 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1483 | -2000 | -2000 | -517 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -913 | -1248 | -1248 | -335 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -912 | -1248 | -1248 | -336 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -908 | -1248 | -1248 | -340 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -908 | -1248 | -1248 | -341 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -902 | -1248 | -1248 | -346 | 72 | []

## 1730Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3058
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1593 |  | 1600 | -7 | 100 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1987 |  | -2000 | -13 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1589 |  | 1601 | -12 | 99 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1903 |  | -2000 | -97 | 95 | []
BC | Base Case | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1228 |  | 1600 | -372 | 77 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1403 |  | 1836 | -433 | 76 | []
BC | Base Case | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1224 |  | 1601 | -377 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1523 |  | 2000 | -477 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1523 |  | -2000 | -477 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1497 |  | -2000 | -503 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1495 |  | -2000 | -505 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1493 |  | -2000 | -507 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1483 |  | -2000 | -517 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -913 |  | -1248 | -335 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -912 |  | -1248 | -336 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -908 |  | -1248 | -340 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -908 |  | -1248 | -341 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -902 |  | -1248 | -346 | 72 | []

## 1830Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3350
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1992 | -2000 | -2000 | -8 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1912 | -2000 | -2000 | -88 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1283 | 1600 | 1600 | -317 | 80 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1283 | 1600 | 1600 | -317 | 80 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1278 | 1601 | 1601 | -323 | 80 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1278 | 1601 | 1601 | -323 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -949 | -1248 | -1248 | -299 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -949 | -1248 | -1248 | -300 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1519 | -2000 | -2000 | -481 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1517 | 2000 | 2000 | -483 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -944 | -1248 | -1248 | -304 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -944 | -1248 | -1248 | -305 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1505 | -2000 | -2000 | -495 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -939 | -1248 | -1248 | -309 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -937 | -1248 | -1248 | -311 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1501 | -2000 | -2000 | -499 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1499 | -2000 | -2000 | -501 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1493 | -2000 | -2000 | -507 | 75 | []

## 1830Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3350
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1992 |  | -2000 | -8 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1912 |  | -2000 | -88 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1283 |  | 1600 | -317 | 80 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1283 |  | 1600 | -317 | 80 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1278 |  | 1601 | -323 | 80 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1278 |  | 1601 | -323 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -949 |  | -1248 | -299 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -949 |  | -1248 | -300 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1519 |  | -2000 | -481 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1517 |  | 2000 | -483 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -944 |  | -1248 | -304 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -944 |  | -1248 | -305 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1505 |  | -2000 | -495 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -939 |  | -1248 | -309 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -937 |  | -1248 | -311 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1501 |  | -2000 | -499 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1499 |  | -2000 | -501 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1493 |  | -2000 | -507 | 75 | []

## 1930Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3380
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1993 | -2000 | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1915 | -2000 | -2000 | -85 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1314 | 1600 | 1600 | -286 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1314 | 1600 | 1600 | -286 | 82 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1309 | 1601 | 1601 | -292 | 82 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1309 | 1601 | 1601 | -292 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -950 | -1248 | -1248 | -298 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1522 | -2000 | -2000 | -478 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -949 | -1248 | -1248 | -299 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1516 | 2000 | 2000 | -484 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -945 | -1248 | -1248 | -304 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -944 | -1248 | -1248 | -304 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1506 | -2000 | -2000 | -494 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -940 | -1248 | -1248 | -309 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1503 | -2000 | -2000 | -497 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -938 | -1248 | -1248 | -311 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1500 | -2000 | -2000 | -500 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1495 | -2000 | -2000 | -505 | 75 | []

## 1930Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3380
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1993 |  | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1915 |  | -2000 | -85 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1314 |  | 1600 | -286 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1314 |  | 1600 | -286 | 82 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1309 |  | 1601 | -292 | 82 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1309 |  | 1601 | -292 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -950 |  | -1248 | -298 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1522 |  | -2000 | -478 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -949 |  | -1248 | -299 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1516 |  | 2000 | -484 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -945 |  | -1248 | -304 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -944 |  | -1248 | -304 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1506 |  | -2000 | -494 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -940 |  | -1248 | -309 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1503 |  | -2000 | -497 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -938 |  | -1248 | -311 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1500 |  | -2000 | -500 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1495 |  | -2000 | -505 | 75 | []

## 2030Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3355
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1996 | -2000 | -2000 | -4 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1924 | -2000 | -2000 | -76 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1352 | 1600 | 1600 | -248 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1352 | 1600 | 1600 | -248 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1347 | 1601 | 1601 | -254 | 84 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1347 | 1601 | 1601 | -254 | 84 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1523 | -2000 | -2000 | -477 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1519 | 2000 | 2000 | -481 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -944 | -1248 | -1248 | -304 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -943 | -1248 | -1248 | -306 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1504 | -2000 | -2000 | -496 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -939 | -1248 | -1248 | -310 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -939 | -1248 | -1248 | -310 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1501 | -2000 | -2000 | -499 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1498 | -2000 | -2000 | -502 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -934 | -1248 | -1248 | -315 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -933 | -1248 | -1248 | -316 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1488 | -2000 | -2000 | -512 | 74 | []

## 2030Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3355
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1996 |  | -2000 | -4 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1924 |  | -2000 | -76 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1352 |  | 1600 | -248 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1352 |  | 1600 | -248 | 85 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1347 |  | 1601 | -254 | 84 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1347 |  | 1601 | -254 | 84 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1523 |  | -2000 | -477 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1519 |  | 2000 | -481 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -944 |  | -1248 | -304 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -943 |  | -1248 | -306 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1504 |  | -2000 | -496 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -939 |  | -1248 | -310 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -939 |  | -1248 | -310 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1501 |  | -2000 | -499 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1498 |  | -2000 | -502 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -934 |  | -1248 | -315 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -933 |  | -1248 | -316 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1488 |  | -2000 | -512 | 74 | []

## 2130Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3339
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1992 | -2000 | -2000 | -8 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1919 | -2000 | -2000 | -81 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1365 | 1601 | 1601 | -236 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1365 | 1601 | 1601 | -236 | 85 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1521 | 2000 | 2000 | -479 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1511 | -2000 | -2000 | -489 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -941 | -1248 | -1248 | -307 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -940 | -1248 | -1248 | -309 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -936 | -1248 | -1248 | -312 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -935 | -1248 | -1248 | -313 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1497 | -2000 | -2000 | -503 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1496 | -2000 | -2000 | -504 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1492 | -2000 | -2000 | -508 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -931 | -1248 | -1248 | -318 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -930 | -1248 | -1248 | -319 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1484 | -2000 | -2000 | -516 | 74 | []

## 2130Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3339
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1992 |  | -2000 | -8 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1919 |  | -2000 | -81 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1370 |  | 1600 | -230 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1370 |  | 1600 | -230 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1365 |  | 1601 | -236 | 85 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1365 |  | 1601 | -236 | 85 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1521 |  | 2000 | -479 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1511 |  | -2000 | -489 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -941 |  | -1248 | -307 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -940 |  | -1248 | -309 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -936 |  | -1248 | -312 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -935 |  | -1248 | -313 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1497 |  | -2000 | -503 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1496 |  | -2000 | -504 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1492 |  | -2000 | -508 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -931 |  | -1248 | -318 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -930 |  | -1248 | -319 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1484 |  | -2000 | -516 | 74 | []

## 2230Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3528
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1993 | -2000 | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1934 | -2000 | -2000 | -66 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1464 | 1600 | 1600 | -136 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1464 | 1600 | 1600 | -136 | 91 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1459 | 1601 | 1601 | -142 | 91 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1459 | 1601 | 1601 | -142 | 91 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 | -1248 | -1248 | -273 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -975 | -1248 | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -971 | -1248 | -1248 | -278 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -970 | -1248 | -1248 | -278 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -965 | -1248 | -1248 | -283 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -964 | -1248 | -1248 | -285 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1519 | -2000 | -2000 | -481 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1517 | 2000 | 2000 | -483 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1502 | -2000 | -2000 | -498 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1497 | -2000 | -2000 | -503 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1492 | -2000 | -2000 | -508 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1485 | -2000 | -2000 | -515 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1142 | 1600 | 1600 | -458 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1142 | 1600 | 1600 | -458 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1137 | 1601 | 1601 | -464 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1137 | 1601 | 1601 | -464 | 71 | []

## 2230Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3528
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1993 |  | -2000 | -7 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1934 |  | -2000 | -66 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1464 |  | 1600 | -136 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1464 |  | 1600 | -136 | 91 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1459 |  | 1601 | -142 | 91 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1459 |  | 1601 | -142 | 91 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 |  | -1248 | -273 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -975 |  | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -971 |  | -1248 | -278 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -970 |  | -1248 | -278 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -965 |  | -1248 | -283 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -964 |  | -1248 | -285 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1519 |  | -2000 | -481 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1517 |  | 2000 | -483 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1502 |  | -2000 | -498 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1497 |  | -2000 | -503 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1492 |  | -2000 | -508 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1485 |  | -2000 | -515 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1142 |  | 1600 | -458 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1142 |  | 1600 | -458 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1137 |  | 1601 | -464 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1137 |  | 1601 | -464 | 71 | []

## 2330Preventive
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3628
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1995 | -2000 | -2000 | -5 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1927 | -2000 | -2000 | -73 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1376 | 1600 | 1600 | -224 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1376 | 1600 | 1600 | -224 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1373 | 1601 | 1601 | -228 | 86 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1373 | 1601 | 1601 | -228 | 86 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1042 | -1248 | -1248 | -206 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1041 | -1248 | -1248 | -207 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1038 | -1248 | -1248 | -211 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1033 | -1248 | -1248 | -215 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1030 | -1248 | -1248 | -218 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1026 | -1248 | -1248 | -222 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 | 1836 | 1836 | -376 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 | 1836 | 1836 | -376 | 80 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1398 | 1836 | 1836 | -438 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1519 | -2000 | -2000 | -481 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1519 | 2000 | 2000 | -481 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1503 | -2000 | -2000 | -497 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1500 | -2000 | -2000 | -500 | 75 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1376 | 1836 | 1836 | -460 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1493 | -2000 | -2000 | -507 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1489 | -2000 | -2000 | -511 | 74 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1358 | 1836 | 1836 | -478 | 74 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1342 | 1836 | 1836 | -494 | 73 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1337 | 1836 | 1836 | -499 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1160 | 1601 | 1601 | -441 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1160 | 1601 | 1601 | -441 | 72 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1330 | 1836 | 1836 | -506 | 72 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1310 | 1836 | 1836 | -526 | 71 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1288 | 1836 | 1836 | -548 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2024-03-05 21:16
Business day: | 07.03.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3628
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00011 | PRA 400 kV Tantareni-Kozlodui 1 ON_2 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1995 |  | -2000 | -5 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1927 |  | -2000 | -73 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1376 |  | 1600 | -224 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1376 |  | 1600 | -224 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1373 |  | 1601 | -228 | 86 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1373 |  | 1601 | -228 | 86 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1042 |  | -1248 | -206 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1041 |  | -1248 | -207 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1038 |  | -1248 | -211 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1033 |  | -1248 | -215 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1030 |  | -1248 | -218 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1026 |  | -1248 | -222 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 |  | 1836 | -376 | 80 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 |  | 1836 | -376 | 80 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1398 |  | 1836 | -438 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1519 |  | -2000 | -481 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1519 |  | 2000 | -481 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1503 |  | -2000 | -497 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1500 |  | -2000 | -500 | 75 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1376 |  | 1836 | -460 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1493 |  | -2000 | -507 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1489 |  | -2000 | -511 | 74 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1358 |  | 1836 | -478 | 74 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1342 |  | 1836 | -494 | 73 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1337 |  | 1836 | -499 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1164 |  | 1600 | -436 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1164 |  | 1600 | -436 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1160 |  | 1601 | -441 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1160 |  | 1601 | -441 | 72 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1330 |  | 1836 | -506 | 72 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1310 |  | 1836 | -526 | 71 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1288 |  | 1836 | -548 | 70 | []