## 0030Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3305
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1995 | -2000 | -2000 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1805 | 1836 | 1836 | -31 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1800 | 1836 | 1836 | -36 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 | 1836 | 1836 | -166 | 91 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 | 1836 | 1836 | -166 | 91 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1668 | 1836 | 1836 | -168 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1662 | 1836 | 1836 | -174 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1643 | 1836 | 1836 | -193 | 89 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1635 | 1836 | 1836 | -201 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 | 1836 | 1836 | -202 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1768 | 2000 | 2000 | -232 | 88 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1604 | 1836 | 1836 | -232 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1565 | -2000 | -2000 | -435 | 78 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1560 | -2000 | -2000 | -440 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1533 | -2000 | -2000 | -467 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1531 | -2000 | -2000 | -469 | 77 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1494 | -2000 | -2000 | -506 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1486 | -2000 | -2000 | -514 | 74 | []

## 0030Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3305
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1995 |  | -2000 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1805 |  | 1836 | -31 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1800 |  | 1836 | -36 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 |  | 1836 | -166 | 91 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 |  | 1836 | -166 | 91 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1668 |  | 1836 | -168 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1662 |  | 1836 | -174 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1643 |  | 1836 | -193 | 89 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1635 |  | 1836 | -201 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 |  | 1836 | -202 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1768 |  | 2000 | -232 | 88 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1604 |  | 1836 | -232 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1565 |  | -2000 | -435 | 78 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1560 |  | -2000 | -440 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1533 |  | -2000 | -467 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1531 |  | -2000 | -469 | 77 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1494 |  | -2000 | -506 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1486 |  | -2000 | -514 | 74 | []

## 0130Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3303
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -995 | -999 | -999 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1829 | 1836 | 1836 | -7 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 | 1836 | 1836 | -11 | 99 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1947 | -2000 | -2000 | -53 | 97 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 | 1836 | 1836 | -151 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1679 | 1836 | 1836 | -157 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1679 | 1836 | 1836 | -157 | 91 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 | 1836 | 1836 | -158 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 | 1836 | 1836 | -158 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 | 1836 | 1836 | -177 | 90 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1648 | 1836 | 1836 | -188 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1616 | 1836 | 1836 | -220 | 88 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1727 | 2000 | 2000 | -273 | 86 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1533 | -2000 | -2000 | -467 | 77 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1528 | -2000 | -2000 | -472 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1497 | -2000 | -2000 | -503 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1494 | -2000 | -2000 | -506 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1460 | 2000 | 2000 | -540 | 73 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1452 | 2000 | 2000 | -548 | 73 | []

## 0130Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3303
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -995 |  | -999 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1829 |  | 1836 | -7 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 |  | 1836 | -11 | 99 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1947 |  | -2000 | -53 | 97 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 |  | 1836 | -151 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1679 |  | 1836 | -157 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1679 |  | 1836 | -157 | 91 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 |  | 1836 | -158 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 |  | 1836 | -158 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 |  | 1836 | -177 | 90 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1648 |  | 1836 | -188 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1616 |  | 1836 | -220 | 88 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1727 |  | 2000 | -273 | 86 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1533 |  | -2000 | -467 | 77 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1528 |  | -2000 | -472 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1497 |  | -2000 | -503 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1494 |  | -2000 | -506 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1460 |  | 2000 | -540 | 73 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1452 |  | 2000 | -548 | 73 | []

## 0230Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3255
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 | 1836 | 1836 | -5 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1822 | 1836 | 1836 | -14 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -971 | -999 | -999 | -29 | 97 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1899 | -2000 | -2000 | -101 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 | 1836 | 1836 | -136 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 | 1836 | 1836 | -138 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1693 | 1836 | 1836 | -143 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1693 | 1836 | 1836 | -143 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1688 | 1836 | 1836 | -148 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1675 | 1836 | 1836 | -161 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 | 1836 | 1836 | -173 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 | 1836 | 1836 | -202 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1682 | 2000 | 2000 | -318 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1497 | -2000 | -2000 | -503 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1491 | -2000 | -2000 | -509 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1461 | -2000 | -2000 | -539 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1459 | -2000 | -2000 | -541 | 73 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1423 | 2000 | 2000 | -577 | 71 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1413 | 2000 | 2000 | -587 | 71 | []

## 0230Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3255
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 |  | 1836 | -5 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1822 |  | 1836 | -14 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -971 |  | -999 | -29 | 97 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1899 |  | -2000 | -101 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 |  | 1836 | -136 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 |  | 1836 | -138 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1693 |  | 1836 | -143 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1693 |  | 1836 | -143 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1688 |  | 1836 | -148 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1675 |  | 1836 | -161 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 |  | 1836 | -173 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 |  | 1836 | -202 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1682 |  | 2000 | -318 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1497 |  | -2000 | -503 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1491 |  | -2000 | -509 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1461 |  | -2000 | -539 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1459 |  | -2000 | -541 | 73 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1423 |  | 2000 | -577 | 71 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1413 |  | 2000 | -587 | 71 | []

## 0330Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3425
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1992 | -2000 | -2000 | -8 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1819 | 1836 | 1836 | -17 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1811 | 1836 | 1836 | -25 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -950 | -999 | -999 | -49 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 | 1836 | 1836 | -130 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 | 1836 | 1836 | -130 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 | 1836 | 1836 | -138 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1695 | 1836 | 1836 | -141 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 | 1836 | 1836 | -149 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1672 | 1836 | 1836 | -164 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1661 | 1836 | 1836 | -175 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 | 1836 | 1836 | -202 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1774 | 2000 | 2000 | -226 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1560 | -2000 | -2000 | -440 | 78 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1554 | -2000 | -2000 | -446 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1533 | -2000 | -2000 | -467 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1525 | -2000 | -2000 | -475 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1488 | -2000 | -2000 | -512 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1475 | -2000 | -2000 | -525 | 74 | []

## 0330Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3425
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1992 |  | -2000 | -8 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1819 |  | 1836 | -17 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1811 |  | 1836 | -25 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -950 |  | -999 | -49 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 |  | 1836 | -130 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 |  | 1836 | -130 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 |  | 1836 | -138 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1695 |  | 1836 | -141 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 |  | 1836 | -149 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1672 |  | 1836 | -164 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1661 |  | 1836 | -175 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 |  | 1836 | -202 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1774 |  | 2000 | -226 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1560 |  | -2000 | -440 | 78 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1554 |  | -2000 | -446 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1533 |  | -2000 | -467 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1525 |  | -2000 | -475 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1488 |  | -2000 | -512 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1475 |  | -2000 | -525 | 74 | []

## 0430Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3391
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 | -2000 | -2000 | -7 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1807 | 1836 | 1836 | -29 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1796 | 1836 | 1836 | -40 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1745 | 1836 | 1836 | -91 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1745 | 1836 | 1836 | -91 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1724 | 1836 | 1836 | -112 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1708 | 1836 | 1836 | -128 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1686 | 1836 | 1836 | -150 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 | 1836 | 1836 | -151 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1668 | 1836 | 1836 | -168 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1646 | 1836 | 1836 | -190 | 90 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1772 | -2000 | -2000 | -228 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1561 | -2000 | -2000 | -439 | 78 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1554 | -2000 | -2000 | -446 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1534 | -2000 | -2000 | -466 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1526 | -2000 | -2000 | -474 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1489 | -2000 | -2000 | -511 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1476 | -2000 | -2000 | -524 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -895 | -1248 | -1248 | -353 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -891 | -1248 | -1248 | -357 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -891 | -1248 | -1248 | -358 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -881 | -1248 | -1248 | -367 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -880 | -1248 | -1248 | -369 | 70 | []

## 0430Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3391
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 |  | -2000 | -7 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1807 |  | 1836 | -29 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1796 |  | 1836 | -40 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1745 |  | 1836 | -91 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1745 |  | 1836 | -91 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1724 |  | 1836 | -112 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1708 |  | 1836 | -128 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1686 |  | 1836 | -150 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 |  | 1836 | -151 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1668 |  | 1836 | -168 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1646 |  | 1836 | -190 | 90 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1772 |  | -2000 | -228 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1561 |  | -2000 | -439 | 78 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1554 |  | -2000 | -446 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1534 |  | -2000 | -466 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1526 |  | -2000 | -474 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1489 |  | -2000 | -511 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1476 |  | -2000 | -524 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -895 |  | -1248 | -353 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -891 |  | -1248 | -357 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -891 |  | -1248 | -358 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -881 |  | -1248 | -367 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -880 |  | -1248 | -369 | 70 | []

## 0530Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3325
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 | -2000 | -2000 | -7 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 | 1836 | 1836 | -177 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1643 | 1836 | 1836 | -193 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1768 | -2000 | -2000 | -232 | 88 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 | 1836 | 1836 | -230 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 | 1836 | 1836 | -230 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1570 | 1836 | 1836 | -266 | 86 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1542 | 1836 | 1836 | -294 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1536 | 1836 | 1836 | -300 | 84 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1532 | 1836 | 1836 | -304 | 83 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1526 | 1836 | 1836 | -310 | 83 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1495 | 1836 | 1836 | -341 | 81 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1559 | -2000 | -2000 | -441 | 78 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1552 | -2000 | -2000 | -448 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1535 | -2000 | -2000 | -465 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1525 | -2000 | -2000 | -475 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1488 | -2000 | -2000 | -512 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1474 | -2000 | -2000 | -526 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -901 | -1248 | -1248 | -347 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -898 | -1248 | -1248 | -351 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -897 | -1248 | -1248 | -352 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -888 | -1248 | -1248 | -361 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -887 | -1248 | -1248 | -361 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -881 | -1248 | -1248 | -367 | 71 | []

## 0530Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3325
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1993 |  | -2000 | -7 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 |  | 1836 | -177 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1643 |  | 1836 | -193 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1768 |  | -2000 | -232 | 88 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 |  | 1836 | -230 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 |  | 1836 | -230 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1570 |  | 1836 | -266 | 86 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1542 |  | 1836 | -294 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1536 |  | 1836 | -300 | 84 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1532 |  | 1836 | -304 | 83 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1526 |  | 1836 | -310 | 83 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1495 |  | 1836 | -341 | 81 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1559 |  | -2000 | -441 | 78 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1552 |  | -2000 | -448 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1535 |  | -2000 | -465 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1525 |  | -2000 | -475 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1488 |  | -2000 | -512 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1474 |  | -2000 | -526 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -901 |  | -1248 | -347 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -898 |  | -1248 | -351 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -897 |  | -1248 | -352 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -888 |  | -1248 | -361 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -887 |  | -1248 | -361 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -881 |  | -1248 | -367 | 71 | []

## 0630Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3447
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1996 | -2000 | -2000 | -4 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1775 | -2000 | -2000 | -225 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1611 | 1836 | 1836 | -225 | 88 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1580 | 1836 | 1836 | -256 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1580 | 1836 | 1836 | -256 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1552 | 1836 | 1836 | -284 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1544 | 1836 | 1836 | -292 | 84 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1542 | 1836 | 1836 | -294 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 792 | 960 | 960 | -168 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1506 | 1836 | 1836 | -330 | 82 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1504 | 1836 | 1836 | -332 | 82 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1485 | 1836 | 1836 | -351 | 81 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 | 1836 | 1836 | -371 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -987 | -1248 | -1248 | -262 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -986 | -1248 | -1248 | -263 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -979 | -1248 | -1248 | -270 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -977 | -1248 | -1248 | -272 | 78 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1560 | -2000 | -2000 | -440 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -970 | -1248 | -1248 | -279 | 78 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1552 | -2000 | -2000 | -448 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -967 | -1248 | -1248 | -282 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1537 | -2000 | -2000 | -463 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1518 | 2000 | 2000 | -482 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1511 | -2000 | -2000 | -489 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1506 | -2000 | -2000 | -494 | 75 | []

## 0630Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3447
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1996 |  | -2000 | -4 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1775 |  | -2000 | -225 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1611 |  | 1836 | -225 | 88 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1580 |  | 1836 | -256 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1580 |  | 1836 | -256 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1552 |  | 1836 | -284 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1544 |  | 1836 | -292 | 84 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1542 |  | 1836 | -294 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 792 |  | 960 | -168 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1506 |  | 1836 | -330 | 82 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1504 |  | 1836 | -332 | 82 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1485 |  | 1836 | -351 | 81 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 |  | 1836 | -371 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -987 |  | -1248 | -262 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -986 |  | -1248 | -263 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -979 |  | -1248 | -270 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -977 |  | -1248 | -272 | 78 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1560 |  | -2000 | -440 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -970 |  | -1248 | -279 | 78 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1552 |  | -2000 | -448 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -967 |  | -1248 | -282 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1537 |  | -2000 | -463 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1518 |  | 2000 | -482 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1511 |  | -2000 | -489 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1506 |  | -2000 | -494 | 75 | []

## 0730Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3408
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1994 | -2000 | -2000 | -6 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1792 | -2000 | -2000 | -208 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1580 | 1836 | 1836 | -256 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 | 1836 | 1836 | -301 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 | 1836 | 1836 | -301 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1655 | -2000 | -2000 | -345 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1519 | 1836 | 1836 | -317 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1514 | 1836 | 1836 | -322 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1646 | -2000 | -2000 | -354 | 82 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1505 | 1836 | 1836 | -331 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1613 | -2000 | -2000 | -387 | 81 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1599 | -2000 | -2000 | -401 | 80 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 | 1836 | 1836 | -371 | 80 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1464 | 1836 | 1836 | -372 | 80 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1441 | 1836 | 1836 | -395 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 | -1248 | -1248 | -273 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -974 | -1248 | -1248 | -274 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -971 | -1248 | -1248 | -278 | 78 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 | 1836 | 1836 | -412 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -965 | -1248 | -1248 | -283 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -962 | -1248 | -1248 | -286 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -957 | -1248 | -1248 | -291 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1494 | -2000 | -2000 | -506 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1417 | -2000 | -2000 | -583 | 71 | []

## 0730Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3408
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1994 |  | -2000 | -6 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1792 |  | -2000 | -208 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1580 |  | 1836 | -256 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 |  | 1836 | -301 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 |  | 1836 | -301 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1655 |  | -2000 | -345 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1519 |  | 1836 | -317 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1514 |  | 1836 | -322 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1646 |  | -2000 | -354 | 82 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1505 |  | 1836 | -331 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1613 |  | -2000 | -387 | 81 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1599 |  | -2000 | -401 | 80 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 |  | 1836 | -371 | 80 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1464 |  | 1836 | -372 | 80 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1441 |  | 1836 | -395 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 |  | -1248 | -273 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -974 |  | -1248 | -274 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -971 |  | -1248 | -278 | 78 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 |  | 1836 | -412 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -965 |  | -1248 | -283 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -962 |  | -1248 | -286 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -957 |  | -1248 | -291 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1494 |  | -2000 | -506 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1417 |  | -2000 | -583 | 71 | []

## 0830Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3518
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1998 | -2000 | -2000 | -2 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1773 | 1836 | 1836 | -63 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 | 1836 | 1836 | -111 | 94 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 | 1836 | 1836 | -111 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1721 | 1836 | 1836 | -115 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 | 1836 | 1836 | -121 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 | 1836 | 1836 | -138 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1665 | 1836 | 1836 | -171 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 | 1836 | 1836 | -173 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1799 | 2000 | 2000 | -201 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1635 | 1836 | 1836 | -201 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1620 | 1836 | 1836 | -216 | 88 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1656 | -2000 | -2000 | -344 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1647 | -2000 | -2000 | -353 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1613 | -2000 | -2000 | -387 | 81 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1600 | -2000 | -2000 | -400 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -982 | -1248 | -1248 | -266 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -980 | -1248 | -1248 | -268 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -978 | -1248 | -1248 | -271 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -970 | -1248 | -1248 | -279 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -968 | -1248 | -1248 | -281 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -962 | -1248 | -1248 | -287 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1496 | -2000 | -2000 | -504 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1430 | -2000 | -2000 | -570 | 72 | []

## 0830Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3518
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1998 |  | -2000 | -2 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1773 |  | 1836 | -63 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 |  | 1836 | -111 | 94 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 |  | 1836 | -111 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1721 |  | 1836 | -115 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 |  | 1836 | -121 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 |  | 1836 | -138 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1665 |  | 1836 | -171 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 |  | 1836 | -173 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1799 |  | 2000 | -201 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1635 |  | 1836 | -201 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1620 |  | 1836 | -216 | 88 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1656 |  | -2000 | -344 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1647 |  | -2000 | -353 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1613 |  | -2000 | -387 | 81 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1600 |  | -2000 | -400 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -982 |  | -1248 | -266 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -980 |  | -1248 | -268 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -978 |  | -1248 | -271 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -970 |  | -1248 | -279 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -968 |  | -1248 | -281 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -962 |  | -1248 | -287 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1496 |  | -2000 | -504 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1430 |  | -2000 | -570 | 72 | []

## 0930Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3530
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1997 | -2000 | -2000 | -3 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1816 | 1836 | 1836 | -20 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 | 1836 | 1836 | -106 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 | 1836 | 1836 | -106 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 | 1836 | 1836 | -111 | 94 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 | 1836 | 1836 | -114 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 | 1836 | 1836 | -114 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 | 1836 | 1836 | -158 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1671 | 1836 | 1836 | -165 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1667 | 1836 | 1836 | -169 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1794 | -2000 | -2000 | -206 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1644 | 1836 | 1836 | -192 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1654 | -2000 | -2000 | -346 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1646 | -2000 | -2000 | -354 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1609 | -2000 | -2000 | -391 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1593 | -2000 | -2000 | -407 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1488 | -2000 | -2000 | -512 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -922 | -1248 | -1248 | -326 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -920 | -1248 | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -916 | -1248 | -1248 | -332 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -910 | -1248 | -1248 | -339 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -907 | -1248 | -1248 | -342 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -901 | -1248 | -1248 | -347 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1429 | -2000 | -2000 | -571 | 71 | []

## 0930Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3530
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1997 |  | -2000 | -3 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1816 |  | 1836 | -20 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 |  | 1836 | -106 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 |  | 1836 | -106 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 |  | 1836 | -111 | 94 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 |  | 1836 | -114 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 |  | 1836 | -114 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 |  | 1836 | -158 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1671 |  | 1836 | -165 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1667 |  | 1836 | -169 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1794 |  | -2000 | -206 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1644 |  | 1836 | -192 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1654 |  | -2000 | -346 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1646 |  | -2000 | -354 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1609 |  | -2000 | -391 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1593 |  | -2000 | -407 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1488 |  | -2000 | -512 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -922 |  | -1248 | -326 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -920 |  | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -916 |  | -1248 | -332 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -910 |  | -1248 | -339 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -907 |  | -1248 | -342 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -901 |  | -1248 | -347 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1429 |  | -2000 | -571 | 71 | []

## 1030Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3511
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1998 | -2000 | -2000 | -2 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1829 | 1836 | 1836 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 937 | 960 | 960 | -23 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1760 | 1836 | 1836 | -76 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1759 | 1836 | 1836 | -77 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1754 | 1836 | 1836 | -82 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1754 | 1836 | 1836 | -82 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1745 | 1836 | 1836 | -91 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1709 | 1836 | 1836 | -127 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 | 1836 | 1836 | -132 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1680 | 1836 | 1836 | -156 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 | 1836 | 1836 | -160 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1795 | -2000 | -2000 | -205 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1657 | -2000 | -2000 | -343 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1649 | -2000 | -2000 | -351 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1610 | -2000 | -2000 | -390 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1595 | -2000 | -2000 | -405 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -960 | -1248 | -1248 | -289 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -959 | -1248 | -1248 | -290 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -955 | -1248 | -1248 | -294 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -949 | -1248 | -1248 | -300 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -946 | -1248 | -1248 | -303 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -941 | -1248 | -1248 | -308 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1489 | -2000 | -2000 | -511 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1429 | -2000 | -2000 | -571 | 71 | []

## 1030Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3511
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1998 |  | -2000 | -2 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1829 |  | 1836 | -7 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 937 |  | 960 | -23 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1760 |  | 1836 | -76 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1759 |  | 1836 | -77 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1754 |  | 1836 | -82 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1754 |  | 1836 | -82 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1745 |  | 1836 | -91 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1709 |  | 1836 | -127 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 |  | 1836 | -132 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1680 |  | 1836 | -156 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 |  | 1836 | -160 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1795 |  | -2000 | -205 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1657 |  | -2000 | -343 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1649 |  | -2000 | -351 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1610 |  | -2000 | -390 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1595 |  | -2000 | -405 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -960 |  | -1248 | -289 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -959 |  | -1248 | -290 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -955 |  | -1248 | -294 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -949 |  | -1248 | -300 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -946 |  | -1248 | -303 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -941 |  | -1248 | -308 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1489 |  | -2000 | -511 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1429 |  | -2000 | -571 | 71 | []

## 1130Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3397
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 | 1836 | 1836 | -5 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 947 | 960 | 960 | -13 | 99 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1936 | -2000 | -2000 | -64 | 97 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1769 | 1836 | 1836 | -67 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1764 | 1836 | 1836 | -72 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1748 | 1836 | 1836 | -88 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1748 | 1836 | 1836 | -88 | 95 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1745 | 1836 | 1836 | -91 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1710 | 1836 | 1836 | -126 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 | 1836 | 1836 | -131 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 | 1836 | 1836 | -160 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1672 | 1836 | 1836 | -164 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1734 | 2000 | 2000 | -266 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1621 | -2000 | -2000 | -379 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1614 | -2000 | -2000 | -386 | 81 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1576 | -2000 | -2000 | -424 | 79 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1560 | -2000 | -2000 | -440 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -962 | -1248 | -1248 | -287 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -961 | -1248 | -1248 | -288 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -957 | -1248 | -1248 | -292 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -951 | -1248 | -1248 | -298 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -948 | -1248 | -1248 | -301 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -943 | -1248 | -1248 | -306 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1455 | 2000 | 2000 | -545 | 73 | []

## 1130Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3397
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 |  | 1836 | -5 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 947 |  | 960 | -13 | 99 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1936 |  | -2000 | -64 | 97 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1769 |  | 1836 | -67 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1764 |  | 1836 | -72 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1748 |  | 1836 | -88 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1748 |  | 1836 | -88 | 95 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1745 |  | 1836 | -91 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1710 |  | 1836 | -126 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 |  | 1836 | -131 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 |  | 1836 | -160 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1672 |  | 1836 | -164 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1734 |  | 2000 | -266 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1621 |  | -2000 | -379 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1614 |  | -2000 | -386 | 81 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1576 |  | -2000 | -424 | 79 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1560 |  | -2000 | -440 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -962 |  | -1248 | -287 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -961 |  | -1248 | -288 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -957 |  | -1248 | -292 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -951 |  | -1248 | -298 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -948 |  | -1248 | -301 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -943 |  | -1248 | -306 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1455 |  | 2000 | -545 | 73 | []

## 1230Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3468
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 | 1836 | 1836 | -2 | 100 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1966 | -2000 | -2000 | -34 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1763 | 1836 | 1836 | -73 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1752 | 1836 | 1836 | -84 | 95 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1742 | 1836 | 1836 | -94 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 | 1836 | 1836 | -101 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 | 1836 | 1836 | -101 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1716 | 1836 | 1836 | -120 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 | 1836 | 1836 | -130 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 | 1836 | 1836 | -140 | 92 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -910 | -999 | -999 | -89 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1662 | 1836 | 1836 | -174 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1766 | 2000 | 2000 | -234 | 88 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1640 | -2000 | -2000 | -360 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1633 | -2000 | -2000 | -367 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1592 | -2000 | -2000 | -408 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1578 | -2000 | -2000 | -422 | 79 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1473 | 2000 | 2000 | -527 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -901 | -1248 | -1248 | -348 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -899 | -1248 | -1248 | -349 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -895 | -1248 | -1248 | -354 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -890 | -1248 | -1248 | -359 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -886 | -1248 | -1248 | -363 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -881 | -1248 | -1248 | -367 | 71 | []

## 1230Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3468
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 |  | 1836 | -2 | 100 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1966 |  | -2000 | -34 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1763 |  | 1836 | -73 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1752 |  | 1836 | -84 | 95 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1742 |  | 1836 | -94 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 |  | 1836 | -101 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 |  | 1836 | -101 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1716 |  | 1836 | -120 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 |  | 1836 | -130 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 |  | 1836 | -140 | 92 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -910 |  | -999 | -89 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1662 |  | 1836 | -174 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1766 |  | 2000 | -234 | 88 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1640 |  | -2000 | -360 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1633 |  | -2000 | -367 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1592 |  | -2000 | -408 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1578 |  | -2000 | -422 | 79 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1473 |  | 2000 | -527 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -901 |  | -1248 | -348 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -899 |  | -1248 | -349 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -895 |  | -1248 | -354 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -890 |  | -1248 | -359 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -886 |  | -1248 | -363 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -881 |  | -1248 | -367 | 71 | []

## 1330Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3526
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1999 | -2000 | -2000 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1824 | 1836 | 1836 | -12 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1752 | 1836 | 1836 | -84 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1736 | 1836 | 1836 | -100 | 95 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1734 | 1836 | 1836 | -102 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1733 | 1836 | 1836 | -103 | 94 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1733 | 1836 | 1836 | -103 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 | 1836 | 1836 | -130 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 | 1836 | 1836 | -144 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 | 1836 | 1836 | -152 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1805 | -2000 | -2000 | -195 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1653 | 1836 | 1836 | -183 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -893 | -999 | -999 | -106 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1656 | -2000 | -2000 | -344 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1649 | -2000 | -2000 | -351 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1613 | -2000 | -2000 | -387 | 81 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1601 | -2000 | -2000 | -399 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1501 | -2000 | -2000 | -499 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -904 | -1248 | -1248 | -344 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -903 | -1248 | -1248 | -346 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -899 | -1248 | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -893 | -1248 | -1248 | -356 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -889 | -1248 | -1248 | -359 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1422 | -2000 | -2000 | -578 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -884 | -1248 | -1248 | -364 | 71 | []

## 1330Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3526
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1999 |  | -2000 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1824 |  | 1836 | -12 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1752 |  | 1836 | -84 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1736 |  | 1836 | -100 | 95 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1734 |  | 1836 | -102 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1733 |  | 1836 | -103 | 94 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1733 |  | 1836 | -103 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 |  | 1836 | -130 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 |  | 1836 | -144 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 |  | 1836 | -152 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1805 |  | -2000 | -195 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1653 |  | 1836 | -183 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -893 |  | -999 | -106 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1656 |  | -2000 | -344 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1649 |  | -2000 | -351 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1613 |  | -2000 | -387 | 81 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1601 |  | -2000 | -399 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1501 |  | -2000 | -499 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -904 |  | -1248 | -344 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -903 |  | -1248 | -346 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -899 |  | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -893 |  | -1248 | -356 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -889 |  | -1248 | -359 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1422 |  | -2000 | -578 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -884 |  | -1248 | -364 | 71 | []

## 1430Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3538
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 | 1836 | 1836 | -2 | 100 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1977 | -2000 | -2000 | -23 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1787 | 1836 | 1836 | -49 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1764 | 1836 | 1836 | -72 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1756 | 1836 | 1836 | -80 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1756 | 1836 | 1836 | -80 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1750 | 1836 | 1836 | -86 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 | 1836 | 1836 | -106 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1720 | 1836 | 1836 | -116 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 | 1836 | 1836 | -125 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 | 1836 | 1836 | -160 | 91 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -911 | -999 | -999 | -88 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1798 | -2000 | -2000 | -202 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1634 | -2000 | -2000 | -366 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1627 | -2000 | -2000 | -373 | 81 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1595 | -2000 | -2000 | -405 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1584 | -2000 | -2000 | -416 | 79 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1492 | -2000 | -2000 | -508 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -926 | -1248 | -1248 | -322 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -925 | -1248 | -1248 | -324 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -921 | -1248 | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -915 | -1248 | -1248 | -334 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -912 | -1248 | -1248 | -337 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -907 | -1248 | -1248 | -342 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1406 | -2000 | -2000 | -594 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3538
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 |  | 1836 | -2 | 100 | []
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1977 |  | -2000 | -23 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1787 |  | 1836 | -49 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1764 |  | 1836 | -72 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1756 |  | 1836 | -80 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1756 |  | 1836 | -80 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1750 |  | 1836 | -86 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 |  | 1836 | -106 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1720 |  | 1836 | -116 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 |  | 1836 | -125 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 |  | 1836 | -160 | 91 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -911 |  | -999 | -88 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1798 |  | -2000 | -202 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1634 |  | -2000 | -366 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1627 |  | -2000 | -373 | 81 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1595 |  | -2000 | -405 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1584 |  | -2000 | -416 | 79 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1492 |  | -2000 | -508 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -926 |  | -1248 | -322 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -925 |  | -1248 | -324 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -921 |  | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -915 |  | -1248 | -334 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -912 |  | -1248 | -337 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -907 |  | -1248 | -342 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1406 |  | -2000 | -594 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3525
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1994 | -2000 | -2000 | -6 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1727 | 1836 | 1836 | -109 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 | 1836 | 1836 | -130 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 | 1836 | 1836 | -130 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 | 1836 | 1836 | -131 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 | 1836 | 1836 | -149 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1827 | -2000 | -2000 | -173 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1668 | 1836 | 1836 | -168 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1640 | 1836 | 1836 | -196 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1640 | 1836 | 1836 | -196 | 89 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1613 | 1836 | 1836 | -223 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1597 | 1836 | 1836 | -239 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1635 | -2000 | -2000 | -365 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1625 | -2000 | -2000 | -375 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 | -1248 | -1248 | -245 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 | -1248 | -1248 | -245 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1601 | -2000 | -2000 | -399 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -996 | -1248 | -1248 | -252 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1591 | -2000 | -2000 | -409 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -993 | -1248 | -1248 | -256 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -987 | -1248 | -1248 | -262 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -983 | -1248 | -1248 | -265 | 79 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1506 | -2000 | -2000 | -494 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1420 | -2000 | -2000 | -580 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3525
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1994 |  | -2000 | -6 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1727 |  | 1836 | -109 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 |  | 1836 | -130 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 |  | 1836 | -130 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 |  | 1836 | -131 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 |  | 1836 | -149 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1827 |  | -2000 | -173 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1668 |  | 1836 | -168 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1640 |  | 1836 | -196 | 89 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1640 |  | 1836 | -196 | 89 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1613 |  | 1836 | -223 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1597 |  | 1836 | -239 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1635 |  | -2000 | -365 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1625 |  | -2000 | -375 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 |  | -1248 | -245 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 |  | -1248 | -245 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1601 |  | -2000 | -399 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -996 |  | -1248 | -252 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1591 |  | -2000 | -409 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -993 |  | -1248 | -256 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -987 |  | -1248 | -262 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -983 |  | -1248 | -265 | 79 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1506 |  | -2000 | -494 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1420 |  | -2000 | -580 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3508
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1999 | -2000 | -2000 | -1 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1843 | -2000 | -2000 | -157 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1562 | 1836 | 1836 | -274 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1562 | 1836 | 1836 | -274 | 85 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1550 | 1836 | 1836 | -286 | 84 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1543 | 1836 | 1836 | -293 | 84 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1523 | 1836 | 1836 | -313 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1517 | 1836 | 1836 | -319 | 83 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1634 | -2000 | -2000 | -366 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1624 | -2000 | -2000 | -376 | 81 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1479 | 1836 | 1836 | -357 | 81 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1476 | 1836 | 1836 | -360 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1607 | -2000 | -2000 | -393 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1600 | -2000 | -2000 | -400 | 80 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1457 | 1836 | 1836 | -379 | 79 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1437 | 1836 | 1836 | -399 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 | -1248 | -1248 | -272 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -975 | -1248 | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -968 | -1248 | -1248 | -280 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -967 | -1248 | -1248 | -282 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -960 | -1248 | -1248 | -289 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -957 | -1248 | -1248 | -292 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1521 | -2000 | -2000 | -479 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1416 | -2000 | -2000 | -584 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3508
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1999 |  | -2000 | -1 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1843 |  | -2000 | -157 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1562 |  | 1836 | -274 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1562 |  | 1836 | -274 | 85 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1550 |  | 1836 | -286 | 84 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1543 |  | 1836 | -293 | 84 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1523 |  | 1836 | -313 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1517 |  | 1836 | -319 | 83 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1634 |  | -2000 | -366 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1624 |  | -2000 | -376 | 81 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1479 |  | 1836 | -357 | 81 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1476 |  | 1836 | -360 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1607 |  | -2000 | -393 | 80 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1600 |  | -2000 | -400 | 80 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1457 |  | 1836 | -379 | 79 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1437 |  | 1836 | -399 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -976 |  | -1248 | -272 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -975 |  | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -968 |  | -1248 | -280 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -967 |  | -1248 | -282 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -960 |  | -1248 | -289 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -957 |  | -1248 | -292 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1521 |  | -2000 | -479 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | -1416 |  | -2000 | -584 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3515
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1999 | -2000 | -2000 | -1 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1852 | -2000 | -2000 | -148 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1552 | 1836 | 1836 | -284 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1552 | 1836 | 1836 | -284 | 85 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 | 1836 | 1836 | -301 | 84 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1516 | 1836 | 1836 | -320 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1512 | 1836 | 1836 | -324 | 82 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1505 | 1836 | 1836 | -331 | 82 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1470 | 1836 | 1836 | -366 | 80 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1467 | 1836 | 1836 | -369 | 80 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1446 | 1836 | 1836 | -390 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -969 | -1248 | -1248 | -279 | 78 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1425 | 1836 | 1836 | -411 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -968 | -1248 | -1248 | -280 | 78 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1551 | -2000 | -2000 | -449 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -961 | -1248 | -1248 | -287 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -960 | -1248 | -1248 | -288 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1538 | -2000 | -2000 | -462 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1530 | -2000 | -2000 | -470 | 77 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1529 | -2000 | -2000 | -471 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -953 | -1248 | -1248 | -296 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1522 | -2000 | -2000 | -478 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -950 | -1248 | -1248 | -298 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1503 | 2000 | 2000 | -497 | 75 | []

## 1730Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3515
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1999 |  | -2000 | -1 | 100 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1852 |  | -2000 | -148 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1552 |  | 1836 | -284 | 85 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1552 |  | 1836 | -284 | 85 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 |  | 1836 | -301 | 84 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1516 |  | 1836 | -320 | 83 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1512 |  | 1836 | -324 | 82 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1505 |  | 1836 | -331 | 82 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1470 |  | 1836 | -366 | 80 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1467 |  | 1836 | -369 | 80 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1446 |  | 1836 | -390 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -969 |  | -1248 | -279 | 78 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1425 |  | 1836 | -411 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -968 |  | -1248 | -280 | 78 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1551 |  | -2000 | -449 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -961 |  | -1248 | -287 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -960 |  | -1248 | -288 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1538 |  | -2000 | -462 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1530 |  | -2000 | -470 | 77 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1529 |  | -2000 | -471 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -953 |  | -1248 | -296 | 76 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1522 |  | -2000 | -478 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -950 |  | -1248 | -298 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1503 |  | 2000 | -497 | 75 | []

## 1830Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3549
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1934 | -2000 | -2000 | -66 | 97 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1815 | -2000 | -2000 | -185 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1651 | 1836 | 1836 | -185 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1651 | 1836 | 1836 | -185 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1622 | 1836 | 1836 | -214 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1611 | 1836 | 1836 | -225 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 | 1836 | 1836 | -236 | 87 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1599 | 1836 | 1836 | -237 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1571 | 1836 | 1836 | -265 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1570 | 1836 | 1836 | -266 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1544 | 1836 | 1836 | -292 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1520 | 1836 | 1836 | -316 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -978 | -1248 | -1248 | -271 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -977 | -1248 | -1248 | -271 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -970 | -1248 | -1248 | -278 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -968 | -1248 | -1248 | -281 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -961 | -1248 | -1248 | -287 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -958 | -1248 | -1248 | -291 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1497 | -2000 | -2000 | -503 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1484 | -2000 | -2000 | -516 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1477 | -2000 | -2000 | -523 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1474 | -2000 | -2000 | -526 | 74 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1471 | -2000 | -2000 | -529 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1457 | 2000 | 2000 | -543 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1127 | 1600 | 1600 | -473 | 70 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1127 | 1600 | 1600 | -473 | 70 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1121 | 1601 | 1601 | -480 | 70 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1121 | 1601 | 1601 | -480 | 70 | []

## 1830Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3549
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1934 |  | -2000 | -66 | 97 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1815 |  | -2000 | -185 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1651 |  | 1836 | -185 | 90 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1651 |  | 1836 | -185 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1622 |  | 1836 | -214 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1611 |  | 1836 | -225 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 |  | 1836 | -236 | 87 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1599 |  | 1836 | -237 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1571 |  | 1836 | -265 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1570 |  | 1836 | -266 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1544 |  | 1836 | -292 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1520 |  | 1836 | -316 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -978 |  | -1248 | -271 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -977 |  | -1248 | -271 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -970 |  | -1248 | -278 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -968 |  | -1248 | -281 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -961 |  | -1248 | -287 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -958 |  | -1248 | -291 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1497 |  | -2000 | -503 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1484 |  | -2000 | -516 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1477 |  | -2000 | -523 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1474 |  | -2000 | -526 | 74 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1471 |  | -2000 | -529 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [OPP] [RO] | XDO_RA11_RRAHM41 _1:line | 1457 |  | 2000 | -543 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1127 |  | 1600 | -473 | 70 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1127 |  | 1600 | -473 | 70 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1121 |  | 1601 | -480 | 70 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1121 |  | 1601 | -480 | 70 | []

## 1930Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3569
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1929 | -2000 | -2000 | -71 | 96 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1826 | -2000 | -2000 | -174 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1587 | 1836 | 1836 | -249 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1578 | 1836 | 1836 | -258 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1578 | 1836 | 1836 | -258 | 86 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 | 1836 | 1836 | -276 | 85 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1520 | 1836 | 1836 | -316 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1517 | 1836 | 1836 | -319 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1491 | 1836 | 1836 | -345 | 81 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1490 | 1836 | 1836 | -346 | 81 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1461 | 1836 | 1836 | -375 | 80 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1438 | 1836 | 1836 | -398 | 78 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1219 | 1601 | 1601 | -382 | 76 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1219 | 1601 | 1601 | -382 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -934 | -1248 | -1248 | -314 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1495 | -2000 | -2000 | -505 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -931 | -1248 | -1248 | -317 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -930 | -1248 | -1248 | -319 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -922 | -1248 | -1248 | -327 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1476 | -2000 | -2000 | -524 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -921 | -1248 | -1248 | -327 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1470 | -2000 | -2000 | -530 | 74 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1468 | -2000 | -2000 | -532 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1467 | -2000 | -2000 | -533 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -915 | -1248 | -1248 | -333 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1452 | 2000 | 2000 | -548 | 73 | []

## 1930Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3569
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1929 |  | -2000 | -71 | 96 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1826 |  | -2000 | -174 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1587 |  | 1836 | -249 | 86 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1578 |  | 1836 | -258 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1578 |  | 1836 | -258 | 86 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 |  | 1836 | -276 | 85 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1520 |  | 1836 | -316 | 83 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1517 |  | 1836 | -319 | 83 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1491 |  | 1836 | -345 | 81 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1490 |  | 1836 | -346 | 81 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1461 |  | 1836 | -375 | 80 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1438 |  | 1836 | -398 | 78 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1224 |  | 1600 | -376 | 76 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1224 |  | 1600 | -376 | 76 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1219 |  | 1601 | -382 | 76 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1219 |  | 1601 | -382 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -934 |  | -1248 | -314 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1495 |  | -2000 | -505 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -931 |  | -1248 | -317 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -930 |  | -1248 | -319 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -922 |  | -1248 | -327 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1476 |  | -2000 | -524 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -921 |  | -1248 | -327 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1470 |  | -2000 | -530 | 74 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1468 |  | -2000 | -532 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1467 |  | -2000 | -533 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -915 |  | -1248 | -333 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1452 |  | 2000 | -548 | 73 | []

## 2030Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3542
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1843 | -2000 | -2000 | -157 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1632 | 1836 | 1836 | -204 | 89 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1630 | 1836 | 1836 | -206 | 89 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1630 | 1836 | 1836 | -206 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1759 | -2000 | -2000 | -241 | 88 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1609 | 1836 | 1836 | -227 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1587 | 1836 | 1836 | -249 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1571 | 1836 | 1836 | -265 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1540 | 1836 | 1836 | -296 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1539 | 1836 | 1836 | -297 | 84 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1509 | 1836 | 1836 | -327 | 82 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1491 | 1836 | 1836 | -345 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1265 | 1601 | 1601 | -336 | 79 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1265 | 1601 | 1601 | -336 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -945 | -1248 | -1248 | -303 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -942 | -1248 | -1248 | -306 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -941 | -1248 | -1248 | -308 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -932 | -1248 | -1248 | -316 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -932 | -1248 | -1248 | -316 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -926 | -1248 | -1248 | -322 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1460 | -2000 | -2000 | -540 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1145 | 1601 | 1601 | -456 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1145 | 1601 | 1601 | -456 | 72 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1419 | -2000 | -2000 | -581 | 71 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1418 | -2000 | -2000 | -582 | 71 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1415 | -2000 | -2000 | -585 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1409 | -2000 | -2000 | -591 | 70 | []

## 2030Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3542
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1843 |  | -2000 | -157 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1632 |  | 1836 | -204 | 89 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1630 |  | 1836 | -206 | 89 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1630 |  | 1836 | -206 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1759 |  | -2000 | -241 | 88 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1609 |  | 1836 | -227 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1587 |  | 1836 | -249 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1571 |  | 1836 | -265 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1540 |  | 1836 | -296 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1539 |  | 1836 | -297 | 84 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1509 |  | 1836 | -327 | 82 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1491 |  | 1836 | -345 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1271 |  | 1600 | -329 | 79 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1271 |  | 1600 | -329 | 79 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1265 |  | 1601 | -336 | 79 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1265 |  | 1601 | -336 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -945 |  | -1248 | -303 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -942 |  | -1248 | -306 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -941 |  | -1248 | -308 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -932 |  | -1248 | -316 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -932 |  | -1248 | -316 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -926 |  | -1248 | -322 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1460 |  | -2000 | -540 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1150 |  | 1600 | -450 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1150 |  | 1600 | -450 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1145 |  | 1601 | -456 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1145 |  | 1601 | -456 | 72 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1419 |  | -2000 | -581 | 71 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1418 |  | -2000 | -582 | 71 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1415 |  | -2000 | -585 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1409 |  | -2000 | -591 | 70 | []

## 2130Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3587
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1829 | -2000 | -2000 | -171 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1658 | 1836 | 1836 | -178 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 | 1836 | 1836 | -202 | 89 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 | 1836 | 1836 | -209 | 89 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 | 1836 | 1836 | -209 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1763 | -2000 | -2000 | -237 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1575 | 1836 | 1836 | -261 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 | 1836 | 1836 | -276 | 85 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1541 | 1836 | 1836 | -295 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1536 | 1836 | 1836 | -300 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1533 | 1836 | 1836 | -303 | 84 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1503 | 1836 | 1836 | -333 | 82 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1297 | 1600 | 1600 | -303 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1297 | 1600 | 1600 | -303 | 81 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1292 | 1601 | 1601 | -309 | 81 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1292 | 1601 | 1601 | -309 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1160 | 1601 | 1601 | -441 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1160 | 1601 | 1601 | -441 | 72 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1445 | -2000 | -2000 | -555 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -888 | -1248 | -1248 | -360 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -885 | -1248 | -1248 | -363 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -884 | -1248 | -1248 | -365 | 71 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1406 | -2000 | -2000 | -594 | 70 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1402 | -2000 | -2000 | -598 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -875 | -1248 | -1248 | -373 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -875 | -1248 | -1248 | -373 | 70 | []

## 2130Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3587
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1829 |  | -2000 | -171 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1658 |  | 1836 | -178 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 |  | 1836 | -202 | 89 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 |  | 1836 | -209 | 89 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 |  | 1836 | -209 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1763 |  | -2000 | -237 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1575 |  | 1836 | -261 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1560 |  | 1836 | -276 | 85 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1541 |  | 1836 | -295 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1536 |  | 1836 | -300 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1533 |  | 1836 | -303 | 84 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1503 |  | 1836 | -333 | 82 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1297 |  | 1600 | -303 | 81 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1297 |  | 1600 | -303 | 81 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1292 |  | 1601 | -309 | 81 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1292 |  | 1601 | -309 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1165 |  | 1600 | -435 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1165 |  | 1600 | -435 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1160 |  | 1601 | -441 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1160 |  | 1601 | -441 | 72 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1445 |  | -2000 | -555 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -888 |  | -1248 | -360 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -885 |  | -1248 | -363 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -884 |  | -1248 | -365 | 71 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1406 |  | -2000 | -594 | 70 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1402 |  | -2000 | -598 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -875 |  | -1248 | -373 | 70 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -875 |  | -1248 | -373 | 70 | []

## 2230Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3684
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1873 | -2000 | -2000 | -127 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1820 | -2000 | -2000 | -180 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 | 1836 | 1836 | -166 | 91 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 | 1836 | 1836 | -166 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1646 | 1836 | 1836 | -190 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1623 | 1836 | 1836 | -213 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1594 | 1836 | 1836 | -242 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 | 1836 | 1836 | -245 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1377 | 1600 | 1600 | -223 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1377 | 1600 | 1600 | -223 | 86 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1372 | 1601 | 1601 | -229 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1372 | 1601 | 1601 | -229 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1567 | 1836 | 1836 | -269 | 85 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 | 1836 | 1836 | -271 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1539 | 1836 | 1836 | -297 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1525 | 1836 | 1836 | -311 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -978 | -1248 | -1248 | -270 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -975 | -1248 | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -974 | -1248 | -1248 | -275 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -965 | -1248 | -1248 | -283 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -965 | -1248 | -1248 | -284 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -959 | -1248 | -1248 | -290 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1217 | 1601 | 1601 | -384 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1217 | 1601 | 1601 | -384 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1467 | -2000 | -2000 | -533 | 73 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1433 | -2000 | -2000 | -567 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1427 | -2000 | -2000 | -573 | 71 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1424 | -2000 | -2000 | -576 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1417 | -2000 | -2000 | -583 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1404 | -2000 | -2000 | -596 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3684
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1873 |  | -2000 | -127 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1820 |  | -2000 | -180 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 |  | 1836 | -166 | 91 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 |  | 1836 | -166 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1646 |  | 1836 | -190 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1623 |  | 1836 | -213 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1594 |  | 1836 | -242 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 |  | 1836 | -245 | 87 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1377 |  | 1600 | -223 | 86 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1377 |  | 1600 | -223 | 86 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1372 |  | 1601 | -229 | 86 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1372 |  | 1601 | -229 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1836 | -269 | 85 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1836 | -271 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1539 |  | 1836 | -297 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1525 |  | 1836 | -311 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -978 |  | -1248 | -270 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -975 |  | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -974 |  | -1248 | -275 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -965 |  | -1248 | -283 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -965 |  | -1248 | -284 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -959 |  | -1248 | -290 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1223 |  | 1600 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1223 |  | 1600 | -377 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1217 |  | 1601 | -384 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1217 |  | 1601 | -384 | 76 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1467 |  | -2000 | -533 | 73 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1433 |  | -2000 | -567 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1427 |  | -2000 | -573 | 71 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1424 |  | -2000 | -576 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1417 |  | -2000 | -583 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | -1404 |  | -2000 | -596 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3749
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1977 | -2000 | -2000 | -23 | 99 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1923 | -2000 | -2000 | -77 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1691 | 1836 | 1836 | -145 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1691 | 1836 | 1836 | -145 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1645 | 1836 | 1836 | -191 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1628 | 1836 | 1836 | -208 | 89 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1595 | 1836 | 1836 | -241 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1579 | 1836 | 1836 | -257 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1576 | 1836 | 1836 | -260 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1572 | 1836 | 1836 | -264 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1562 | 1836 | 1836 | -274 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1344 | 1600 | 1600 | -256 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1344 | 1600 | 1600 | -256 | 84 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1341 | 1601 | 1601 | -260 | 84 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1341 | 1601 | 1601 | -260 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1530 | 1836 | 1836 | -306 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1012 | -1248 | -1248 | -237 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1009 | -1248 | -1248 | -239 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1007 | -1248 | -1248 | -241 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -999 | -1248 | -1248 | -250 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -998 | -1248 | -1248 | -250 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -992 | -1248 | -1248 | -256 | 79 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1520 | -2000 | -2000 | -480 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1202 | 1601 | 1601 | -399 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1202 | 1601 | 1601 | -399 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1497 | -2000 | -2000 | -503 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1496 | 2000 | 2000 | -504 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1495 | -2000 | -2000 | -505 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1491 | -2000 | -2000 | -509 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1487 | -2000 | -2000 | -513 | 74 | []

## 2330Curative
Detailed results
Generated at: | 2024-03-11 19:20
Business day: | 12.03.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3749
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Dobrudja-Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1977 |  | -2000 | -23 | 99 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1923 |  | -2000 | -77 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1691 |  | 1836 | -145 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1691 |  | 1836 | -145 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1645 |  | 1836 | -191 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1628 |  | 1836 | -208 | 89 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1595 |  | 1836 | -241 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1579 |  | 1836 | -257 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1576 |  | 1836 | -260 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1572 |  | 1836 | -264 | 86 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1562 |  | 1836 | -274 | 85 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1344 |  | 1600 | -256 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1344 |  | 1600 | -256 | 84 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1341 |  | 1601 | -260 | 84 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1341 |  | 1601 | -260 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1530 |  | 1836 | -306 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1012 |  | -1248 | -237 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1009 |  | -1248 | -239 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1007 |  | -1248 | -241 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -999 |  | -1248 | -250 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -998 |  | -1248 | -250 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -992 |  | -1248 | -256 | 79 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1520 |  | -2000 | -480 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1205 |  | 1600 | -395 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1205 |  | 1600 | -395 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 1 [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1202 |  | 1601 | -399 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1202 |  | 1601 | -399 | 75 | []
BC | Base Case | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1497 |  | -2000 | -503 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Rahman - Dobrudja [DIR] [RO] | XDO_RA11_RRAHM41 _1:line | 1496 |  | 2000 | -504 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1495 |  | -2000 | -505 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1491 |  | -2000 | -509 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1487 |  | -2000 | -513 | 74 | []