## 0030Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3029
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1738 | 1740 | 1740 | -2 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1721 | 1740 | 1740 | -19 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 | 1740 | 1740 | -35 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 | 1740 | 1740 | -35 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1690 | 1740 | 1740 | -50 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 | 1740 | 1740 | -63 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 | 1740 | 1740 | -66 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1665 | 1740 | 1740 | -75 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1653 | 1740 | 1740 | -87 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1628 | 1740 | 1740 | -112 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1744 | -1995 | -1995 | -251 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1715 | -1995 | -1995 | -280 | 86 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1693 | -1995 | -1995 | -302 | 85 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 | -1995 | -1995 | -307 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1638 | -1995 | -1995 | -357 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1633 | -1995 | -1995 | -362 | 82 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1627 | -1995 | -1995 | -368 | 82 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 | -1995 | -1995 | -370 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 | -1995 | -1995 | -370 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1623 | -1995 | -1995 | -372 | 81 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1621 | -1995 | -1995 | -374 | 81 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1621 | -1995 | -1995 | -374 | 81 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1620 | -1995 | -1995 | -375 | 81 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1578 | -1995 | -1995 | -417 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -982 | -1248 | -1248 | -266 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -978 | -1248 | -1248 | -270 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -978 | -1248 | -1248 | -271 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -968 | -1248 | -1248 | -281 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -967 | -1248 | -1248 | -281 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -961 | -1248 | -1248 | -288 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1472 | -1995 | -1995 | -523 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1453 | -1995 | -1995 | -542 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1249 | -1740 | -1740 | -491 | 72 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1431 | -2000 | -2000 | -569 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1414 | -2000 | -2000 | -586 | 71 | []

## 0030Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3029
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1738 |  | 1740 | -2 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1721 |  | 1740 | -19 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 |  | 1740 | -35 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 |  | 1740 | -35 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1690 |  | 1740 | -50 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 |  | 1740 | -63 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 |  | 1740 | -66 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1665 |  | 1740 | -75 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1653 |  | 1740 | -87 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1628 |  | 1740 | -112 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1744 |  | -1995 | -251 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1715 |  | -1995 | -280 | 86 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1693 |  | -1995 | -302 | 85 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 |  | -1995 | -307 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1638 |  | -1995 | -357 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1633 |  | -1995 | -362 | 82 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1627 |  | -1995 | -368 | 82 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 |  | -1995 | -370 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 |  | -1995 | -370 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1623 |  | -1995 | -372 | 81 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1621 |  | -1995 | -374 | 81 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1621 |  | -1995 | -374 | 81 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1620 |  | -1995 | -375 | 81 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1578 |  | -1995 | -417 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -982 |  | -1248 | -266 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -978 |  | -1248 | -270 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -978 |  | -1248 | -271 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -968 |  | -1248 | -281 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -967 |  | -1248 | -281 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -961 |  | -1248 | -288 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1472 |  | -1995 | -523 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1453 |  | -1995 | -542 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1249 |  | -1740 | -491 | 72 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1431 |  | -2000 | -569 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1414 |  | -2000 | -586 | 71 | []

## 0130Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2881
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1740 | 1740 | 1740 | 0 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 | 1740 | 1740 | -18 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1694 | 1740 | 1740 | -46 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1694 | 1740 | 1740 | -46 | 97 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1689 | 1740 | 1740 | -51 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 | 1740 | 1740 | -66 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 | 1740 | 1740 | -70 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1661 | 1740 | 1740 | -79 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1650 | 1740 | 1740 | -90 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1624 | 1740 | 1740 | -116 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1682 | -1995 | -1995 | -313 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1658 | -1995 | -1995 | -337 | 83 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1635 | -1995 | -1995 | -360 | 82 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1628 | -1995 | -1995 | -367 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1573 | -1995 | -1995 | -422 | 79 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1570 | -1995 | -1995 | -425 | 79 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1565 | -1995 | -1995 | -430 | 78 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1561 | -1995 | -1995 | -434 | 78 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1554 | -1995 | -1995 | -441 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -972 | -1248 | -1248 | -276 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -968 | -1248 | -1248 | -280 | 78 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1546 | -1995 | -1995 | -449 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -968 | -1248 | -1248 | -281 | 78 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1545 | -1995 | -1995 | -450 | 77 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1541 | -1995 | -1995 | -454 | 77 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1539 | -1995 | -1995 | -456 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -958 | -1248 | -1248 | -291 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -957 | -1248 | -1248 | -291 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -951 | -1248 | -1248 | -298 | 76 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1506 | -1995 | -1995 | -489 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1417 | -1995 | -1995 | -578 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1227 | -1740 | -1740 | -513 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1398 | -1995 | -1995 | -597 | 70 | []

## 0130Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2881
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1740 |  | 1740 | 0 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 |  | 1740 | -18 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1694 |  | 1740 | -46 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1694 |  | 1740 | -46 | 97 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1689 |  | 1740 | -51 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 |  | 1740 | -66 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 |  | 1740 | -70 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1661 |  | 1740 | -79 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1650 |  | 1740 | -90 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1624 |  | 1740 | -116 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1682 |  | -1995 | -313 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1658 |  | -1995 | -337 | 83 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1635 |  | -1995 | -360 | 82 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1628 |  | -1995 | -367 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1573 |  | -1995 | -422 | 79 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1570 |  | -1995 | -425 | 79 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1565 |  | -1995 | -430 | 78 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1561 |  | -1995 | -434 | 78 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1554 |  | -1995 | -441 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -972 |  | -1248 | -276 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -968 |  | -1248 | -280 | 78 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1546 |  | -1995 | -449 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -968 |  | -1248 | -281 | 78 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1545 |  | -1995 | -450 | 77 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1541 |  | -1995 | -454 | 77 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1539 |  | -1995 | -456 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -958 |  | -1248 | -291 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -957 |  | -1248 | -291 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -951 |  | -1248 | -298 | 76 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1506 |  | -1995 | -489 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1417 |  | -1995 | -578 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1227 |  | -1740 | -513 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1398 |  | -1995 | -597 | 70 | []

## 0230Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3049
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1739 | 1740 | 1740 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 | 1740 | 1740 | -18 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1710 | 1740 | 1740 | -30 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1710 | 1740 | 1740 | -30 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 | 1740 | 1740 | -48 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 | 1740 | 1740 | -62 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 | 1740 | 1740 | -64 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 | 1740 | 1740 | -74 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1655 | 1740 | 1740 | -85 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1630 | 1740 | 1740 | -110 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1744 | -1995 | -1995 | -251 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1720 | -1995 | -1995 | -275 | 86 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1705 | -1995 | -1995 | -290 | 85 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1696 | -1995 | -1995 | -299 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1642 | -1995 | -1995 | -353 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1636 | -1995 | -1995 | -359 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1628 | -1995 | -1995 | -367 | 82 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1628 | -1995 | -1995 | -367 | 82 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1627 | -1995 | -1995 | -368 | 82 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 | -1995 | -1995 | -370 | 81 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1623 | -1995 | -1995 | -372 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1620 | -1995 | -1995 | -375 | 81 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1619 | -1995 | -1995 | -376 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -988 | -1248 | -1248 | -260 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1577 | -1995 | -1995 | -418 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -984 | -1248 | -1248 | -264 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -984 | -1248 | -1248 | -265 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -974 | -1248 | -1248 | -275 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -973 | -1248 | -1248 | -275 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -967 | -1248 | -1248 | -282 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1475 | -1995 | -1995 | -520 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1455 | -1995 | -1995 | -540 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1264 | -1740 | -1740 | -476 | 73 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1431 | -2000 | -2000 | -569 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | 1413 | 2000 | 2000 | -587 | 71 | []

## 0230Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3049
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1739 |  | 1740 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 |  | 1740 | -18 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1710 |  | 1740 | -30 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1710 |  | 1740 | -30 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 |  | 1740 | -48 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 |  | 1740 | -62 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 |  | 1740 | -64 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 |  | 1740 | -74 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1655 |  | 1740 | -85 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1630 |  | 1740 | -110 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1744 |  | -1995 | -251 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1720 |  | -1995 | -275 | 86 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1705 |  | -1995 | -290 | 85 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1696 |  | -1995 | -299 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1642 |  | -1995 | -353 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1636 |  | -1995 | -359 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1628 |  | -1995 | -367 | 82 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1628 |  | -1995 | -367 | 82 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1627 |  | -1995 | -368 | 82 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 |  | -1995 | -370 | 81 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1623 |  | -1995 | -372 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1620 |  | -1995 | -375 | 81 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1619 |  | -1995 | -376 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -988 |  | -1248 | -260 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1577 |  | -1995 | -418 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -984 |  | -1248 | -264 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -984 |  | -1248 | -265 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -974 |  | -1248 | -275 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -973 |  | -1248 | -275 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -967 |  | -1248 | -282 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1475 |  | -1995 | -520 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1455 |  | -1995 | -540 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1264 |  | -1740 | -476 | 73 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1431 |  | -2000 | -569 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | 1413 |  | 2000 | -587 | 71 | []

## 0330Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3148
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 | 1740 | 1740 | -3 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1721 | 1740 | 1740 | -19 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -987 | -999 | -999 | -12 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1693 | 1740 | 1740 | -47 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1693 | 1740 | 1740 | -47 | 97 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 | 1740 | 1740 | -62 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 | 1740 | 1740 | -67 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 | 1740 | 1740 | -77 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 | 1740 | 1740 | -81 | 95 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1650 | 1740 | 1740 | -90 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1610 | 1740 | 1740 | -130 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1753 | -1995 | -1995 | -242 | 88 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1733 | -1995 | -1995 | -262 | 87 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1726 | -1995 | -1995 | -269 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1714 | -1995 | -1995 | -281 | 86 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1660 | -1995 | -1995 | -335 | 83 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1655 | -1995 | -1995 | -340 | 83 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1654 | -1995 | -1995 | -341 | 83 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1654 | -1995 | -1995 | -341 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1648 | -1995 | -1995 | -347 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1644 | -1995 | -1995 | -351 | 82 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1644 | -1995 | -1995 | -351 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1644 | -1995 | -1995 | -351 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1642 | -1995 | -1995 | -353 | 82 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1597 | -1995 | -1995 | -398 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -957 | -1248 | -1248 | -291 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -955 | -1248 | -1248 | -293 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -953 | -1248 | -1248 | -295 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -945 | -1248 | -1248 | -304 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -944 | -1248 | -1248 | -304 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -937 | -1248 | -1248 | -311 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1487 | -1995 | -1995 | -508 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1484 | -2000 | -2000 | -516 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1466 | -1995 | -1995 | -529 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1465 | -2000 | -2000 | -535 | 73 | []

## 0330Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3148
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 |  | 1740 | -3 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1721 |  | 1740 | -19 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -987 |  | -999 | -12 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1693 |  | 1740 | -47 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1693 |  | 1740 | -47 | 97 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 |  | 1740 | -62 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 |  | 1740 | -67 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 |  | 1740 | -77 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 |  | 1740 | -81 | 95 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1650 |  | 1740 | -90 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1610 |  | 1740 | -130 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1753 |  | -1995 | -242 | 88 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1733 |  | -1995 | -262 | 87 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1726 |  | -1995 | -269 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1714 |  | -1995 | -281 | 86 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1660 |  | -1995 | -335 | 83 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1655 |  | -1995 | -340 | 83 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1654 |  | -1995 | -341 | 83 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1654 |  | -1995 | -341 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1648 |  | -1995 | -347 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1644 |  | -1995 | -351 | 82 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1644 |  | -1995 | -351 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1644 |  | -1995 | -351 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1642 |  | -1995 | -353 | 82 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1597 |  | -1995 | -398 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -957 |  | -1248 | -291 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -955 |  | -1248 | -293 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -953 |  | -1248 | -295 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -945 |  | -1248 | -304 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -944 |  | -1248 | -304 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -937 |  | -1248 | -311 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1487 |  | -1995 | -508 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1484 |  | -2000 | -516 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1466 |  | -1995 | -529 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1465 |  | -2000 | -535 | 73 | []

## 0430Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3447
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 | 1740 | 1740 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1727 | 1740 | 1740 | -13 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1727 | 1740 | 1740 | -13 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 | 1740 | 1740 | -18 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 | 1740 | 1740 | -48 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 | 1740 | 1740 | -64 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 | 1740 | 1740 | -64 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1669 | 1740 | 1740 | -71 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1665 | 1740 | 1740 | -75 | 96 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -940 | -999 | -999 | -59 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1628 | 1740 | 1740 | -112 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1804 | -1995 | -1995 | -191 | 90 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1798 | -1995 | -1995 | -197 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1791 | -1995 | -1995 | -204 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1783 | -1995 | -1995 | -212 | 89 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1757 | -1995 | -1995 | -238 | 88 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1754 | -1995 | -1995 | -241 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1746 | -1995 | -1995 | -249 | 87 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1745 | -1995 | -1995 | -250 | 87 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1739 | -1995 | -1995 | -256 | 87 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1721 | -1995 | -1995 | -274 | 86 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1715 | -1995 | -1995 | -280 | 86 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1712 | -1995 | -1995 | -283 | 86 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1712 | -1995 | -1995 | -283 | 86 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1686 | -1995 | -1995 | -309 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1654 | -2000 | -2000 | -346 | 83 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1634 | -2000 | -2000 | -366 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -990 | -1248 | -1248 | -259 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -987 | -1248 | -1248 | -262 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -985 | -1248 | -1248 | -263 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -976 | -1248 | -1248 | -272 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -976 | -1248 | -1248 | -272 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -970 | -1248 | -1248 | -279 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1543 | -1995 | -1995 | -452 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1520 | -1995 | -1995 | -475 | 76 | []

## 0430Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3447
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 |  | 1740 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1727 |  | 1740 | -13 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1727 |  | 1740 | -13 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 |  | 1740 | -18 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 |  | 1740 | -48 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 |  | 1740 | -64 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 |  | 1740 | -64 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1669 |  | 1740 | -71 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1665 |  | 1740 | -75 | 96 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -940 |  | -999 | -59 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1628 |  | 1740 | -112 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1804 |  | -1995 | -191 | 90 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1798 |  | -1995 | -197 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1791 |  | -1995 | -204 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1783 |  | -1995 | -212 | 89 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1757 |  | -1995 | -238 | 88 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1754 |  | -1995 | -241 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1746 |  | -1995 | -249 | 87 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1745 |  | -1995 | -250 | 87 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1739 |  | -1995 | -256 | 87 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1721 |  | -1995 | -274 | 86 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1715 |  | -1995 | -280 | 86 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1712 |  | -1995 | -283 | 86 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1712 |  | -1995 | -283 | 86 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1686 |  | -1995 | -309 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1654 |  | -2000 | -346 | 83 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1634 |  | -2000 | -366 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -990 |  | -1248 | -259 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -987 |  | -1248 | -262 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -985 |  | -1248 | -263 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -976 |  | -1248 | -272 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -976 |  | -1248 | -272 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -970 |  | -1248 | -279 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1543 |  | -1995 | -452 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1520 |  | -1995 | -475 | 76 | []

## 0530Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3393
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1739 | 1740 | 1740 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 | 1740 | 1740 | -15 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1719 | 1740 | 1740 | -21 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1719 | 1740 | 1740 | -21 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1690 | 1740 | 1740 | -50 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -965 | -999 | -999 | -34 | 97 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 | 1740 | 1740 | -63 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 | 1740 | 1740 | -66 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1667 | 1740 | 1740 | -73 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 | 1740 | 1740 | -77 | 96 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1623 | 1740 | 1740 | -117 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1790 | -1995 | -1995 | -205 | 90 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1784 | -1995 | -1995 | -211 | 89 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1778 | -1995 | -1995 | -217 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1769 | -1995 | -1995 | -226 | 89 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1736 | -1995 | -1995 | -259 | 87 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1733 | -1995 | -1995 | -262 | 87 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1725 | -1995 | -1995 | -270 | 86 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1725 | -1995 | -1995 | -270 | 86 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1723 | -1995 | -1995 | -272 | 86 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1705 | -1995 | -1995 | -290 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1703 | -1995 | -1995 | -292 | 85 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1696 | -1995 | -1995 | -299 | 85 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1692 | -1995 | -1995 | -303 | 85 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1668 | -1995 | -1995 | -327 | 84 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1622 | -2000 | -2000 | -378 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1602 | -2000 | -2000 | -398 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -975 | -1248 | -1248 | -274 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -972 | -1248 | -1248 | -277 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -970 | -1248 | -1248 | -278 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -961 | -1248 | -1248 | -288 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -961 | -1248 | -1248 | -288 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1531 | -1995 | -1995 | -464 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -954 | -1248 | -1248 | -294 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1509 | -1995 | -1995 | -486 | 76 | []

## 0530Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3393
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1739 |  | 1740 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 |  | 1740 | -15 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1719 |  | 1740 | -21 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1719 |  | 1740 | -21 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1690 |  | 1740 | -50 | 97 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -965 |  | -999 | -34 | 97 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 |  | 1740 | -63 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 |  | 1740 | -66 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1667 |  | 1740 | -73 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 |  | 1740 | -77 | 96 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1623 |  | 1740 | -117 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1790 |  | -1995 | -205 | 90 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1784 |  | -1995 | -211 | 89 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1778 |  | -1995 | -217 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1769 |  | -1995 | -226 | 89 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1736 |  | -1995 | -259 | 87 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1733 |  | -1995 | -262 | 87 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1725 |  | -1995 | -270 | 86 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1725 |  | -1995 | -270 | 86 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1723 |  | -1995 | -272 | 86 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1705 |  | -1995 | -290 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1703 |  | -1995 | -292 | 85 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1696 |  | -1995 | -299 | 85 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1692 |  | -1995 | -303 | 85 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1668 |  | -1995 | -327 | 84 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1622 |  | -2000 | -378 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1602 |  | -2000 | -398 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -975 |  | -1248 | -274 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -972 |  | -1248 | -277 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -970 |  | -1248 | -278 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -961 |  | -1248 | -288 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -961 |  | -1248 | -288 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1531 |  | -1995 | -464 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -954 |  | -1248 | -294 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1509 |  | -1995 | -486 | 76 | []

## 0630Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2637
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1739 | 1740 | 1740 | -1 | 100 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 | 1740 | 1740 | -10 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1727 | 1740 | 1740 | -13 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 | 1740 | 1740 | -18 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1689 | 1740 | 1740 | -51 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1689 | 1740 | 1740 | -51 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 | 1740 | 1740 | -62 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1671 | 1740 | 1740 | -69 | 96 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1629 | 1740 | 1740 | -111 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1629 | 1740 | 1740 | -111 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1642 | -1995 | -1995 | -353 | 82 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1636 | -1995 | -1995 | -359 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1006 | -1248 | -1248 | -243 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1002 | -1248 | -1248 | -246 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1001 | -1248 | -1248 | -247 | 80 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1598 | -1995 | -1995 | -397 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1589 | -1995 | -1995 | -406 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -992 | -1248 | -1248 | -256 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -992 | -1248 | -1248 | -257 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -986 | -1248 | -1248 | -263 | 79 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1504 | -1995 | -1995 | -491 | 75 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1497 | -1995 | -1995 | -498 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1497 | -1995 | -1995 | -498 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1495 | -1995 | -1995 | -500 | 75 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1477 | -1995 | -1995 | -518 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1472 | -1995 | -1995 | -523 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1453 | -1995 | -1995 | -542 | 73 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1452 | -1995 | -1995 | -543 | 73 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1451 | -1995 | -1995 | -544 | 73 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1444 | -1995 | -1995 | -551 | 72 | []

## 0630Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2637
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1739 |  | 1740 | -1 | 100 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 |  | 1740 | -10 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1727 |  | 1740 | -13 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 |  | 1740 | -18 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1689 |  | 1740 | -51 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1689 |  | 1740 | -51 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 |  | 1740 | -62 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1671 |  | 1740 | -69 | 96 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1629 |  | 1740 | -111 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1629 |  | 1740 | -111 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1642 |  | -1995 | -353 | 82 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1636 |  | -1995 | -359 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1006 |  | -1248 | -243 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1002 |  | -1248 | -246 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1001 |  | -1248 | -247 | 80 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1598 |  | -1995 | -397 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1589 |  | -1995 | -406 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -992 |  | -1248 | -256 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -992 |  | -1248 | -257 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -986 |  | -1248 | -263 | 79 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1504 |  | -1995 | -491 | 75 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1497 |  | -1995 | -498 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1497 |  | -1995 | -498 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1495 |  | -1995 | -500 | 75 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1477 |  | -1995 | -518 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1472 |  | -1995 | -523 | 74 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1453 |  | -1995 | -542 | 73 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1452 |  | -1995 | -543 | 73 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1451 |  | -1995 | -544 | 73 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1444 |  | -1995 | -551 | 72 | []

## 0730Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2278
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1736 | 1740 | 1740 | -4 | 100 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 | 1740 | 1740 | -29 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 | 1740 | 1740 | -35 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1697 | 1740 | 1740 | -43 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 | 1740 | 1740 | -64 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1631 | 1740 | 1740 | -109 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1631 | 1740 | 1740 | -109 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1611 | 1740 | 1740 | -129 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 | 1740 | 1740 | -149 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 | 1740 | 1740 | -149 | 91 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -977 | -1248 | -1248 | -272 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -974 | -1248 | -1248 | -275 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -972 | -1248 | -1248 | -276 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1548 | -1995 | -1995 | -447 | 78 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1543 | -1995 | -1995 | -452 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -964 | -1248 | -1248 | -285 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -963 | -1248 | -1248 | -285 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -957 | -1248 | -1248 | -291 | 77 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1484 | -1995 | -1995 | -511 | 74 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1480 | -1995 | -1995 | -515 | 74 | []

## 0730Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2278
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1736 |  | 1740 | -4 | 100 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 |  | 1740 | -29 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 |  | 1740 | -35 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1697 |  | 1740 | -43 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 |  | 1740 | -64 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1631 |  | 1740 | -109 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1631 |  | 1740 | -109 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1611 |  | 1740 | -129 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 |  | 1740 | -149 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1591 |  | 1740 | -149 | 91 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -977 |  | -1248 | -272 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -974 |  | -1248 | -275 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -972 |  | -1248 | -276 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1548 |  | -1995 | -447 | 78 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1543 |  | -1995 | -452 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -964 |  | -1248 | -285 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -963 |  | -1248 | -285 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -957 |  | -1248 | -291 | 77 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1484 |  | -1995 | -511 | 74 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1480 |  | -1995 | -515 | 74 | []

## 0830Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1986
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1734 | 1740 | 1740 | -6 | 100 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 | 1740 | 1740 | -18 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 | 1740 | 1740 | -40 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 | 1740 | 1740 | -48 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 | 1740 | 1740 | -77 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1608 | 1740 | 1740 | -132 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1608 | 1740 | 1740 | -132 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1601 | 1740 | 1740 | -139 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1583 | 1740 | 1740 | -157 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1583 | 1740 | 1740 | -157 | 91 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -957 | -1248 | -1248 | -292 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -953 | -1248 | -1248 | -295 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -952 | -1248 | -1248 | -296 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -943 | -1248 | -1248 | -305 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -943 | -1248 | -1248 | -306 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -937 | -1248 | -1248 | -312 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1488 | -1995 | -1995 | -507 | 75 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-UA] Rosiori-Mukacevo [DIR] [RO] | RROSI41 _XRO_MU11_1:line | 1288 | 1740 | 1740 | -452 | 74 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1470 | -1995 | -1995 | -525 | 74 | []

## 0830Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1986
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1734 |  | 1740 | -6 | 100 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 |  | 1740 | -18 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 |  | 1740 | -40 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 |  | 1740 | -48 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1663 |  | 1740 | -77 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1608 |  | 1740 | -132 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1608 |  | 1740 | -132 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1601 |  | 1740 | -139 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1583 |  | 1740 | -157 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1583 |  | 1740 | -157 | 91 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -957 |  | -1248 | -292 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -953 |  | -1248 | -295 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -952 |  | -1248 | -296 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -943 |  | -1248 | -305 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -943 |  | -1248 | -306 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -937 |  | -1248 | -312 | 75 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1488 |  | -1995 | -507 | 75 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-UA] Rosiori-Mukacevo [DIR] [RO] | RROSI41 _XRO_MU11_1:line | 1288 |  | 1740 | -452 | 74 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1470 |  | -1995 | -525 | 74 | []

## 0930Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1969
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 | 1740 | 1740 | -3 | 100 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 | 1740 | 1740 | -3 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 | 1740 | 1740 | -10 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1721 | 1740 | 1740 | -19 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 | 1740 | 1740 | -67 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1621 | 1740 | 1740 | -119 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1621 | 1740 | 1740 | -119 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1615 | 1740 | 1740 | -125 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 | 1740 | 1740 | -140 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 | 1740 | 1740 | -140 | 92 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -921 | -1248 | -1248 | -328 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -917 | -1248 | -1248 | -331 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -916 | -1248 | -1248 | -332 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -907 | -1248 | -1248 | -341 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -907 | -1248 | -1248 | -341 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -901 | -1248 | -1248 | -347 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1430 | -1995 | -1995 | -565 | 72 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1429 | -1995 | -1995 | -566 | 72 | []

## 0930Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1969
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 |  | 1740 | -3 | 100 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 |  | 1740 | -3 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 |  | 1740 | -10 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1721 |  | 1740 | -19 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 |  | 1740 | -67 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1621 |  | 1740 | -119 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1621 |  | 1740 | -119 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1615 |  | 1740 | -125 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 |  | 1740 | -140 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 |  | 1740 | -140 | 92 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -921 |  | -1248 | -328 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -917 |  | -1248 | -331 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -916 |  | -1248 | -332 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -907 |  | -1248 | -341 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -907 |  | -1248 | -341 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -901 |  | -1248 | -347 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1430 |  | -1995 | -565 | 72 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1429 |  | -1995 | -566 | 72 | []

## 1030Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1993
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1738 | 1740 | 1740 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1729 | 1740 | 1740 | -11 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1728 | 1740 | 1740 | -12 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1727 | 1740 | 1740 | -13 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 | 1740 | 1740 | -66 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1617 | 1740 | 1740 | -123 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1617 | 1740 | 1740 | -123 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1615 | 1740 | 1740 | -125 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 | 1740 | 1740 | -137 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 | 1740 | 1740 | -137 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1526 | -1995 | -1995 | -469 | 77 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1520 | -1995 | -1995 | -475 | 76 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1452 | -1995 | -1995 | -543 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -907 | -1248 | -1248 | -341 | 73 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1450 | -1995 | -1995 | -545 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -904 | -1248 | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -894 | -1248 | -1248 | -355 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -894 | -1248 | -1248 | -355 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -888 | -1248 | -1248 | -361 | 71 | []

## 1030Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1993
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1738 |  | 1740 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1729 |  | 1740 | -11 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1728 |  | 1740 | -12 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1727 |  | 1740 | -13 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1674 |  | 1740 | -66 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1617 |  | 1740 | -123 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1617 |  | 1740 | -123 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1615 |  | 1740 | -125 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 |  | 1740 | -137 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 |  | 1740 | -137 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1526 |  | -1995 | -469 | 77 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1520 |  | -1995 | -475 | 76 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1452 |  | -1995 | -543 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -907 |  | -1248 | -341 | 73 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1450 |  | -1995 | -545 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -904 |  | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -894 |  | -1248 | -355 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -894 |  | -1248 | -355 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -888 |  | -1248 | -361 | 71 | []

## 1130Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1814
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1738 | 1740 | 1740 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 | 1740 | 1740 | -10 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 | 1740 | 1740 | -35 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 | 1740 | 1740 | -36 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1665 | 1740 | 1740 | -75 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1608 | 1740 | 1740 | -132 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 | 1740 | 1740 | -137 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 | 1740 | 1740 | -137 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1598 | 1740 | 1740 | -142 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1598 | 1740 | 1740 | -142 | 92 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -890 | -1248 | -1248 | -359 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -886 | -1248 | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -885 | -1248 | -1248 | -363 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -876 | -1248 | -1248 | -372 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -876 | -1248 | -1248 | -373 | 70 | []

## 1130Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1814
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1738 |  | 1740 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 |  | 1740 | -10 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 |  | 1740 | -35 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 |  | 1740 | -36 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1665 |  | 1740 | -75 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1608 |  | 1740 | -132 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 |  | 1740 | -137 | 92 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 |  | 1740 | -137 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1598 |  | 1740 | -142 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1598 |  | 1740 | -142 | 92 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -890 |  | -1248 | -359 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -886 |  | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -885 |  | -1248 | -363 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -876 |  | -1248 | -372 | 70 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -876 |  | -1248 | -373 | 70 | []

## 1230Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1877
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1723 | 1740 | 1740 | -17 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 | 1740 | 1740 | -29 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 | 1740 | 1740 | -53 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 | 1740 | 1740 | -70 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1640 | 1740 | 1740 | -100 | 94 | []
RO_CO_00005 | N-1 Tantareni-Urechesti | [RO-RO] AT Urechesti [OPP] [RO] | RURE241 _RURE212 _1:trf | -921 | -999 | -999 | -79 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1593 | 1740 | 1740 | -147 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1589 | 1740 | 1740 | -151 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1589 | 1740 | 1740 | -151 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1584 | 1740 | 1740 | -156 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1584 | 1740 | 1740 | -156 | 91 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -907 | -1248 | -1248 | -341 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -904 | -1248 | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -346 | 72 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1434 | -1995 | -1995 | -561 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -894 | -1248 | -1248 | -355 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -894 | -1248 | -1248 | -355 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1427 | -1995 | -1995 | -568 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -888 | -1248 | -1248 | -361 | 71 | []

## 1230Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1877
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1723 |  | 1740 | -17 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 |  | 1740 | -29 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 |  | 1740 | -53 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 |  | 1740 | -70 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1640 |  | 1740 | -100 | 94 | []
RO_CO_00005 | N-1 Tantareni-Urechesti | [RO-RO] AT Urechesti [OPP] [RO] | RURE241 _RURE212 _1:trf | -921 |  | -999 | -79 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1593 |  | 1740 | -147 | 92 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1589 |  | 1740 | -151 | 91 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1589 |  | 1740 | -151 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1584 |  | 1740 | -156 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1584 |  | 1740 | -156 | 91 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -907 |  | -1248 | -341 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -904 |  | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -346 | 72 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1434 |  | -1995 | -561 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -894 |  | -1248 | -355 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -894 |  | -1248 | -355 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1427 |  | -1995 | -568 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -888 |  | -1248 | -361 | 71 | []

## 1330Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1987
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1738 | 1740 | 1740 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1729 | 1740 | 1740 | -11 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 | 1740 | 1740 | -34 | 98 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 | 1740 | 1740 | -48 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 | 1740 | 1740 | -74 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 | 1740 | 1740 | -106 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 | 1740 | 1740 | -106 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1619 | 1740 | 1740 | -121 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1611 | 1740 | 1740 | -129 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1611 | 1740 | 1740 | -129 | 93 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -925 | -1248 | -1248 | -324 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -921 | -1248 | -1248 | -327 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -920 | -1248 | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -911 | -1248 | -1248 | -337 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -911 | -1248 | -1248 | -337 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -905 | -1248 | -1248 | -343 | 72 | []

## 1330Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1987
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1738 |  | 1740 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1729 |  | 1740 | -11 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 |  | 1740 | -34 | 98 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 |  | 1740 | -48 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 |  | 1740 | -74 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 |  | 1740 | -106 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 |  | 1740 | -106 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1619 |  | 1740 | -121 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1611 |  | 1740 | -129 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1611 |  | 1740 | -129 | 93 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -925 |  | -1248 | -324 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -921 |  | -1248 | -327 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -920 |  | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -911 |  | -1248 | -337 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -911 |  | -1248 | -337 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -905 |  | -1248 | -343 | 72 | []

## 1430Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2008
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 | 1740 | 1740 | -3 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1729 | 1740 | 1740 | -11 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1709 | 1740 | 1740 | -31 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1703 | 1740 | 1740 | -37 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1675 | 1740 | 1740 | -65 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 | 1740 | 1740 | -106 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 | 1740 | 1740 | -106 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1620 | 1740 | 1740 | -120 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1612 | 1740 | 1740 | -128 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1612 | 1740 | 1740 | -128 | 93 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -933 | -1248 | -1248 | -316 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -929 | -1248 | -1248 | -319 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -928 | -1248 | -1248 | -320 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -919 | -1248 | -1248 | -330 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -919 | -1248 | -1248 | -330 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -913 | -1248 | -1248 | -336 | 73 | []

## 1430Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2008
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 |  | 1740 | -3 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1729 |  | 1740 | -11 | 99 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1709 |  | 1740 | -31 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1703 |  | 1740 | -37 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1675 |  | 1740 | -65 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 |  | 1740 | -106 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 |  | 1740 | -106 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1620 |  | 1740 | -120 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1612 |  | 1740 | -128 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1612 |  | 1740 | -128 | 93 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -933 |  | -1248 | -316 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -929 |  | -1248 | -319 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -928 |  | -1248 | -320 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -919 |  | -1248 | -330 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -919 |  | -1248 | -330 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -913 |  | -1248 | -336 | 73 | []

## 1530Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2439
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1732 | 1740 | 1740 | -8 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 | 1740 | 1740 | -10 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1720 | 1740 | 1740 | -20 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 | 1740 | 1740 | -36 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 | 1740 | 1740 | -56 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 | 1740 | 1740 | -67 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 | 1740 | 1740 | -67 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1637 | 1740 | 1740 | -103 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 | 1740 | 1740 | -113 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 | 1740 | 1740 | -113 | 94 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -980 | -1248 | -1248 | -268 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -977 | -1248 | -1248 | -271 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -976 | -1248 | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -967 | -1248 | -1248 | -282 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -967 | -1248 | -1248 | -282 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -960 | -1248 | -1248 | -288 | 77 | []

## 1530Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2439
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1732 |  | 1740 | -8 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 |  | 1740 | -10 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1720 |  | 1740 | -20 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 |  | 1740 | -36 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 |  | 1740 | -56 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 |  | 1740 | -67 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 |  | 1740 | -67 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1637 |  | 1740 | -103 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 |  | 1740 | -113 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1627 |  | 1740 | -113 | 94 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -980 |  | -1248 | -268 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -977 |  | -1248 | -271 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -976 |  | -1248 | -273 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -967 |  | -1248 | -282 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -967 |  | -1248 | -282 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -960 |  | -1248 | -288 | 77 | []

## 1630Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3025
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1739 | 1740 | 1740 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1718 | 1740 | 1740 | -22 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1708 | 1740 | 1740 | -32 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1708 | 1740 | 1740 | -32 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1703 | 1740 | 1740 | -37 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1702 | 1740 | 1740 | -38 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 | 1740 | 1740 | -53 | 97 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1645 | 1740 | 1740 | -95 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1635 | 1740 | 1740 | -105 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1635 | 1740 | 1740 | -105 | 94 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1738 | -1995 | -1995 | -257 | 87 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1041 | -1248 | -1248 | -207 | 83 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1660 | -1995 | -1995 | -335 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1038 | -1248 | -1248 | -210 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1036 | -1248 | -1248 | -212 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1028 | -1248 | -1248 | -221 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1027 | -1248 | -1248 | -221 | 82 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1641 | -1995 | -1995 | -354 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1021 | -1248 | -1248 | -227 | 82 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1619 | -1995 | -1995 | -376 | 81 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1615 | -1995 | -1995 | -380 | 81 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1610 | -1995 | -1995 | -385 | 81 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1610 | -1995 | -1995 | -385 | 81 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1610 | -1995 | -1995 | -385 | 81 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1608 | -1995 | -1995 | -387 | 81 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1605 | -1995 | -1995 | -390 | 80 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1604 | -1995 | -1995 | -391 | 80 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1599 | -1995 | -1995 | -396 | 80 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1593 | -1995 | -1995 | -402 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1586 | -1995 | -1995 | -409 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1422 | -2000 | -2000 | -578 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1406 | -2000 | -2000 | -594 | 70 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1400 | 1995 | 1995 | -595 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3025
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1739 |  | 1740 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1718 |  | 1740 | -22 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1708 |  | 1740 | -32 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1708 |  | 1740 | -32 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1703 |  | 1740 | -37 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1702 |  | 1740 | -38 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1687 |  | 1740 | -53 | 97 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1645 |  | 1740 | -95 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1635 |  | 1740 | -105 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1635 |  | 1740 | -105 | 94 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1738 |  | -1995 | -257 | 87 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1041 |  | -1248 | -207 | 83 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1660 |  | -1995 | -335 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1038 |  | -1248 | -210 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1036 |  | -1248 | -212 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1028 |  | -1248 | -221 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1027 |  | -1248 | -221 | 82 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1641 |  | -1995 | -354 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1021 |  | -1248 | -227 | 82 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1619 |  | -1995 | -376 | 81 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1615 |  | -1995 | -380 | 81 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1610 |  | -1995 | -385 | 81 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1610 |  | -1995 | -385 | 81 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1610 |  | -1995 | -385 | 81 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1608 |  | -1995 | -387 | 81 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1605 |  | -1995 | -390 | 80 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1604 |  | -1995 | -391 | 80 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1599 |  | -1995 | -396 | 80 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1593 |  | -1995 | -402 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1586 |  | -1995 | -409 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1422 |  | -2000 | -578 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1406 |  | -2000 | -594 | 70 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1400 |  | 1995 | -595 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3386
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1991 | 1995 | 1995 | -4 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1736 | 1740 | 1740 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 | 1740 | 1740 | -10 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 | 1740 | 1740 | -10 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1716 | 1740 | 1740 | -24 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1706 | -1740 | -1740 | -34 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 | 1740 | 1740 | -48 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1664 | 1740 | 1740 | -76 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 | 1740 | 1740 | -81 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1630 | 1740 | 1740 | -110 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1630 | 1740 | 1740 | -110 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1866 | 1995 | 1995 | -129 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1846 | 1995 | 1995 | -149 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1826 | 1995 | 1995 | -169 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1822 | 1995 | 1995 | -173 | 91 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1816 | 1995 | 1995 | -179 | 91 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1816 | 1995 | 1995 | -179 | 91 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1816 | 1995 | 1995 | -179 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1810 | 1995 | 1995 | -185 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1810 | 1995 | 1995 | -185 | 91 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1797 | 1995 | 1995 | -198 | 90 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1788 | 1995 | 1995 | -207 | 90 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1784 | 1995 | 1995 | -211 | 89 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1777 | 1995 | 1995 | -218 | 89 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1013 | -1248 | -1248 | -235 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1619 | -2000 | -2000 | -381 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1010 | -1248 | -1248 | -239 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1009 | -1248 | -1248 | -240 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1600 | -2000 | -2000 | -400 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -999 | -1248 | -1248 | -249 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -999 | -1248 | -1248 | -250 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -992 | -1248 | -1248 | -256 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1581 | 1995 | 1995 | -414 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1361 | -1740 | -1740 | -379 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1560 | 1995 | 1995 | -435 | 78 | []

## 1730Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3386
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1991 |  | 1995 | -4 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1736 |  | 1740 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 |  | 1740 | -10 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 |  | 1740 | -10 | 99 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1716 |  | 1740 | -24 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1706 |  | -1740 | -34 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 |  | 1740 | -48 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1664 |  | 1740 | -76 | 96 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 |  | 1740 | -81 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1630 |  | 1740 | -110 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1630 |  | 1740 | -110 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1866 |  | 1995 | -129 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1846 |  | 1995 | -149 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1826 |  | 1995 | -169 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1822 |  | 1995 | -173 | 91 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1816 |  | 1995 | -179 | 91 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1816 |  | 1995 | -179 | 91 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1816 |  | 1995 | -179 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1810 |  | 1995 | -185 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1810 |  | 1995 | -185 | 91 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1797 |  | 1995 | -198 | 90 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1788 |  | 1995 | -207 | 90 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1784 |  | 1995 | -211 | 89 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1777 |  | 1995 | -218 | 89 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1013 |  | -1248 | -235 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1619 |  | -2000 | -381 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1010 |  | -1248 | -239 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1009 |  | -1248 | -240 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1600 |  | -2000 | -400 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -999 |  | -1248 | -249 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -999 |  | -1248 | -250 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -992 |  | -1248 | -256 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1581 |  | 1995 | -414 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1361 |  | -1740 | -379 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1560 |  | 1995 | -435 | 78 | []

## 1830Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3364
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1738 | -1740 | -1740 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1717 | -1740 | -1740 | -23 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1713 | -1740 | -1740 | -27 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1713 | -1740 | -1740 | -27 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1707 | -1740 | -1740 | -33 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1691 | -1740 | -1740 | -49 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1657 | -1740 | -1740 | -83 | 95 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1654 | -1740 | -1740 | -86 | 95 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1886 | -1995 | -1995 | -109 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1879 | -1995 | -1995 | -116 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1879 | -1995 | -1995 | -116 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1865 | -1995 | -1995 | -130 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1619 | -1740 | -1740 | -121 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1619 | -1740 | -1740 | -121 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1852 | -1995 | -1995 | -143 | 93 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1828 | -1995 | -1995 | -167 | 92 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1818 | -1995 | -1995 | -177 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1809 | -1995 | -1995 | -186 | 91 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1807 | -1995 | -1995 | -188 | 91 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1807 | -1995 | -1995 | -188 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1806 | -1995 | -1995 | -189 | 91 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1784 | -1995 | -1995 | -211 | 89 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1775 | -1995 | -1995 | -220 | 89 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1773 | -1995 | -1995 | -222 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1651 | -2000 | -2000 | -349 | 83 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1633 | -2000 | -2000 | -367 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1013 | -1248 | -1248 | -235 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1010 | -1248 | -1248 | -239 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1612 | 1995 | 1995 | -383 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1009 | -1248 | -1248 | -240 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -999 | -1248 | -1248 | -249 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -999 | -1248 | -1248 | -250 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1586 | -1995 | -1995 | -409 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -992 | -1248 | -1248 | -256 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1357 | -1740 | -1740 | -383 | 78 | []

## 1830Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3364
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1738 |  | -1740 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1717 |  | -1740 | -23 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1713 |  | -1740 | -27 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1713 |  | -1740 | -27 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1707 |  | -1740 | -33 | 98 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1691 |  | -1740 | -49 | 97 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1657 |  | -1740 | -83 | 95 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1654 |  | -1740 | -86 | 95 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1886 |  | -1995 | -109 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1879 |  | -1995 | -116 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1879 |  | -1995 | -116 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1865 |  | -1995 | -130 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1619 |  | -1740 | -121 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1619 |  | -1740 | -121 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1852 |  | -1995 | -143 | 93 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1828 |  | -1995 | -167 | 92 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1818 |  | -1995 | -177 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1809 |  | -1995 | -186 | 91 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1807 |  | -1995 | -188 | 91 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1807 |  | -1995 | -188 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1806 |  | -1995 | -189 | 91 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1784 |  | -1995 | -211 | 89 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1775 |  | -1995 | -220 | 89 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1773 |  | -1995 | -222 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1651 |  | -2000 | -349 | 83 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1633 |  | -2000 | -367 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1013 |  | -1248 | -235 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1010 |  | -1248 | -239 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1612 |  | 1995 | -383 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1009 |  | -1248 | -240 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -999 |  | -1248 | -249 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -999 |  | -1248 | -250 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1586 |  | -1995 | -409 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -992 |  | -1248 | -256 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1357 |  | -1740 | -383 | 78 | []

## 1930Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3339
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1900 | -1995 | -1995 | -95 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1882 | -1995 | -1995 | -113 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1877 | -1995 | -1995 | -118 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1873 | -1995 | -1995 | -122 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1629 | -1740 | -1740 | -111 | 94 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1618 | -1740 | -1740 | -122 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1618 | -1740 | -1740 | -122 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1610 | -1740 | -1740 | -130 | 93 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1831 | -1995 | -1995 | -164 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1594 | -1740 | -1740 | -146 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1828 | -1995 | -1995 | -167 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1592 | -1740 | -1740 | -148 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1815 | -1995 | -1995 | -180 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1813 | -1995 | -1995 | -182 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1810 | -1995 | -1995 | -185 | 91 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1796 | -1995 | -1995 | -199 | 90 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1560 | -1740 | -1740 | -180 | 90 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1558 | -1740 | -1740 | -182 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1777 | -1995 | -1995 | -218 | 89 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1767 | -1995 | -1995 | -228 | 89 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1763 | -1995 | -1995 | -232 | 88 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1753 | -1995 | -1995 | -242 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1526 | -1740 | -1740 | -214 | 88 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1526 | -1740 | -1740 | -214 | 88 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1724 | -2000 | -2000 | -276 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1705 | -2000 | -2000 | -295 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1034 | -1248 | -1248 | -214 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1032 | -1248 | -1248 | -216 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1030 | -1248 | -1248 | -219 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1023 | -1248 | -1248 | -226 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1021 | -1248 | -1248 | -227 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1016 | -1248 | -1248 | -232 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1613 | -1995 | -1995 | -382 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1591 | -1995 | -1995 | -404 | 80 | []

## 1930Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3339
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1900 |  | -1995 | -95 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1882 |  | -1995 | -113 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1877 |  | -1995 | -118 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1873 |  | -1995 | -122 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1629 |  | -1740 | -111 | 94 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1618 |  | -1740 | -122 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1618 |  | -1740 | -122 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1610 |  | -1740 | -130 | 93 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1831 |  | -1995 | -164 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1594 |  | -1740 | -146 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1828 |  | -1995 | -167 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1592 |  | -1740 | -148 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1815 |  | -1995 | -180 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1813 |  | -1995 | -182 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1810 |  | -1995 | -185 | 91 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1796 |  | -1995 | -199 | 90 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1560 |  | -1740 | -180 | 90 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1558 |  | -1740 | -182 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1777 |  | -1995 | -218 | 89 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1767 |  | -1995 | -228 | 89 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1763 |  | -1995 | -232 | 88 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1753 |  | -1995 | -242 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1526 |  | -1740 | -214 | 88 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1526 |  | -1740 | -214 | 88 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1724 |  | -2000 | -276 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1705 |  | -2000 | -295 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1034 |  | -1248 | -214 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1032 |  | -1248 | -216 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1030 |  | -1248 | -219 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1023 |  | -1248 | -226 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1021 |  | -1248 | -227 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1016 |  | -1248 | -232 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1613 |  | -1995 | -382 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1591 |  | -1995 | -404 | 80 | []

## 2030Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3374
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1668 | -1740 | -1740 | -72 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1663 | -1740 | -1740 | -77 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1663 | -1740 | -1740 | -77 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1650 | -1740 | -1740 | -90 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1890 | -1995 | -1995 | -105 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1634 | -1740 | -1740 | -106 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1872 | -1995 | -1995 | -123 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1871 | -1995 | -1995 | -124 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1631 | -1740 | -1740 | -109 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1864 | -1995 | -1995 | -131 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1605 | -1740 | -1740 | -135 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1604 | -1740 | -1740 | -136 | 92 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1826 | -1995 | -1995 | -169 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1822 | -1995 | -1995 | -173 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1809 | -1995 | -1995 | -186 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1809 | -1995 | -1995 | -186 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1807 | -1995 | -1995 | -188 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1572 | -1740 | -1740 | -168 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1572 | -1740 | -1740 | -168 | 90 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1790 | -1995 | -1995 | -205 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1772 | -1995 | -1995 | -223 | 89 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1762 | -1995 | -1995 | -233 | 88 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1758 | -1995 | -1995 | -237 | 88 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1748 | -1995 | -1995 | -247 | 88 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1720 | -2000 | -2000 | -280 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1702 | -2000 | -2000 | -298 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1044 | -1248 | -1248 | -205 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1041 | -1248 | -1248 | -207 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1039 | -1248 | -1248 | -209 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1032 | -1248 | -1248 | -217 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1030 | -1248 | -1248 | -218 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1025 | -1248 | -1248 | -223 | 82 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1606 | -1995 | -1995 | -389 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1585 | -1995 | -1995 | -410 | 79 | []

## 2030Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3374
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1668 |  | -1740 | -72 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1663 |  | -1740 | -77 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1663 |  | -1740 | -77 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1650 |  | -1740 | -90 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1890 |  | -1995 | -105 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1634 |  | -1740 | -106 | 94 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1872 |  | -1995 | -123 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1871 |  | -1995 | -124 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1631 |  | -1740 | -109 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1864 |  | -1995 | -131 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1605 |  | -1740 | -135 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1604 |  | -1740 | -136 | 92 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1826 |  | -1995 | -169 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1822 |  | -1995 | -173 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1809 |  | -1995 | -186 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1809 |  | -1995 | -186 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1807 |  | -1995 | -188 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1572 |  | -1740 | -168 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1572 |  | -1740 | -168 | 90 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1790 |  | -1995 | -205 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1772 |  | -1995 | -223 | 89 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1762 |  | -1995 | -233 | 88 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1758 |  | -1995 | -237 | 88 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1748 |  | -1995 | -247 | 88 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1720 |  | -2000 | -280 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1702 |  | -2000 | -298 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1044 |  | -1248 | -205 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1041 |  | -1248 | -207 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1039 |  | -1248 | -209 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1032 |  | -1248 | -217 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1030 |  | -1248 | -218 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1025 |  | -1248 | -223 | 82 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1606 |  | -1995 | -389 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1585 |  | -1995 | -410 | 79 | []

## 2130Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3416
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1699 | -1740 | -1740 | -41 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1694 | -1740 | -1740 | -46 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1694 | -1740 | -1740 | -46 | 97 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1679 | -1740 | -1740 | -61 | 97 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1924 | -1995 | -1995 | -71 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1676 | -1740 | -1740 | -64 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1670 | -1740 | -1740 | -70 | 96 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1908 | -1995 | -1995 | -87 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1907 | -1995 | -1995 | -88 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1900 | -1995 | -1995 | -95 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1638 | -1740 | -1740 | -102 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1635 | -1740 | -1740 | -105 | 94 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1851 | -1995 | -1995 | -144 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1847 | -1995 | -1995 | -148 | 93 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1842 | -1995 | -1995 | -153 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1601 | -1740 | -1740 | -139 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1601 | -1740 | -1740 | -139 | 92 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1834 | -1995 | -1995 | -161 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1833 | -1995 | -1995 | -162 | 92 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1821 | -1995 | -1995 | -174 | 91 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1796 | -1995 | -1995 | -199 | 90 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1788 | -1995 | -1995 | -207 | 90 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1785 | -1995 | -1995 | -210 | 89 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1772 | -1995 | -1995 | -223 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1724 | -2000 | -2000 | -276 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1706 | -2000 | -2000 | -294 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1043 | -1248 | -1248 | -205 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1040 | -1248 | -1248 | -208 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1039 | -1248 | -1248 | -210 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1031 | -1248 | -1248 | -218 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1029 | -1248 | -1248 | -219 | 82 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1637 | -1995 | -1995 | -358 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1024 | -1248 | -1248 | -225 | 82 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1615 | -1995 | -1995 | -380 | 81 | []

## 2130Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3416
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1699 |  | -1740 | -41 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1694 |  | -1740 | -46 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1694 |  | -1740 | -46 | 97 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1679 |  | -1740 | -61 | 97 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1924 |  | -1995 | -71 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1676 |  | -1740 | -64 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1670 |  | -1740 | -70 | 96 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1908 |  | -1995 | -87 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1907 |  | -1995 | -88 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1900 |  | -1995 | -95 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1638 |  | -1740 | -102 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1635 |  | -1740 | -105 | 94 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1851 |  | -1995 | -144 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1847 |  | -1995 | -148 | 93 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1842 |  | -1995 | -153 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1601 |  | -1740 | -139 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1601 |  | -1740 | -139 | 92 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1834 |  | -1995 | -161 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1833 |  | -1995 | -162 | 92 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1821 |  | -1995 | -174 | 91 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1796 |  | -1995 | -199 | 90 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1788 |  | -1995 | -207 | 90 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1785 |  | -1995 | -210 | 89 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1772 |  | -1995 | -223 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1724 |  | -2000 | -276 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1706 |  | -2000 | -294 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1043 |  | -1248 | -205 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1040 |  | -1248 | -208 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1039 |  | -1248 | -210 | 83 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1031 |  | -1248 | -218 | 83 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1029 |  | -1248 | -219 | 82 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1637 |  | -1995 | -358 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1024 |  | -1248 | -225 | 82 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1615 |  | -1995 | -380 | 81 | []

## 2230Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3541
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1905 | -1995 | -1995 | -90 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1654 | 1740 | 1740 | -86 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1654 | 1740 | 1740 | -86 | 95 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1888 | -1995 | -1995 | -107 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1884 | -1995 | -1995 | -111 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1882 | -1995 | -1995 | -113 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1633 | 1740 | 1740 | -107 | 94 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1870 | -1995 | -1995 | -125 | 94 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1866 | -1995 | -1995 | -129 | 94 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1853 | -1995 | -1995 | -142 | 93 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1850 | -1995 | -1995 | -145 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1613 | 1740 | 1740 | -127 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1607 | 1740 | 1740 | -133 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1604 | 1740 | 1740 | -136 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1837 | -1995 | -1995 | -158 | 92 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1817 | -1995 | -1995 | -178 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1582 | 1740 | 1740 | -158 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1581 | 1740 | 1740 | -159 | 91 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1809 | -2000 | -2000 | -191 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1800 | -1995 | -1995 | -195 | 90 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1792 | -1995 | -1995 | -203 | 90 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1788 | -1995 | -1995 | -207 | 90 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1789 | -2000 | -2000 | -211 | 89 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1784 | -1995 | -1995 | -211 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1549 | 1740 | 1740 | -191 | 89 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1549 | 1740 | 1740 | -191 | 89 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1055 | -1248 | -1248 | -193 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1053 | -1248 | -1248 | -196 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1051 | -1248 | -1248 | -198 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1043 | -1248 | -1248 | -205 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1042 | -1248 | -1248 | -207 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1037 | -1248 | -1248 | -212 | 83 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1625 | 1995 | 1995 | -370 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1601 | -1995 | -1995 | -394 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1224 | -1740 | -1740 | -516 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3541
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1905 |  | -1995 | -90 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1654 |  | 1740 | -86 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1654 |  | 1740 | -86 | 95 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1888 |  | -1995 | -107 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1884 |  | -1995 | -111 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1882 |  | -1995 | -113 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1633 |  | 1740 | -107 | 94 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1870 |  | -1995 | -125 | 94 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1866 |  | -1995 | -129 | 94 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1853 |  | -1995 | -142 | 93 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1850 |  | -1995 | -145 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1613 |  | 1740 | -127 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1607 |  | 1740 | -133 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1604 |  | 1740 | -136 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1837 |  | -1995 | -158 | 92 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1817 |  | -1995 | -178 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1582 |  | 1740 | -158 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1581 |  | 1740 | -159 | 91 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1809 |  | -2000 | -191 | 90 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1800 |  | -1995 | -195 | 90 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1792 |  | -1995 | -203 | 90 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1788 |  | -1995 | -207 | 90 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1789 |  | -2000 | -211 | 89 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1784 |  | -1995 | -211 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1549 |  | 1740 | -191 | 89 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1549 |  | 1740 | -191 | 89 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1055 |  | -1248 | -193 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1053 |  | -1248 | -196 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1051 |  | -1248 | -198 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1043 |  | -1248 | -205 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1042 |  | -1248 | -207 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1037 |  | -1248 | -212 | 83 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1625 |  | 1995 | -370 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1601 |  | -1995 | -394 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1224 |  | -1740 | -516 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3561
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1941 | -1995 | -1995 | -54 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 | 1740 | 1740 | -63 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 | 1740 | 1740 | -63 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1916 | -1995 | -1995 | -79 | 96 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1915 | -1995 | -1995 | -80 | 96 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1912 | -1995 | -1995 | -83 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1912 | -1995 | -1995 | -83 | 96 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1911 | 1995 | 1995 | -84 | 96 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1664 | 1740 | 1740 | -76 | 96 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1897 | -1995 | -1995 | -98 | 95 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1893 | -1995 | -1995 | -102 | 95 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1886 | -2000 | -2000 | -114 | 94 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1641 | 1740 | 1740 | -99 | 94 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1872 | -1995 | -1995 | -123 | 94 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1867 | -2000 | -2000 | -133 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1622 | 1740 | 1740 | -118 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1621 | 1740 | 1740 | -119 | 93 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1852 | -1995 | -1995 | -143 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1604 | 1740 | 1740 | -136 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 | 1740 | 1740 | -137 | 92 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1837 | -1995 | -1995 | -158 | 92 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1829 | -1995 | -1995 | -166 | 92 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1826 | -1995 | -1995 | -169 | 92 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1821 | -1995 | -1995 | -174 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1574 | 1740 | 1740 | -166 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1574 | 1740 | 1740 | -166 | 90 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1079 | -1248 | -1248 | -169 | 86 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1076 | -1248 | -1248 | -173 | 86 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1074 | -1248 | -1248 | -174 | 86 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1065 | -1248 | -1248 | -183 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1065 | -1248 | -1248 | -184 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1059 | -1248 | -1248 | -190 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1653 | 1995 | 1995 | -342 | 83 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1630 | 1995 | 1995 | -365 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1389 | -1740 | -1740 | -351 | 80 | []

## 2330Curative
Detailed results
Generated at: | 2024-04-07 20:00
Business day: | 08.04.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3561
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1941 |  | -1995 | -54 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 |  | 1740 | -63 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 |  | 1740 | -63 | 96 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1916 |  | -1995 | -79 | 96 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1915 |  | -1995 | -80 | 96 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1912 |  | -1995 | -83 | 96 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1912 |  | -1995 | -83 | 96 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1911 |  | 1995 | -84 | 96 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1664 |  | 1740 | -76 | 96 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1897 |  | -1995 | -98 | 95 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1893 |  | -1995 | -102 | 95 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1886 |  | -2000 | -114 | 94 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1641 |  | 1740 | -99 | 94 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1872 |  | -1995 | -123 | 94 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1867 |  | -2000 | -133 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1622 |  | 1740 | -118 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1621 |  | 1740 | -119 | 93 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1852 |  | -1995 | -143 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1604 |  | 1740 | -136 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1603 |  | 1740 | -137 | 92 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1837 |  | -1995 | -158 | 92 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1829 |  | -1995 | -166 | 92 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1826 |  | -1995 | -169 | 92 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1821 |  | -1995 | -174 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1574 |  | 1740 | -166 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1574 |  | 1740 | -166 | 90 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1079 |  | -1248 | -169 | 86 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1076 |  | -1248 | -173 | 86 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1074 |  | -1248 | -174 | 86 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1065 |  | -1248 | -183 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1065 |  | -1248 | -184 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1059 |  | -1248 | -190 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1653 |  | 1995 | -342 | 83 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1630 |  | 1995 | -365 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Tantareni-Urechesti [DIR] [RO] | RTINTA1 _RURE241 _1:line | -1389 |  | -1740 | -351 | 80 | []