## 0030Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2900
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1736 | 1740 | 1740 | -4 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1794 | -1995 | -1995 | -201 | 90 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1789 | -1995 | -1995 | -206 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1789 | -1995 | -1995 | -206 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1773 | -1995 | -1995 | -222 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1530 | 1740 | 1740 | -210 | 88 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1515 | 1740 | 1740 | -225 | 87 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1736 | -1995 | -1995 | -259 | 87 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1732 | -1995 | -1995 | -263 | 87 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1724 | -1995 | -1995 | -271 | 86 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1723 | -1995 | -1995 | -272 | 86 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1722 | -1995 | -1995 | -273 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1491 | 1740 | 1740 | -249 | 86 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1707 | -1995 | -1995 | -288 | 86 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1701 | -1995 | -1995 | -294 | 85 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1692 | -1995 | -1995 | -303 | 85 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1687 | -1995 | -1995 | -308 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1468 | 1740 | 1740 | -272 | 84 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1674 | -1995 | -1995 | -321 | 84 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1457 | 1740 | 1740 | -283 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1455 | 1740 | 1740 | -285 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1326 | 1600 | 1600 | -274 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1323 | 1601 | 1601 | -278 | 83 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1432 | 1740 | 1740 | -308 | 82 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1432 | 1740 | 1740 | -308 | 82 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1622 | -2000 | -2000 | -378 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1607 | -2000 | -2000 | -393 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -999 | -1248 | -1248 | -250 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -997 | -1248 | -1248 | -252 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -994 | -1248 | -1248 | -254 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -987 | -1248 | -1248 | -261 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -986 | -1248 | -1248 | -263 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -981 | -1248 | -1248 | -267 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1540 | -1995 | -1995 | -455 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1521 | -1995 | -1995 | -474 | 76 | []
RO_CO_00005 | N-1 Tantareni-Urechesti | [RO-RO] AT Urechesti [OPP] [RO] | RURE241 _RURE212 _1:trf | -725 | -999 | -999 | -274 | 73 | []

## 0030Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2900
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1736 |  | 1740 | -4 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1794 |  | -1995 | -201 | 90 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1789 |  | -1995 | -206 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1789 |  | -1995 | -206 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1773 |  | -1995 | -222 | 89 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1530 |  | 1740 | -210 | 88 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1515 |  | 1740 | -225 | 87 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1736 |  | -1995 | -259 | 87 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1732 |  | -1995 | -263 | 87 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1724 |  | -1995 | -271 | 86 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1723 |  | -1995 | -272 | 86 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1722 |  | -1995 | -273 | 86 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1491 |  | 1740 | -249 | 86 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1707 |  | -1995 | -288 | 86 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1701 |  | -1995 | -294 | 85 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1692 |  | -1995 | -303 | 85 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1687 |  | -1995 | -308 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1468 |  | 1740 | -272 | 84 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1674 |  | -1995 | -321 | 84 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1457 |  | 1740 | -283 | 84 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1455 |  | 1740 | -285 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1326 |  | 1600 | -274 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1323 |  | 1601 | -278 | 83 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1432 |  | 1740 | -308 | 82 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1432 |  | 1740 | -308 | 82 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1622 |  | -2000 | -378 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1607 |  | -2000 | -393 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -999 |  | -1248 | -250 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -997 |  | -1248 | -252 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -994 |  | -1248 | -254 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -987 |  | -1248 | -261 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -986 |  | -1248 | -263 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -981 |  | -1248 | -267 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1540 |  | -1995 | -455 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1521 |  | -1995 | -474 | 76 | []
RO_CO_00005 | N-1 Tantareni-Urechesti | [RO-RO] AT Urechesti [OPP] [RO] | RURE241 _RURE212 _1:trf | -725 |  | -999 | -274 | 73 | []

## 0130Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2671
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 | 1740 | 1740 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1617 | 1740 | 1740 | -123 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1719 | -1995 | -1995 | -276 | 86 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1705 | -1995 | -1995 | -290 | 85 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1690 | -1995 | -1995 | -305 | 85 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1679 | -1995 | -1995 | -316 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 | 1740 | 1740 | -280 | 84 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 | 1740 | 1740 | -286 | 84 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1642 | -1995 | -1995 | -353 | 82 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1640 | -1995 | -1995 | -355 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1637 | -1995 | -1995 | -358 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1629 | -1995 | -1995 | -366 | 82 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1629 | -1995 | -1995 | -366 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1629 | -1995 | -1995 | -366 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1623 | -1995 | -1995 | -372 | 81 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1615 | -1995 | -1995 | -380 | 81 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1614 | -1995 | -1995 | -381 | 81 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1407 | 1740 | 1740 | -333 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 | -1248 | -1248 | -245 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1001 | -1248 | -1248 | -247 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -998 | -1248 | -1248 | -250 | 80 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1587 | -1995 | -1995 | -408 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -993 | -1248 | -1248 | -256 | 79 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1382 | 1740 | 1740 | -358 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -990 | -1248 | -1248 | -258 | 79 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1379 | 1740 | 1740 | -361 | 79 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1378 | 1740 | 1740 | -362 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -986 | -1248 | -1248 | -262 | 79 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1361 | 1740 | 1740 | -379 | 78 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1361 | 1740 | 1740 | -379 | 78 | []
RO_CO_00005 | N-1 Tantareni-Urechesti | [RO-RO] AT Urechesti [DIR] [RO] | RURE241 _RURE212 _1:trf | -763 | -999 | -999 | -236 | 76 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1509 | 2000 | 2000 | -491 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | 1495 | 2000 | 2000 | -505 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1465 | -1995 | -1995 | -530 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1168 | 1601 | 1601 | -433 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1447 | -1995 | -1995 | -548 | 73 | []

## 0130Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2671
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 |  | 1740 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1617 |  | 1740 | -123 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1719 |  | -1995 | -276 | 86 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1705 |  | -1995 | -290 | 85 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1690 |  | -1995 | -305 | 85 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1679 |  | -1995 | -316 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 |  | 1740 | -280 | 84 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1740 | -286 | 84 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1642 |  | -1995 | -353 | 82 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1640 |  | -1995 | -355 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1637 |  | -1995 | -358 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1629 |  | -1995 | -366 | 82 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1629 |  | -1995 | -366 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1629 |  | -1995 | -366 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1623 |  | -1995 | -372 | 81 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1615 |  | -1995 | -380 | 81 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1614 |  | -1995 | -381 | 81 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1407 |  | 1740 | -333 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1003 |  | -1248 | -245 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1001 |  | -1248 | -247 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -998 |  | -1248 | -250 | 80 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1587 |  | -1995 | -408 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -993 |  | -1248 | -256 | 79 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1382 |  | 1740 | -358 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -990 |  | -1248 | -258 | 79 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1379 |  | 1740 | -361 | 79 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1378 |  | 1740 | -362 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -986 |  | -1248 | -262 | 79 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1361 |  | 1740 | -379 | 78 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1361 |  | 1740 | -379 | 78 | []
RO_CO_00005 | N-1 Tantareni-Urechesti | [RO-RO] AT Urechesti [DIR] [RO] | RURE241 _RURE212 _1:trf | -763 |  | -999 | -236 | 76 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1509 |  | 2000 | -491 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | 1495 |  | 2000 | -505 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1465 |  | -1995 | -530 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1175 |  | 1600 | -425 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1168 |  | 1601 | -433 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1447 |  | -1995 | -548 | 73 | []

## 0230Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2850
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1739 | 1740 | 1740 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1548 | 1740 | 1740 | -192 | 89 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1771 | -1995 | -1995 | -224 | 89 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 | 1740 | 1740 | -205 | 88 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1758 | -1995 | -1995 | -237 | 88 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1751 | -1995 | -1995 | -244 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1738 | -1995 | -1995 | -257 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 | 1740 | 1740 | -233 | 87 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1703 | -1995 | -1995 | -292 | 85 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1701 | -1995 | -1995 | -294 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1482 | 1740 | 1740 | -258 | 85 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1478 | 1740 | 1740 | -262 | 85 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1476 | 1740 | 1740 | -264 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1690 | -1995 | -1995 | -305 | 85 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1690 | -1995 | -1995 | -305 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1688 | -1995 | -1995 | -307 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1687 | -1995 | -1995 | -308 | 85 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1675 | -1995 | -1995 | -320 | 84 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1672 | -1995 | -1995 | -323 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 | 1740 | 1740 | -284 | 84 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 | 1740 | 1740 | -284 | 84 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1668 | -1995 | -1995 | -327 | 84 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1640 | -1995 | -1995 | -355 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1009 | -1248 | -1248 | -239 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1007 | -1248 | -1248 | -242 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1004 | -1248 | -1248 | -244 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1280 | 1600 | 1600 | -320 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -997 | -1248 | -1248 | -251 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -996 | -1248 | -1248 | -253 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1276 | 1601 | 1601 | -325 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -991 | -1248 | -1248 | -257 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1584 | 2000 | 2000 | -416 | 79 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | 1569 | 2000 | 2000 | -431 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1514 | -1995 | -1995 | -481 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1496 | -1995 | -1995 | -499 | 75 | []
RO_CO_00005 | N-1 Tantareni-Urechesti | [RO-RO] AT Urechesti [OPP] [RO] | RURE241 _RURE212 _1:trf | -740 | -999 | -999 | -260 | 74 | []

## 0230Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2850
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1739 |  | 1740 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1548 |  | 1740 | -192 | 89 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1771 |  | -1995 | -224 | 89 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 |  | 1740 | -205 | 88 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1758 |  | -1995 | -237 | 88 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1751 |  | -1995 | -244 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1738 |  | -1995 | -257 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 |  | 1740 | -233 | 87 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1703 |  | -1995 | -292 | 85 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1701 |  | -1995 | -294 | 85 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1482 |  | 1740 | -258 | 85 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1478 |  | 1740 | -262 | 85 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1476 |  | 1740 | -264 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1690 |  | -1995 | -305 | 85 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1690 |  | -1995 | -305 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1688 |  | -1995 | -307 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1687 |  | -1995 | -308 | 85 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1675 |  | -1995 | -320 | 84 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1672 |  | -1995 | -323 | 84 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 |  | 1740 | -284 | 84 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 |  | 1740 | -284 | 84 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1668 |  | -1995 | -327 | 84 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1640 |  | -1995 | -355 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1009 |  | -1248 | -239 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1007 |  | -1248 | -242 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1004 |  | -1248 | -244 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1280 |  | 1600 | -320 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -997 |  | -1248 | -251 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -996 |  | -1248 | -253 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV NPP Kozloduy - Tantareni ck. 2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1276 |  | 1601 | -325 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -991 |  | -1248 | -257 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | 1584 |  | 2000 | -416 | 79 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | 1569 |  | 2000 | -431 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1514 |  | -1995 | -481 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1496 |  | -1995 | -499 | 75 | []
RO_CO_00005 | N-1 Tantareni-Urechesti | [RO-RO] AT Urechesti [OPP] [RO] | RURE241 _RURE212 _1:trf | -740 |  | -999 | -260 | 74 | []

## 0330Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2619
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 | 1740 | 1740 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1599 | 1740 | 1740 | -141 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 | -1995 | -1995 | -307 | 85 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1679 | -1995 | -1995 | -316 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 | 1740 | 1740 | -286 | 84 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1665 | -1995 | -1995 | -330 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1451 | 1740 | 1740 | -289 | 83 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1653 | -1995 | -1995 | -342 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1009 | -1248 | -1248 | -239 | 81 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1612 | -1995 | -1995 | -383 | 81 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1612 | -1995 | -1995 | -383 | 81 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1610 | -1995 | -1995 | -385 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1007 | -1248 | -1248 | -241 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1004 | -1248 | -1248 | -244 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1599 | -1995 | -1995 | -396 | 80 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1598 | -1995 | -1995 | -397 | 80 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1598 | -1995 | -1995 | -397 | 80 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1598 | -1995 | -1995 | -397 | 80 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1393 | 1740 | 1740 | -347 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -999 | -1248 | -1248 | -250 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -996 | -1248 | -1248 | -252 | 80 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1589 | -1995 | -1995 | -406 | 80 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1587 | -1995 | -1995 | -408 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -992 | -1248 | -1248 | -256 | 79 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1365 | 1740 | 1740 | -375 | 78 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1365 | 1740 | 1740 | -375 | 78 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1364 | 1740 | 1740 | -376 | 78 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1559 | -1995 | -1995 | -436 | 78 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1348 | 1740 | 1740 | -392 | 77 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1348 | 1740 | 1740 | -392 | 77 | []
RO_CO_00005 | N-1 Tantareni-Urechesti | [RO-RO] AT Urechesti [OPP] [RO] | RURE241 _RURE212 _1:trf | -762 | -999 | -999 | -237 | 76 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1477 | 2000 | 2000 | -523 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | 1464 | 2000 | 2000 | -536 | 73 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1439 | -1995 | -1995 | -556 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1422 | -1995 | -1995 | -573 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1135 | 1601 | 1601 | -466 | 71 | []

## 0330Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2619
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 |  | 1740 | -3 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1599 |  | 1740 | -141 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 |  | -1995 | -307 | 85 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1679 |  | -1995 | -316 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1740 | -286 | 84 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1665 |  | -1995 | -330 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1451 |  | 1740 | -289 | 83 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1653 |  | -1995 | -342 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1009 |  | -1248 | -239 | 81 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1612 |  | -1995 | -383 | 81 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1612 |  | -1995 | -383 | 81 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1610 |  | -1995 | -385 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1007 |  | -1248 | -241 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1004 |  | -1248 | -244 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1599 |  | -1995 | -396 | 80 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1598 |  | -1995 | -397 | 80 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1598 |  | -1995 | -397 | 80 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1598 |  | -1995 | -397 | 80 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1393 |  | 1740 | -347 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -999 |  | -1248 | -250 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -996 |  | -1248 | -252 | 80 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1589 |  | -1995 | -406 | 80 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1587 |  | -1995 | -408 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -992 |  | -1248 | -256 | 79 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1365 |  | 1740 | -375 | 78 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1365 |  | 1740 | -375 | 78 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1364 |  | 1740 | -376 | 78 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1559 |  | -1995 | -436 | 78 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1348 |  | 1740 | -392 | 77 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1348 |  | 1740 | -392 | 77 | []
RO_CO_00005 | N-1 Tantareni-Urechesti | [RO-RO] AT Urechesti [OPP] [RO] | RURE241 _RURE212 _1:trf | -762 |  | -999 | -237 | 76 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1477 |  | 2000 | -523 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | 1464 |  | 2000 | -536 | 73 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1439 |  | -1995 | -556 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1422 |  | -1995 | -573 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1140 |  | 1600 | -460 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1135 |  | 1601 | -466 | 71 | []

## 0430Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2611
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1738 | 1740 | 1740 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1617 | 1740 | 1740 | -123 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 | -1995 | -1995 | -300 | 85 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1689 | -1995 | -1995 | -306 | 85 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1678 | -1995 | -1995 | -317 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1665 | -1995 | -1995 | -330 | 83 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1435 | 1740 | 1740 | -305 | 82 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1635 | -1995 | -1995 | -360 | 82 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1632 | -1995 | -1995 | -363 | 82 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1420 | 1740 | 1740 | -320 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1627 | -1995 | -1995 | -368 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1620 | -1995 | -1995 | -375 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1619 | -1995 | -1995 | -376 | 81 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1613 | -1995 | -1995 | -382 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1612 | -1995 | -1995 | -383 | 81 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1601 | -1995 | -1995 | -394 | 80 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1601 | -1995 | -1995 | -394 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -998 | -1248 | -1248 | -251 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -997 | -1248 | -1248 | -252 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -993 | -1248 | -1248 | -255 | 80 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1379 | 1740 | 1740 | -361 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -988 | -1248 | -1248 | -261 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1578 | -1995 | -1995 | -417 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -986 | -1248 | -1248 | -263 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -981 | -1248 | -1248 | -268 | 79 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1351 | 1740 | 1740 | -389 | 78 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1350 | 1740 | 1740 | -390 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1349 | 1740 | 1740 | -391 | 78 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1337 | 1740 | 1740 | -403 | 77 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1337 | 1740 | 1740 | -403 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1524 | 2000 | 2000 | -476 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | 1511 | 2000 | 2000 | -489 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | 603 | 800 | 800 | -197 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | -601 | -800 | -800 | -199 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1197 | 1601 | 1601 | -404 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1449 | -1995 | -1995 | -546 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1431 | -1995 | -1995 | -564 | 72 | []

## 0430Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2611
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1738 |  | 1740 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1617 |  | 1740 | -123 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 |  | -1995 | -300 | 85 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1689 |  | -1995 | -306 | 85 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1678 |  | -1995 | -317 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1665 |  | -1995 | -330 | 83 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1740 | -305 | 82 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1635 |  | -1995 | -360 | 82 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1632 |  | -1995 | -363 | 82 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1420 |  | 1740 | -320 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1627 |  | -1995 | -368 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1620 |  | -1995 | -375 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1619 |  | -1995 | -376 | 81 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1613 |  | -1995 | -382 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1612 |  | -1995 | -383 | 81 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1601 |  | -1995 | -394 | 80 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1601 |  | -1995 | -394 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -998 |  | -1248 | -251 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -997 |  | -1248 | -252 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -993 |  | -1248 | -255 | 80 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1379 |  | 1740 | -361 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -988 |  | -1248 | -261 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1578 |  | -1995 | -417 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -986 |  | -1248 | -263 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -981 |  | -1248 | -268 | 79 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1351 |  | 1740 | -389 | 78 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1350 |  | 1740 | -390 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1349 |  | 1740 | -391 | 78 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1337 |  | 1740 | -403 | 77 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1337 |  | 1740 | -403 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1524 |  | 2000 | -476 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | 1511 |  | 2000 | -489 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | 603 |  | 800 | -197 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | -601 |  | -800 | -199 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1201 |  | 1600 | -399 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1197 |  | 1601 | -404 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1449 |  | -1995 | -546 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1431 |  | -1995 | -564 | 72 | []

## 0530Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2556
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | 768 | 800 | 800 | -32 | 96 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | -767 | -800 | -800 | -33 | 96 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1866 | -1995 | -1995 | -129 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1623 | 1740 | 1740 | -117 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1859 | -1995 | -1995 | -136 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1854 | -1995 | -1995 | -141 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1845 | -1995 | -1995 | -150 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1608 | 1740 | 1740 | -132 | 92 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1833 | -1995 | -1995 | -162 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1827 | -1995 | -1995 | -168 | 92 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1824 | -2000 | -2000 | -176 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1814 | -1995 | -1995 | -181 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1812 | -1995 | -1995 | -183 | 91 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1577 | 1740 | 1740 | -163 | 91 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1810 | -2000 | -2000 | -190 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1800 | -1995 | -1995 | -195 | 90 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1781 | -1995 | -1995 | -214 | 89 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1546 | 1740 | 1740 | -194 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1768 | -1995 | -1995 | -227 | 89 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 | 1740 | 1740 | -205 | 88 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1534 | 1740 | 1740 | -206 | 88 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1757 | -1995 | -1995 | -238 | 88 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1755 | -1995 | -1995 | -240 | 88 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1749 | -1995 | -1995 | -246 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1516 | 1740 | 1740 | -224 | 87 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1516 | 1740 | 1740 | -224 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT Urechesti [OPP] [RO] | RURE241 _RURE212 _1:trf | -845 | -999 | -999 | -155 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1640 | -1995 | -1995 | -355 | 82 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1620 | -1995 | -1995 | -375 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -977 | -1248 | -1248 | -272 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -974 | -1248 | -1248 | -275 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -972 | -1248 | -1248 | -276 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -964 | -1248 | -1248 | -285 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -963 | -1248 | -1248 | -285 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -957 | -1248 | -1248 | -291 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Baru Mare [DIR] [RO] | RPARO22 _RBARU22 _1:line | -589 | -800 | -800 | -211 | 74 | []

## 0530Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2556
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | 768 |  | 800 | -32 | 96 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | -767 |  | -800 | -33 | 96 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1866 |  | -1995 | -129 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1623 |  | 1740 | -117 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1859 |  | -1995 | -136 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1854 |  | -1995 | -141 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1845 |  | -1995 | -150 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1608 |  | 1740 | -132 | 92 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1833 |  | -1995 | -162 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1827 |  | -1995 | -168 | 92 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1824 |  | -2000 | -176 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1814 |  | -1995 | -181 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1812 |  | -1995 | -183 | 91 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1577 |  | 1740 | -163 | 91 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1810 |  | -2000 | -190 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1800 |  | -1995 | -195 | 90 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1781 |  | -1995 | -214 | 89 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1546 |  | 1740 | -194 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1768 |  | -1995 | -227 | 89 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 |  | 1740 | -205 | 88 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1534 |  | 1740 | -206 | 88 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1757 |  | -1995 | -238 | 88 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1755 |  | -1995 | -240 | 88 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1749 |  | -1995 | -246 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1516 |  | 1740 | -224 | 87 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1516 |  | 1740 | -224 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT Urechesti [OPP] [RO] | RURE241 _RURE212 _1:trf | -845 |  | -999 | -155 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1640 |  | -1995 | -355 | 82 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1620 |  | -1995 | -375 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -977 |  | -1248 | -272 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -974 |  | -1248 | -275 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -972 |  | -1248 | -276 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -964 |  | -1248 | -285 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -963 |  | -1248 | -285 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -957 |  | -1248 | -291 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Baru Mare [DIR] [RO] | RPARO22 _RBARU22 _1:line | -589 |  | -800 | -211 | 74 | []

## 0630Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2357
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 | 1740 | 1740 | -35 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 | 1740 | 1740 | -44 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1638 | 1740 | 1740 | -102 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1626 | 1740 | 1740 | -114 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1588 | 1740 | 1740 | -152 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1587 | 1740 | 1740 | -153 | 91 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1800 | -1995 | -1995 | -195 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1800 | -1995 | -1995 | -195 | 90 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1563 | 1740 | 1740 | -177 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1563 | 1740 | 1740 | -177 | 90 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1783 | -1995 | -1995 | -212 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1768 | -1995 | -1995 | -227 | 89 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1699 | -1995 | -1995 | -296 | 85 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1698 | -1995 | -1995 | -297 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 | -1995 | -1995 | -300 | 85 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1694 | -1995 | -1995 | -301 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1689 | -1995 | -1995 | -306 | 85 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1689 | -1995 | -1995 | -306 | 85 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1686 | -1995 | -1995 | -309 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1683 | -1995 | -1995 | -312 | 84 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1669 | -1995 | -1995 | -326 | 84 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1609 | -1995 | -1995 | -386 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 639 | 800 | 800 | -161 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -639 | -800 | -800 | -161 | 80 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1579 | -1995 | -1995 | -416 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1571 | 2000 | 2000 | -429 | 79 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1562 | -1995 | -1995 | -433 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | 1558 | 2000 | 2000 | -442 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -918 | -1248 | -1248 | -330 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -914 | -1248 | -1248 | -335 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -914 | -1248 | -1248 | -335 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -904 | -1248 | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -897 | -1248 | -1248 | -351 | 72 | []

## 0630Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2357
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 |  | 1740 | -35 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 |  | 1740 | -44 | 97 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1638 |  | 1740 | -102 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1626 |  | 1740 | -114 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1588 |  | 1740 | -152 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1587 |  | 1740 | -153 | 91 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1800 |  | -1995 | -195 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1800 |  | -1995 | -195 | 90 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1563 |  | 1740 | -177 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1563 |  | 1740 | -177 | 90 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1783 |  | -1995 | -212 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1768 |  | -1995 | -227 | 89 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1699 |  | -1995 | -296 | 85 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1698 |  | -1995 | -297 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 |  | -1995 | -300 | 85 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1694 |  | -1995 | -301 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1689 |  | -1995 | -306 | 85 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1689 |  | -1995 | -306 | 85 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1686 |  | -1995 | -309 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1683 |  | -1995 | -312 | 84 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1669 |  | -1995 | -326 | 84 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1609 |  | -1995 | -386 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 639 |  | 800 | -161 | 80 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -639 |  | -800 | -161 | 80 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1579 |  | -1995 | -416 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | 1571 |  | 2000 | -429 | 79 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1562 |  | -1995 | -433 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | 1558 |  | 2000 | -442 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -918 |  | -1248 | -330 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -914 |  | -1248 | -335 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -914 |  | -1248 | -335 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -904 |  | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -897 |  | -1248 | -351 | 72 | []

## 0730Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1784
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 693 | 800 | 800 | -107 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -693 | -800 | -800 | -107 | 87 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1472 | 1740 | 1740 | -268 | 85 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1466 | 1740 | 1740 | -274 | 84 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1404 | 1740 | 1740 | -336 | 81 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1390 | 1740 | 1740 | -350 | 80 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1383 | 1740 | 1740 | -357 | 79 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1584 | -1995 | -1995 | -411 | 79 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1553 | -1995 | -1995 | -442 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1550 | -1995 | -1995 | -445 | 78 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1527 | -1995 | -1995 | -468 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1318 | 1740 | 1740 | -422 | 76 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1297 | 1740 | 1740 | -443 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1297 | 1740 | 1740 | -443 | 75 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1435 | -1995 | -1995 | -560 | 72 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1428 | -1995 | -1995 | -567 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1422 | -1995 | -1995 | -573 | 71 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1422 | -1995 | -1995 | -573 | 71 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1420 | -1995 | -1995 | -575 | 71 | []

## 0730Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1784
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 693 |  | 800 | -107 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -693 |  | -800 | -107 | 87 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1472 |  | 1740 | -268 | 85 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1466 |  | 1740 | -274 | 84 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1404 |  | 1740 | -336 | 81 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1390 |  | 1740 | -350 | 80 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1383 |  | 1740 | -357 | 79 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1584 |  | -1995 | -411 | 79 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1553 |  | -1995 | -442 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1550 |  | -1995 | -445 | 78 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1527 |  | -1995 | -468 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1318 |  | 1740 | -422 | 76 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1297 |  | 1740 | -443 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1297 |  | 1740 | -443 | 75 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1435 |  | -1995 | -560 | 72 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1428 |  | -1995 | -567 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1422 |  | -1995 | -573 | 71 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1422 |  | -1995 | -573 | 71 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1420 |  | -1995 | -575 | 71 | []

## 0830Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1561
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1729 | 1740 | 1740 | -11 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 704 | 800 | 800 | -96 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -703 | -800 | -800 | -97 | 88 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1362 | 1740 | 1740 | -378 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1360 | 1740 | 1740 | -380 | 78 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1529 | -1995 | -1995 | -466 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1502 | -1995 | -1995 | -493 | 75 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1299 | 1740 | 1740 | -441 | 75 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1479 | -1995 | -1995 | -516 | 74 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1454 | -1995 | -1995 | -541 | 73 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1266 | 1740 | 1740 | -474 | 73 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1264 | 1740 | 1740 | -476 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Baru Mare [DIR] [RO] | RPARO22 _RBARU22 _1:line | 562 | 800 | 800 | -238 | 70 | []

## 0830Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1561
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1729 |  | 1740 | -11 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 704 |  | 800 | -96 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -703 |  | -800 | -97 | 88 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1362 |  | 1740 | -378 | 78 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1360 |  | 1740 | -380 | 78 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1529 |  | -1995 | -466 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1502 |  | -1995 | -493 | 75 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1299 |  | 1740 | -441 | 75 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1479 |  | -1995 | -516 | 74 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1454 |  | -1995 | -541 | 73 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1266 |  | 1740 | -474 | 73 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1264 |  | 1740 | -476 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Baru Mare [DIR] [RO] | RPARO22 _RBARU22 _1:line | 562 |  | 800 | -238 | 70 | []

## 0930Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1498
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 | 1740 | 1740 | -10 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 722 | 800 | 800 | -78 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -722 | -800 | -800 | -78 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1475 | 1740 | 1740 | -265 | 85 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1474 | 1740 | 1740 | -266 | 85 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1408 | 1740 | 1740 | -332 | 81 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1403 | 1740 | 1740 | -337 | 81 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1382 | 1740 | 1740 | -358 | 79 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1307 | 1740 | 1740 | -433 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1293 | 1740 | 1740 | -447 | 74 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1293 | 1740 | 1740 | -447 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Baru Mare [DIR] [RO] | RPARO22 _RBARU22 _1:line | 573 | 800 | 800 | -227 | 72 | []

## 0930Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1498
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1730 |  | 1740 | -10 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 722 |  | 800 | -78 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -722 |  | -800 | -78 | 90 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1475 |  | 1740 | -265 | 85 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1474 |  | 1740 | -266 | 85 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1408 |  | 1740 | -332 | 81 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1403 |  | 1740 | -337 | 81 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1382 |  | 1740 | -358 | 79 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1307 |  | 1740 | -433 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1293 |  | 1740 | -447 | 74 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1293 |  | 1740 | -447 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Baru Mare [DIR] [RO] | RPARO22 _RBARU22 _1:line | 573 |  | 800 | -227 | 72 | []

## 1030Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1654
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1643 | -1740 | -1740 | -97 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1614 | -1740 | -1740 | -126 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1585 | -1740 | -1740 | -155 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1548 | -1740 | -1740 | -192 | 89 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1543 | -1740 | -1740 | -197 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 698 | 800 | 800 | -102 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -698 | -800 | -800 | -102 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1470 | -1740 | -1740 | -270 | 85 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1461 | -1740 | -1740 | -279 | 84 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1461 | -1740 | -1740 | -279 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1441 | -1995 | -1995 | -554 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1411 | -1995 | -1995 | -584 | 71 | []

## 1030Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1654
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1643 |  | -1740 | -97 | 94 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1614 |  | -1740 | -126 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1585 |  | -1740 | -155 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1548 |  | -1740 | -192 | 89 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1543 |  | -1740 | -197 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 698 |  | 800 | -102 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -698 |  | -800 | -102 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1470 |  | -1740 | -270 | 85 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1461 |  | -1740 | -279 | 84 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | -1461 |  | -1740 | -279 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1441 |  | -1995 | -554 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1411 |  | -1995 | -584 | 71 | []

## 1130Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1512
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1740 | 1740 | 1740 | 0 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1475 | 1740 | 1740 | -265 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 668 | 800 | 800 | -132 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -668 | -800 | -800 | -132 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 | 1740 | 1740 | -295 | 83 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1405 | 1740 | 1740 | -335 | 81 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1365 | 1740 | 1740 | -375 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1356 | 1740 | 1740 | -384 | 78 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1300 | 1740 | 1740 | -440 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1294 | 1740 | 1740 | -446 | 74 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1294 | 1740 | 1740 | -446 | 74 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1397 | -1995 | -1995 | -598 | 70 | []

## 1130Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1512
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1740 |  | 1740 | 0 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1475 |  | 1740 | -265 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 668 |  | 800 | -132 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -668 |  | -800 | -132 | 84 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1740 | -295 | 83 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1405 |  | 1740 | -335 | 81 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1365 |  | 1740 | -375 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1356 |  | 1740 | -384 | 78 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1300 |  | 1740 | -440 | 75 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1294 |  | 1740 | -446 | 74 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1294 |  | 1740 | -446 | 74 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1397 |  | -1995 | -598 | 70 | []

## 1230Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1508
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1732 | 1740 | 1740 | -8 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 683 | 800 | 800 | -117 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -683 | -800 | -800 | -117 | 85 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1450 | 1740 | 1740 | -290 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1447 | 1740 | 1740 | -293 | 83 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1388 | 1740 | 1740 | -352 | 80 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1352 | 1740 | 1740 | -388 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1350 | 1740 | 1740 | -390 | 78 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1287 | 1740 | 1740 | -453 | 74 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1280 | 1740 | 1740 | -460 | 74 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1280 | 1740 | 1740 | -460 | 74 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1422 | -1995 | -1995 | -573 | 71 | []

## 1230Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1508
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1732 |  | 1740 | -8 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 683 |  | 800 | -117 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -683 |  | -800 | -117 | 85 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1450 |  | 1740 | -290 | 83 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1447 |  | 1740 | -293 | 83 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1388 |  | 1740 | -352 | 80 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1352 |  | 1740 | -388 | 78 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1350 |  | 1740 | -390 | 78 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1287 |  | 1740 | -453 | 74 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1280 |  | 1740 | -460 | 74 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1280 |  | 1740 | -460 | 74 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1422 |  | -1995 | -573 | 71 | []

## 1330Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1515
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1732 | 1740 | 1740 | -8 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 692 | 800 | 800 | -108 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -691 | -800 | -800 | -109 | 86 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1450 | 1740 | 1740 | -290 | 83 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1423 | 1740 | 1740 | -317 | 82 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1367 | 1740 | 1740 | -373 | 79 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1346 | 1740 | 1740 | -394 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1338 | 1740 | 1740 | -402 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1274 | 1740 | 1740 | -466 | 73 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1266 | 1740 | 1740 | -474 | 73 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1266 | 1740 | 1740 | -474 | 73 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1441 | -1995 | -1995 | -554 | 72 | []

## 1330Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1515
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1732 |  | 1740 | -8 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 692 |  | 800 | -108 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -691 |  | -800 | -109 | 86 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1450 |  | 1740 | -290 | 83 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1423 |  | 1740 | -317 | 82 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1367 |  | 1740 | -373 | 79 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1346 |  | 1740 | -394 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1338 |  | 1740 | -402 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1274 |  | 1740 | -466 | 73 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1266 |  | 1740 | -474 | 73 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1266 |  | 1740 | -474 | 73 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1441 |  | -1995 | -554 | 72 | []

## 1430Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1518
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1734 | 1740 | 1740 | -6 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1444 | 1740 | 1740 | -296 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 652 | 800 | 800 | -148 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -652 | -800 | -800 | -148 | 81 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1415 | 1740 | 1740 | -325 | 81 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1380 | 1740 | 1740 | -360 | 79 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1344 | 1740 | 1740 | -396 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1334 | 1740 | 1740 | -406 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1277 | 1740 | 1740 | -463 | 73 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1268 | 1740 | 1740 | -472 | 73 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1268 | 1740 | 1740 | -472 | 73 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1420 | -1995 | -1995 | -575 | 71 | []

## 1430Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1518
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1734 |  | 1740 | -6 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1740 | -296 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 652 |  | 800 | -148 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -652 |  | -800 | -148 | 81 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1415 |  | 1740 | -325 | 81 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1380 |  | 1740 | -360 | 79 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1344 |  | 1740 | -396 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1334 |  | 1740 | -406 | 77 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1277 |  | 1740 | -463 | 73 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1268 |  | 1740 | -472 | 73 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1268 |  | 1740 | -472 | 73 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1420 |  | -1995 | -575 | 71 | []

## 1530Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1549
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1731 | 1740 | 1740 | -9 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 647 | 800 | 800 | -153 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -647 | -800 | -800 | -153 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1370 | 1740 | 1740 | -370 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1367 | 1740 | 1740 | -373 | 79 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1304 | 1740 | 1740 | -436 | 75 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1265 | 1740 | 1740 | -475 | 73 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1252 | 1740 | 1740 | -488 | 72 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1407 | -1995 | -1995 | -588 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1549
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1731 |  | 1740 | -9 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 647 |  | 800 | -153 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -647 |  | -800 | -153 | 81 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1370 |  | 1740 | -370 | 79 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1367 |  | 1740 | -373 | 79 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1304 |  | 1740 | -436 | 75 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1265 |  | 1740 | -475 | 73 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1252 |  | 1740 | -488 | 72 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1407 |  | -1995 | -588 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1628
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 | 1740 | 1740 | -5 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1436 | -1995 | -1995 | -559 | 72 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1435 | -1995 | -1995 | -560 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 570 | 800 | 800 | -230 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -570 | -800 | -800 | -230 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1628
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 |  | 1740 | -5 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1436 |  | -1995 | -559 | 72 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1435 |  | -1995 | -560 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 570 |  | 800 | -230 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -570 |  | -800 | -230 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2335
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1941 | -1995 | -1995 | -54 | 97 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1906 | -1995 | -1995 | -89 | 96 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1885 | -1995 | -1995 | -110 | 94 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1881 | -1995 | -1995 | -114 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1874 | -1995 | -1995 | -121 | 94 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1873 | -1995 | -1995 | -122 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1872 | -1995 | -1995 | -123 | 94 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1867 | -1995 | -1995 | -128 | 94 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1858 | -2000 | -2000 | -142 | 93 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1852 | -1995 | -1995 | -143 | 93 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1845 | -2000 | -2000 | -155 | 92 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1827 | -1995 | -1995 | -168 | 92 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1823 | -1995 | -1995 | -172 | 91 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1796 | -1995 | -1995 | -199 | 90 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1776 | -1995 | -1995 | -219 | 89 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1766 | -1995 | -1995 | -229 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1691 | -1995 | -1995 | -304 | 85 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1672 | -1995 | -1995 | -323 | 84 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1303 | -1740 | -1740 | -437 | 75 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1298 | -1740 | -1740 | -442 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -930 | -1248 | -1248 | -319 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -928 | -1248 | -1248 | -320 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -925 | -1248 | -1248 | -323 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -920 | -1248 | -1248 | -328 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -918 | -1248 | -1248 | -331 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -914 | -1248 | -1248 | -334 | 73 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1251 | -1740 | -1740 | -489 | 72 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1222 | -1740 | -1740 | -518 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2335
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1941 |  | -1995 | -54 | 97 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1906 |  | -1995 | -89 | 96 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1885 |  | -1995 | -110 | 94 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1881 |  | -1995 | -114 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1874 |  | -1995 | -121 | 94 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1873 |  | -1995 | -122 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1872 |  | -1995 | -123 | 94 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1867 |  | -1995 | -128 | 94 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1858 |  | -2000 | -142 | 93 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1852 |  | -1995 | -143 | 93 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1845 |  | -2000 | -155 | 92 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1827 |  | -1995 | -168 | 92 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1823 |  | -1995 | -172 | 91 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1796 |  | -1995 | -199 | 90 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1776 |  | -1995 | -219 | 89 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1766 |  | -1995 | -229 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1691 |  | -1995 | -304 | 85 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1672 |  | -1995 | -323 | 84 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1303 |  | -1740 | -437 | 75 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1298 |  | -1740 | -442 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -930 |  | -1248 | -319 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -928 |  | -1248 | -320 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -925 |  | -1248 | -323 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -920 |  | -1248 | -328 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -918 |  | -1248 | -331 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -914 |  | -1248 | -334 | 73 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1251 |  | -1740 | -489 | 72 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1222 |  | -1740 | -518 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2403
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1992 | -1995 | -1995 | -3 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1971 | -1995 | -1995 | -24 | 99 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1955 | -1995 | -1995 | -40 | 98 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1951 | -1995 | -1995 | -44 | 98 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1950 | -1995 | -1995 | -45 | 98 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1952 | -2000 | -2000 | -48 | 98 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1946 | -1995 | -1995 | -49 | 98 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1940 | -1995 | -1995 | -55 | 97 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1938 | -1995 | -1995 | -57 | 97 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1939 | -2000 | -2000 | -61 | 97 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1918 | -1995 | -1995 | -77 | 96 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1892 | -1995 | -1995 | -103 | 95 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1882 | -1995 | -1995 | -113 | 94 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1856 | -1995 | -1995 | -139 | 93 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1838 | -1995 | -1995 | -157 | 92 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1830 | -1995 | -1995 | -165 | 92 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1748 | -1995 | -1995 | -247 | 88 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1728 | -1995 | -1995 | -267 | 87 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1348 | -1740 | -1740 | -392 | 77 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1346 | -1740 | -1740 | -394 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1282 | -1740 | -1740 | -458 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -901 | -1248 | -1248 | -347 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -899 | -1248 | -1248 | -350 | 72 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1248 | 1740 | 1740 | -492 | 72 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1245 | 1740 | 1740 | -495 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -892 | -1248 | -1248 | -356 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -891 | -1248 | -1248 | -358 | 71 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1241 | 1740 | 1740 | -499 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -886 | -1248 | -1248 | -362 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2403
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1992 |  | -1995 | -3 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1971 |  | -1995 | -24 | 99 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1955 |  | -1995 | -40 | 98 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1951 |  | -1995 | -44 | 98 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1950 |  | -1995 | -45 | 98 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1952 |  | -2000 | -48 | 98 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1946 |  | -1995 | -49 | 98 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1940 |  | -1995 | -55 | 97 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1938 |  | -1995 | -57 | 97 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1939 |  | -2000 | -61 | 97 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1918 |  | -1995 | -77 | 96 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1892 |  | -1995 | -103 | 95 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1882 |  | -1995 | -113 | 94 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1856 |  | -1995 | -139 | 93 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1838 |  | -1995 | -157 | 92 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1830 |  | -1995 | -165 | 92 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1748 |  | -1995 | -247 | 88 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1728 |  | -1995 | -267 | 87 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1348 |  | -1740 | -392 | 77 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1346 |  | -1740 | -394 | 77 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | -1282 |  | -1740 | -458 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -901 |  | -1248 | -347 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -899 |  | -1248 | -350 | 72 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1248 |  | 1740 | -492 | 72 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1245 |  | 1740 | -495 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -892 |  | -1248 | -356 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -891 |  | -1248 | -358 | 71 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1241 |  | 1740 | -499 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -886 |  | -1248 | -362 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2079
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1640 | -1995 | -1995 | -355 | 82 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1619 | -1995 | -1995 | -376 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1574 | -1995 | -1995 | -421 | 79 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1567 | -1995 | -1995 | -428 | 79 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1548 | -1995 | -1995 | -447 | 78 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1545 | -1995 | -1995 | -450 | 77 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1538 | -1995 | -1995 | -457 | 77 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1536 | -1995 | -1995 | -459 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1531 | -1995 | -1995 | -464 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1530 | -1995 | -1995 | -465 | 77 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1523 | -1995 | -1995 | -472 | 76 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1520 | -1995 | -1995 | -475 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1508 | -1995 | -1995 | -487 | 76 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1492 | -1995 | -1995 | -503 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1403 | -2000 | -2000 | -597 | 70 | []

## 1930Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2079
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1596 |  | 1600 | -4 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1640 |  | -1995 | -355 | 82 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1619 |  | -1995 | -376 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1574 |  | -1995 | -421 | 79 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1567 |  | -1995 | -428 | 79 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1548 |  | -1995 | -447 | 78 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1545 |  | -1995 | -450 | 77 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1538 |  | -1995 | -457 | 77 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1536 |  | -1995 | -459 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1531 |  | -1995 | -464 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1530 |  | -1995 | -465 | 77 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1523 |  | -1995 | -472 | 76 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1520 |  | -1995 | -475 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1508 |  | -1995 | -487 | 76 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1492 |  | -1995 | -503 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1403 |  | -2000 | -597 | 70 | []

## 2030Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2106
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1621 | -1995 | -1995 | -374 | 81 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1595 | -1995 | -1995 | -400 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1551 | -1995 | -1995 | -444 | 78 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1544 | -1995 | -1995 | -451 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1534 | -1995 | -1995 | -461 | 77 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1530 | -1995 | -1995 | -465 | 77 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1525 | -1995 | -1995 | -470 | 76 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1522 | -1995 | -1995 | -473 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1516 | -1995 | -1995 | -479 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1511 | -1995 | -1995 | -484 | 76 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1506 | -1995 | -1995 | -489 | 75 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1506 | -1995 | -1995 | -489 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1494 | -1995 | -1995 | -501 | 75 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1478 | -1995 | -1995 | -517 | 74 | []

## 2030Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2106
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1597 |  | 1600 | -3 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1621 |  | -1995 | -374 | 81 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1595 |  | -1995 | -400 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1551 |  | -1995 | -444 | 78 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1544 |  | -1995 | -451 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1534 |  | -1995 | -461 | 77 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1530 |  | -1995 | -465 | 77 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1525 |  | -1995 | -470 | 76 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1522 |  | -1995 | -473 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1516 |  | -1995 | -479 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1511 |  | -1995 | -484 | 76 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1506 |  | -1995 | -489 | 75 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1506 |  | -1995 | -489 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1494 |  | -1995 | -501 | 75 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1478 |  | -1995 | -517 | 74 | []

## 2130Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2095
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1619 | -1995 | -1995 | -376 | 81 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1593 | -1995 | -1995 | -402 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1549 | -1995 | -1995 | -446 | 78 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1541 | -1995 | -1995 | -454 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1526 | -1995 | -1995 | -469 | 76 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1523 | -1995 | -1995 | -472 | 76 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1518 | -1995 | -1995 | -477 | 76 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1515 | -1995 | -1995 | -480 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1512 | -1995 | -1995 | -483 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1507 | -1995 | -1995 | -488 | 76 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1501 | -1995 | -1995 | -494 | 75 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1500 | -1995 | -1995 | -495 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1489 | -1995 | -1995 | -506 | 75 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1472 | -1995 | -1995 | -523 | 74 | []

## 2130Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2095
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1595 |  | 1600 | -5 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1619 |  | -1995 | -376 | 81 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1593 |  | -1995 | -402 | 80 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1549 |  | -1995 | -446 | 78 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1541 |  | -1995 | -454 | 77 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1526 |  | -1995 | -469 | 76 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1523 |  | -1995 | -472 | 76 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1518 |  | -1995 | -477 | 76 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1515 |  | -1995 | -480 | 76 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1512 |  | -1995 | -483 | 76 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1507 |  | -1995 | -488 | 76 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1501 |  | -1995 | -494 | 75 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1500 |  | -1995 | -495 | 75 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1489 |  | -1995 | -506 | 75 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1472 |  | -1995 | -523 | 74 | []

## 2230Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1968
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1521 | -1995 | -1995 | -474 | 76 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1492 | -1995 | -1995 | -503 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1451 | -1995 | -1995 | -544 | 73 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1446 | -1995 | -1995 | -549 | 73 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1445 | -1995 | -1995 | -550 | 72 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1443 | -1995 | -1995 | -552 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1440 | -1995 | -1995 | -555 | 72 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1439 | -1995 | -1995 | -556 | 72 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1431 | -1995 | -1995 | -564 | 72 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1431 | -1995 | -1995 | -564 | 72 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1415 | -1995 | -1995 | -580 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1415 | -1995 | -1995 | -580 | 71 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1413 | -1995 | -1995 | -582 | 71 | []

## 2230Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1968
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1596 |  | 1600 | -4 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1521 |  | -1995 | -474 | 76 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1492 |  | -1995 | -503 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1451 |  | -1995 | -544 | 73 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1446 |  | -1995 | -549 | 73 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1445 |  | -1995 | -550 | 72 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1443 |  | -1995 | -552 | 72 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1440 |  | -1995 | -555 | 72 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1439 |  | -1995 | -556 | 72 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1431 |  | -1995 | -564 | 72 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1431 |  | -1995 | -564 | 72 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1415 |  | -1995 | -580 | 71 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1415 |  | -1995 | -580 | 71 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1413 |  | -1995 | -582 | 71 | []

## 2330Preventive
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1895
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1489 | -1995 | -1995 | -506 | 75 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1461 | -1995 | -1995 | -534 | 73 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1431 | -1995 | -1995 | -564 | 72 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1424 | -1995 | -1995 | -571 | 71 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1422 | -1995 | -1995 | -573 | 71 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1419 | -1995 | -1995 | -576 | 71 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1416 | -1995 | -1995 | -579 | 71 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1416 | -1995 | -1995 | -579 | 71 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1411 | -1995 | -1995 | -584 | 71 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1399 | -1995 | -1995 | -596 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2024-04-08 21:42
Business day: | 10.04.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1895
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00044 | N-1 Medgidia Sud - Varna_Dobrudja | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1594 |  | 1600 | -6 | 100 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1489 |  | -1995 | -506 | 75 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1461 |  | -1995 | -534 | 73 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1431 |  | -1995 | -564 | 72 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1424 |  | -1995 | -571 | 71 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1422 |  | -1995 | -573 | 71 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1419 |  | -1995 | -576 | 71 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1416 |  | -1995 | -579 | 71 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1416 |  | -1995 | -579 | 71 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1411 |  | -1995 | -584 | 71 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1399 |  | -1995 | -596 | 70 | []