## 0030Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3463
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 | 1836 | 1836 | -1 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -998 | -999 | -999 | -1 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1809 | 1836 | 1836 | -27 | 99 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1916 | -2000 | -2000 | -84 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 | 1836 | 1836 | -79 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 | 1836 | 1836 | -79 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1747 | 1836 | 1836 | -89 | 95 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1897 | -2000 | -2000 | -103 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1897 | 2000 | 2000 | -103 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 | 1836 | 1836 | -114 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1721 | 1836 | 1836 | -115 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1712 | 1836 | 1836 | -124 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 | 1836 | 1836 | -125 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1680 | 1836 | 1836 | -156 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1770 | 2000 | 2000 | -230 | 89 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1741 | 2000 | 2000 | -259 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1732 | 2000 | 2000 | -268 | 87 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1727 | 2000 | 2000 | -273 | 86 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1694 | 2000 | 2000 | -306 | 85 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1692 | 2000 | 2000 | -308 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1691 | 2000 | 2000 | -309 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1660 | 2000 | 2000 | -340 | 83 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1641 | 2000 | 2000 | -359 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1640 | 2000 | 2000 | -360 | 82 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1637 | 2000 | 2000 | -363 | 82 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1589 | 2000 | 2000 | -411 | 79 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1540 | 2000 | 2000 | -460 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -916 | -1248 | -1248 | -332 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -913 | -1248 | -1248 | -336 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -912 | -1248 | -1248 | -336 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -902 | -1248 | -1248 | -346 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -902 | -1248 | -1248 | -347 | 72 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1437 | 2000 | 2000 | -563 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -896 | -1248 | -1248 | -353 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1414 | 2000 | 2000 | -586 | 71 | []

## 0030Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3463
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 |  | 1836 | -1 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -998 |  | -999 | -1 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1809 |  | 1836 | -27 | 99 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1916 |  | -2000 | -84 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 |  | 1836 | -79 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 |  | 1836 | -79 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1747 |  | 1836 | -89 | 95 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1897 |  | -2000 | -103 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1897 |  | 2000 | -103 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 |  | 1836 | -114 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1721 |  | 1836 | -115 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1712 |  | 1836 | -124 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 |  | 1836 | -125 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1680 |  | 1836 | -156 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1770 |  | 2000 | -230 | 89 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1741 |  | 2000 | -259 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1732 |  | 2000 | -268 | 87 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1727 |  | 2000 | -273 | 86 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1694 |  | 2000 | -306 | 85 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1692 |  | 2000 | -308 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1691 |  | 2000 | -309 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1660 |  | 2000 | -340 | 83 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1641 |  | 2000 | -359 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1640 |  | 2000 | -360 | 82 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1637 |  | 2000 | -363 | 82 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1589 |  | 2000 | -411 | 79 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1540 |  | 2000 | -460 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -916 |  | -1248 | -332 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -913 |  | -1248 | -336 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -912 |  | -1248 | -336 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -902 |  | -1248 | -346 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -902 |  | -1248 | -347 | 72 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1437 |  | 2000 | -563 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -896 |  | -1248 | -353 | 72 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1414 |  | 2000 | -586 | 71 | []

## 0130Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3335
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 | 1836 | 1836 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1807 | 1836 | 1836 | -29 | 98 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -981 | -999 | -999 | -19 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1740 | 1836 | 1836 | -96 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1740 | 1836 | 1836 | -96 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 | 1836 | 1836 | -99 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1713 | 1836 | 1836 | -123 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 | 1836 | 1836 | -125 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1702 | 1836 | 1836 | -134 | 93 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1854 | 2000 | 2000 | -146 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1702 | 1836 | 1836 | -134 | 93 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1849 | -2000 | -2000 | -151 | 92 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1831 | -2000 | -2000 | -169 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1672 | 1836 | 1836 | -164 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1712 | 2000 | 2000 | -288 | 86 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1671 | 2000 | 2000 | -329 | 84 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1664 | 2000 | 2000 | -336 | 83 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1648 | 2000 | 2000 | -352 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1635 | 2000 | 2000 | -365 | 82 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1631 | 2000 | 2000 | -369 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1631 | 2000 | 2000 | -369 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1573 | 2000 | 2000 | -427 | 79 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1566 | 2000 | 2000 | -434 | 78 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1564 | 2000 | 2000 | -436 | 78 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1548 | 2000 | 2000 | -452 | 77 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1509 | 2000 | 2000 | -491 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -902 | -1248 | -1248 | -346 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1444 | 2000 | 2000 | -556 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -899 | -1248 | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -898 | -1248 | -1248 | -350 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -888 | -1248 | -1248 | -360 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -888 | -1248 | -1248 | -361 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -882 | -1248 | -1248 | -367 | 71 | []

## 0130Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3335
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 |  | 1836 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1807 |  | 1836 | -29 | 98 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -981 |  | -999 | -19 | 98 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1740 |  | 1836 | -96 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1740 |  | 1836 | -96 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 |  | 1836 | -99 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1713 |  | 1836 | -123 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 |  | 1836 | -125 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1702 |  | 1836 | -134 | 93 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1854 |  | 2000 | -146 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1702 |  | 1836 | -134 | 93 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1849 |  | -2000 | -151 | 92 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1831 |  | -2000 | -169 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1672 |  | 1836 | -164 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1712 |  | 2000 | -288 | 86 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1671 |  | 2000 | -329 | 84 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1664 |  | 2000 | -336 | 83 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1648 |  | 2000 | -352 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1635 |  | 2000 | -365 | 82 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1631 |  | 2000 | -369 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1631 |  | 2000 | -369 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1573 |  | 2000 | -427 | 79 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1566 |  | 2000 | -434 | 78 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1564 |  | 2000 | -436 | 78 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1548 |  | 2000 | -452 | 77 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1509 |  | 2000 | -491 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -902 |  | -1248 | -346 | 72 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1444 |  | 2000 | -556 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -899 |  | -1248 | -350 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -898 |  | -1248 | -350 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -888 |  | -1248 | -360 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -888 |  | -1248 | -361 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -882 |  | -1248 | -367 | 71 | []

## 0230Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3276
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1836 | 1836 | 1836 | 0 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1813 | 1836 | 1836 | -23 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -968 | -999 | -999 | -31 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1741 | 1836 | 1836 | -95 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1741 | 1836 | 1836 | -95 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1741 | 1836 | 1836 | -95 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1718 | 1836 | 1836 | -118 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 | 1836 | 1836 | -121 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 | 1836 | 1836 | -130 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 | 1836 | 1836 | -130 | 93 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1834 | 2000 | 2000 | -166 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 | 1836 | 1836 | -159 | 91 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1816 | -2000 | -2000 | -184 | 91 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1797 | -2000 | -2000 | -203 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1684 | 2000 | 2000 | -316 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1642 | 2000 | 2000 | -358 | 82 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1628 | 2000 | 2000 | -372 | 81 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1612 | 2000 | 2000 | -388 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1607 | 2000 | 2000 | -393 | 80 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1604 | 2000 | 2000 | -396 | 80 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1603 | 2000 | 2000 | -397 | 80 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1533 | 2000 | 2000 | -467 | 77 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1533 | 2000 | 2000 | -467 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1530 | 2000 | 2000 | -470 | 77 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1507 | 2000 | 2000 | -493 | 75 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1472 | 2000 | 2000 | -528 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -900 | -1248 | -1248 | -348 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -897 | -1248 | -1248 | -352 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -896 | -1248 | -1248 | -352 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -887 | -1248 | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -886 | -1248 | -1248 | -363 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -880 | -1248 | -1248 | -369 | 70 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1402 | 2000 | 2000 | -598 | 70 | []

## 0230Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3276
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1836 |  | 1836 | 0 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1813 |  | 1836 | -23 | 99 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -968 |  | -999 | -31 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1741 |  | 1836 | -95 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1741 |  | 1836 | -95 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1741 |  | 1836 | -95 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1718 |  | 1836 | -118 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 |  | 1836 | -121 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 |  | 1836 | -130 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 |  | 1836 | -130 | 93 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1834 |  | 2000 | -166 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 |  | 1836 | -159 | 91 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1816 |  | -2000 | -184 | 91 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1797 |  | -2000 | -203 | 90 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1684 |  | 2000 | -316 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1642 |  | 2000 | -358 | 82 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1628 |  | 2000 | -372 | 81 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1612 |  | 2000 | -388 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1607 |  | 2000 | -393 | 80 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1604 |  | 2000 | -396 | 80 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1603 |  | 2000 | -397 | 80 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1533 |  | 2000 | -467 | 77 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1533 |  | 2000 | -467 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1530 |  | 2000 | -470 | 77 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1507 |  | 2000 | -493 | 75 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1472 |  | 2000 | -528 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -900 |  | -1248 | -348 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -897 |  | -1248 | -352 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -896 |  | -1248 | -352 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -887 |  | -1248 | -362 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -886 |  | -1248 | -363 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -880 |  | -1248 | -369 | 70 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1402 |  | 2000 | -598 | 70 | []

## 0330Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3406
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 | 1836 | 1836 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1811 | 1836 | 1836 | -25 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1761 | 1836 | 1836 | -75 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1761 | 1836 | 1836 | -75 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1749 | 1836 | 1836 | -87 | 95 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1886 | -2000 | -2000 | -114 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1724 | 1836 | 1836 | -112 | 94 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -938 | -999 | -999 | -62 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1723 | 1836 | 1836 | -113 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 | 1836 | 1836 | -121 | 93 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1867 | -2000 | -2000 | -133 | 93 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1866 | 2000 | 2000 | -134 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1709 | 1836 | 1836 | -127 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1689 | 1836 | 1836 | -147 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1726 | 2000 | 2000 | -274 | 86 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1689 | 2000 | 2000 | -311 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1684 | 2000 | 2000 | -316 | 84 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1673 | 2000 | 2000 | -327 | 84 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1651 | 2000 | 2000 | -349 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1648 | 2000 | 2000 | -352 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1648 | 2000 | 2000 | -352 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1599 | 2000 | 2000 | -401 | 80 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1585 | 2000 | 2000 | -415 | 79 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1584 | 2000 | 2000 | -416 | 79 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1574 | 2000 | 2000 | -426 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1531 | 2000 | 2000 | -469 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -928 | -1248 | -1248 | -321 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -924 | -1248 | -1248 | -324 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -924 | -1248 | -1248 | -325 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -914 | -1248 | -1248 | -334 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1464 | 2000 | 2000 | -536 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -913 | -1248 | -1248 | -335 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -907 | -1248 | -1248 | -341 | 73 | []

## 0330Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3406
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 |  | 1836 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1811 |  | 1836 | -25 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1761 |  | 1836 | -75 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1761 |  | 1836 | -75 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1749 |  | 1836 | -87 | 95 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1886 |  | -2000 | -114 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1724 |  | 1836 | -112 | 94 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -938 |  | -999 | -62 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1723 |  | 1836 | -113 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 |  | 1836 | -121 | 93 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1867 |  | -2000 | -133 | 93 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1866 |  | 2000 | -134 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1709 |  | 1836 | -127 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1689 |  | 1836 | -147 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1726 |  | 2000 | -274 | 86 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1689 |  | 2000 | -311 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1684 |  | 2000 | -316 | 84 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1673 |  | 2000 | -327 | 84 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1651 |  | 2000 | -349 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1648 |  | 2000 | -352 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1648 |  | 2000 | -352 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1599 |  | 2000 | -401 | 80 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1585 |  | 2000 | -415 | 79 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1584 |  | 2000 | -416 | 79 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1574 |  | 2000 | -426 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1531 |  | 2000 | -469 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -928 |  | -1248 | -321 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -924 |  | -1248 | -324 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -924 |  | -1248 | -325 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -914 |  | -1248 | -334 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1464 |  | 2000 | -536 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -913 |  | -1248 | -335 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -907 |  | -1248 | -341 | 73 | []

## 0430Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3538
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1999 | -2000 | -2000 | -1 | 100 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1979 | -2000 | -2000 | -21 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1811 | 1836 | 1836 | -25 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1795 | 1836 | 1836 | -41 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1795 | 1836 | 1836 | -41 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1791 | 1836 | 1836 | -45 | 98 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1906 | 2000 | 2000 | -94 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1749 | 1836 | 1836 | -87 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 | 1836 | 1836 | -99 | 95 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 | 1836 | 1836 | -101 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1723 | 1836 | 1836 | -113 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 | 1836 | 1836 | -114 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 | 1836 | 1836 | -121 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1765 | 2000 | 2000 | -235 | 88 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1753 | 2000 | 2000 | -247 | 88 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1737 | 2000 | 2000 | -263 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1715 | 2000 | 2000 | -285 | 86 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1695 | 2000 | 2000 | -305 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1692 | 2000 | 2000 | -308 | 85 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1692 | 2000 | 2000 | -308 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1660 | 2000 | 2000 | -340 | 83 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1633 | 2000 | 2000 | -367 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1630 | 2000 | 2000 | -370 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1017 | -1248 | -1248 | -231 | 81 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1629 | 2000 | 2000 | -371 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1014 | -1248 | -1248 | -235 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1012 | -1248 | -1248 | -236 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1003 | -1248 | -1248 | -246 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1003 | -1248 | -1248 | -246 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -996 | -1248 | -1248 | -253 | 80 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1584 | 2000 | 2000 | -416 | 79 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1497 | 2000 | 2000 | -503 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1419 | 2000 | 2000 | -581 | 71 | []

## 0430Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3538
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1999 |  | -2000 | -1 | 100 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1979 |  | -2000 | -21 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1811 |  | 1836 | -25 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1795 |  | 1836 | -41 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1795 |  | 1836 | -41 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1791 |  | 1836 | -45 | 98 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1906 |  | 2000 | -94 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1749 |  | 1836 | -87 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1737 |  | 1836 | -99 | 95 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1735 |  | 1836 | -101 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1723 |  | 1836 | -113 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 |  | 1836 | -114 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 |  | 1836 | -121 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1765 |  | 2000 | -235 | 88 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1753 |  | 2000 | -247 | 88 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1737 |  | 2000 | -263 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1715 |  | 2000 | -285 | 86 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1695 |  | 2000 | -305 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1692 |  | 2000 | -308 | 85 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1692 |  | 2000 | -308 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1660 |  | 2000 | -340 | 83 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1633 |  | 2000 | -367 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1630 |  | 2000 | -370 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1017 |  | -1248 | -231 | 81 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1629 |  | 2000 | -371 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1014 |  | -1248 | -235 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1012 |  | -1248 | -236 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1003 |  | -1248 | -246 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1003 |  | -1248 | -246 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -996 |  | -1248 | -253 | 80 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1584 |  | 2000 | -416 | 79 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1497 |  | 2000 | -503 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1419 |  | 2000 | -581 | 71 | []

## 0530Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3422
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1996 | -2000 | -2000 | -4 | 100 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1978 | -2000 | -2000 | -22 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1764 | 1836 | 1836 | -72 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1755 | 1836 | 1836 | -81 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1755 | 1836 | 1836 | -81 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1749 | 1836 | 1836 | -87 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1871 | 2000 | 2000 | -129 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 | 1836 | 1836 | -131 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1688 | 1836 | 1836 | -148 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1682 | 1836 | 1836 | -154 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1675 | 1836 | 1836 | -161 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1671 | 1836 | 1836 | -165 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1640 | 1836 | 1836 | -196 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1727 | 2000 | 2000 | -273 | 86 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1727 | 2000 | 2000 | -273 | 86 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1709 | 2000 | 2000 | -291 | 85 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1677 | 2000 | 2000 | -323 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1669 | 2000 | 2000 | -331 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1662 | 2000 | 2000 | -338 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1650 | 2000 | 2000 | -350 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1020 | -1248 | -1248 | -229 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1629 | 2000 | 2000 | -371 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1016 | -1248 | -1248 | -233 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1015 | -1248 | -1248 | -233 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1005 | -1248 | -1248 | -243 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1004 | -1248 | -1248 | -245 | 80 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1601 | 2000 | 2000 | -399 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -997 | -1248 | -1248 | -251 | 80 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1594 | 2000 | 2000 | -406 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1591 | 2000 | 2000 | -409 | 80 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1555 | 2000 | 2000 | -445 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1454 | 2000 | 2000 | -546 | 73 | []

## 0530Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3422
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1996 |  | -2000 | -4 | 100 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1978 |  | -2000 | -22 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1764 |  | 1836 | -72 | 96 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1755 |  | 1836 | -81 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1755 |  | 1836 | -81 | 96 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1749 |  | 1836 | -87 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1871 |  | 2000 | -129 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 |  | 1836 | -131 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1688 |  | 1836 | -148 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1682 |  | 1836 | -154 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1675 |  | 1836 | -161 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1671 |  | 1836 | -165 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1640 |  | 1836 | -196 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1727 |  | 2000 | -273 | 86 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1727 |  | 2000 | -273 | 86 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1709 |  | 2000 | -291 | 85 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1677 |  | 2000 | -323 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1669 |  | 2000 | -331 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1662 |  | 2000 | -338 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1650 |  | 2000 | -350 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1020 |  | -1248 | -229 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1629 |  | 2000 | -371 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1016 |  | -1248 | -233 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1015 |  | -1248 | -233 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1005 |  | -1248 | -243 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1004 |  | -1248 | -245 | 80 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1601 |  | 2000 | -399 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -997 |  | -1248 | -251 | 80 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1594 |  | 2000 | -406 | 80 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1591 |  | 2000 | -409 | 80 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1555 |  | 2000 | -445 | 78 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1454 |  | 2000 | -546 | 73 | []

## 0630Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3381
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1833 | 1836 | 1836 | -3 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1807 | 1836 | 1836 | -29 | 98 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1951 | -2000 | -2000 | -49 | 98 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -966 | -999 | -999 | -33 | 97 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1934 | -2000 | -2000 | -66 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 | 1836 | 1836 | -93 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 | 1836 | 1836 | -93 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1742 | 1836 | 1836 | -94 | 95 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1732 | 1836 | 1836 | -104 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 | 1836 | 1836 | -111 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1723 | 1836 | 1836 | -113 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1716 | 1836 | 1836 | -120 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1679 | 1836 | 1836 | -157 | 91 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1603 | 2000 | 2000 | -397 | 80 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1594 | 2000 | 2000 | -406 | 80 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1589 | 2000 | 2000 | -411 | 79 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1572 | 2000 | 2000 | -428 | 79 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1565 | 2000 | 2000 | -435 | 78 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1554 | 2000 | 2000 | -446 | 78 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1522 | 2000 | 2000 | -478 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1500 | 2000 | 2000 | -500 | 75 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1500 | 2000 | 2000 | -500 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1500 | 2000 | 2000 | -500 | 75 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1496 | 2000 | 2000 | -504 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -920 | -1248 | -1248 | -328 | 74 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1469 | 2000 | 2000 | -531 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -917 | -1248 | -1248 | -332 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -916 | -1248 | -1248 | -332 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -907 | -1248 | -1248 | -342 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -906 | -1248 | -1248 | -343 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -900 | -1248 | -1248 | -349 | 72 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1432 | 2000 | 2000 | -568 | 72 | []

## 0630Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3381
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 ON_1 | preventive | topological |  | helpful
[n/a] | RO_RA_00012 | PRA 400 kV Tantareni-Kozlodui 2 ON_1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1833 |  | 1836 | -3 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1807 |  | 1836 | -29 | 98 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1951 |  | -2000 | -49 | 98 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -966 |  | -999 | -33 | 97 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1934 |  | -2000 | -66 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 |  | 1836 | -93 | 95 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 |  | 1836 | -93 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1742 |  | 1836 | -94 | 95 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1732 |  | 1836 | -104 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 |  | 1836 | -111 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1723 |  | 1836 | -113 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1716 |  | 1836 | -120 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1679 |  | 1836 | -157 | 91 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1603 |  | 2000 | -397 | 80 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1594 |  | 2000 | -406 | 80 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1589 |  | 2000 | -411 | 79 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1572 |  | 2000 | -428 | 79 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1565 |  | 2000 | -435 | 78 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1554 |  | 2000 | -446 | 78 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1522 |  | 2000 | -478 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1500 |  | 2000 | -500 | 75 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1500 |  | 2000 | -500 | 75 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1500 |  | 2000 | -500 | 75 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1496 |  | 2000 | -504 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -920 |  | -1248 | -328 | 74 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1469 |  | 2000 | -531 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -917 |  | -1248 | -332 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -916 |  | -1248 | -332 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -907 |  | -1248 | -342 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -906 |  | -1248 | -343 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -900 |  | -1248 | -349 | 72 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1432 |  | 2000 | -568 | 72 | []

## 0730Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2373
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1832 | 1836 | 1836 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1824 | 1836 | 1836 | -12 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1764 | 1836 | 1836 | -72 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 | 1836 | 1836 | -130 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 | 1836 | 1836 | -131 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1701 | 1836 | 1836 | -135 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1688 | 1836 | 1836 | -148 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 | 1836 | 1836 | -170 | 91 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1519 | -2000 | -2000 | -481 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1509 | -2000 | -2000 | -491 | 75 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1407 | 2000 | 2000 | -593 | 70 | []

## 0730Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2373
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1832 |  | 1836 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1824 |  | 1836 | -12 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1764 |  | 1836 | -72 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1706 |  | 1836 | -130 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1705 |  | 1836 | -131 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1701 |  | 1836 | -135 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1688 |  | 1836 | -148 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 |  | 1836 | -170 | 91 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1519 |  | -2000 | -481 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1509 |  | -2000 | -491 | 75 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1407 |  | 2000 | -593 | 70 | []

## 0830Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2150
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 | 1836 | 1836 | -1 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 | 1836 | 1836 | -11 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1761 | 1836 | 1836 | -75 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1701 | 1836 | 1836 | -135 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 | 1836 | 1836 | -140 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1683 | 1836 | 1836 | -153 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 | 1836 | 1836 | -160 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1642 | 1836 | 1836 | -194 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 677 | 890 | 890 | -213 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -677 | -890 | -890 | -213 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -742 | -999 | -999 | -257 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [OPP] [RO] | RRESI22 _RTIMI22 _2:line | 684 | 960 | 960 | -276 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 682 | 960 | 960 | -278 | 71 | []

## 0830Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2150
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 |  | 1836 | -1 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 |  | 1836 | -11 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1761 |  | 1836 | -75 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1701 |  | 1836 | -135 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 |  | 1836 | -140 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1683 |  | 1836 | -153 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 |  | 1836 | -160 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1642 |  | 1836 | -194 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 677 |  | 890 | -213 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -677 |  | -890 | -213 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -742 |  | -999 | -257 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [OPP] [RO] | RRESI22 _RTIMI22 _2:line | 684 |  | 960 | -276 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 682 |  | 960 | -278 | 71 | []

## 0930Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2083
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 | 1836 | 1836 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 | 1836 | 1836 | -11 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1771 | 1836 | 1836 | -65 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1708 | 1836 | 1836 | -128 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 | 1836 | 1836 | -136 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 | 1836 | 1836 | -152 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 | 1836 | 1836 | -159 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1643 | 1836 | 1836 | -193 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -747 | -999 | -999 | -252 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 635 | 890 | 890 | -255 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -635 | -890 | -890 | -255 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [DIR] [RO] | RRESI22 _RTIMI22 _2:line | 679 | 960 | 960 | -281 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 676 | 960 | 960 | -284 | 70 | []

## 0930Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2083
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 |  | 1836 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 |  | 1836 | -11 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1771 |  | 1836 | -65 | 96 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1708 |  | 1836 | -128 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 |  | 1836 | -136 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 |  | 1836 | -152 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 |  | 1836 | -159 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1643 |  | 1836 | -193 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -747 |  | -999 | -252 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | 635 |  | 890 | -255 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -635 |  | -890 | -255 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [DIR] [RO] | RRESI22 _RTIMI22 _2:line | 679 |  | 960 | -281 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 676 |  | 960 | -284 | 70 | []

## 1030Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2055
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 | 1836 | 1836 | -1 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1830 | 1836 | 1836 | -6 | 100 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1770 | 1836 | 1836 | -66 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 | 1836 | 1836 | -132 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1694 | 1836 | 1836 | -142 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 | 1836 | 1836 | -151 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 | 1836 | 1836 | -163 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1641 | 1836 | 1836 | -195 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | -673 | -890 | -890 | -217 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -673 | -890 | -890 | -217 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -726 | -999 | -999 | -273 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [DIR] [RO] | RRESI22 _RTIMI22 _2:line | 688 | 960 | 960 | -272 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 686 | 960 | 960 | -274 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 686 | 970 | 970 | -284 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c2 [OPP] [RO] | RPDF222 _RRESI22 _1:line | 684 | 970 | 970 | -286 | 71 | []

## 1030Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2055
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 |  | 1836 | -1 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1830 |  | 1836 | -6 | 100 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1770 |  | 1836 | -66 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 |  | 1836 | -132 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1694 |  | 1836 | -142 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1685 |  | 1836 | -151 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 |  | 1836 | -163 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1641 |  | 1836 | -195 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | -673 |  | -890 | -217 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -673 |  | -890 | -217 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -726 |  | -999 | -273 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [DIR] [RO] | RRESI22 _RTIMI22 _2:line | 688 |  | 960 | -272 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 686 |  | 960 | -274 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 686 |  | 970 | -284 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c2 [OPP] [RO] | RPDF222 _RRESI22 _1:line | 684 |  | 970 | -286 | 71 | []

## 1130Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2070
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1833 | 1836 | 1836 | -3 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 | 1836 | 1836 | -11 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1763 | 1836 | 1836 | -73 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 | 1836 | 1836 | -136 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 | 1836 | 1836 | -152 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1680 | 1836 | 1836 | -156 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1668 | 1836 | 1836 | -168 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 | 1836 | 1836 | -202 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | -689 | -890 | -890 | -201 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -689 | -890 | -890 | -201 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -745 | -999 | -999 | -254 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [DIR] [RO] | RRESI22 _RTIMI22 _2:line | 702 | 960 | 960 | -258 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 700 | 960 | 960 | -260 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 692 | 970 | 970 | -278 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c2 [DIR] [RO] | RPDF222 _RRESI22 _1:line | 691 | 970 | 970 | -279 | 71 | []

## 1130Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2070
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1833 |  | 1836 | -3 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1825 |  | 1836 | -11 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1763 |  | 1836 | -73 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 |  | 1836 | -136 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 |  | 1836 | -152 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1680 |  | 1836 | -156 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1668 |  | 1836 | -168 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1634 |  | 1836 | -202 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | -689 |  | -890 | -201 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -689 |  | -890 | -201 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -745 |  | -999 | -254 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [DIR] [RO] | RRESI22 _RTIMI22 _2:line | 702 |  | 960 | -258 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 700 |  | 960 | -260 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 692 |  | 970 | -278 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c2 [DIR] [RO] | RPDF222 _RRESI22 _1:line | 691 |  | 970 | -279 | 71 | []

## 1230Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2185
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1836 | 1836 | 1836 | 0 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1824 | 1836 | 1836 | -12 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1750 | 1836 | 1836 | -86 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1689 | 1836 | 1836 | -147 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1675 | 1836 | 1836 | -161 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1669 | 1836 | 1836 | -167 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1660 | 1836 | 1836 | -176 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1625 | 1836 | 1836 | -211 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | -751 | -890 | -890 | -139 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -751 | -890 | -890 | -139 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [OPP] [RO] | RRESI22 _RTIMI22 _2:line | 721 | 960 | 960 | -239 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 719 | 960 | 960 | -241 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -747 | -999 | -999 | -252 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 704 | 970 | 970 | -266 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c2 [OPP] [RO] | RPDF222 _RRESI22 _1:line | 702 | 970 | 970 | -268 | 72 | []

## 1230Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2185
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1836 |  | 1836 | 0 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1824 |  | 1836 | -12 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1750 |  | 1836 | -86 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1689 |  | 1836 | -147 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1675 |  | 1836 | -161 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1669 |  | 1836 | -167 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1660 |  | 1836 | -176 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1625 |  | 1836 | -211 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | -751 |  | -890 | -139 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [OPP] [RO] | RPARO22 _RTRGJ22 _1:line | -751 |  | -890 | -139 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [OPP] [RO] | RRESI22 _RTIMI22 _2:line | 721 |  | 960 | -239 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 719 |  | 960 | -241 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -747 |  | -999 | -252 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 704 |  | 970 | -266 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c2 [OPP] [RO] | RPDF222 _RRESI22 _1:line | 702 |  | 970 | -268 | 72 | []

## 1330Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2273
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1832 | 1836 | 1836 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1823 | 1836 | 1836 | -13 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1741 | 1836 | 1836 | -95 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 | 1836 | 1836 | -158 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 | 1836 | 1836 | -163 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 | 1836 | 1836 | -177 | 90 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1655 | 1836 | 1836 | -181 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | -785 | -890 | -890 | -105 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -785 | -890 | -890 | -105 | 88 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1618 | 1836 | 1836 | -218 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -767 | -999 | -999 | -232 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [DIR] [RO] | RRESI22 _RTIMI22 _2:line | 725 | 960 | 960 | -235 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 723 | 960 | 960 | -237 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 714 | 970 | 970 | -256 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c2 [OPP] [RO] | RPDF222 _RRESI22 _1:line | 712 | 970 | 970 | -258 | 73 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1427 | -2000 | -2000 | -573 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1418 | -2000 | -2000 | -582 | 71 | []

## 1330Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2273
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1832 |  | 1836 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1823 |  | 1836 | -13 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1741 |  | 1836 | -95 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1678 |  | 1836 | -158 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1673 |  | 1836 | -163 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1659 |  | 1836 | -177 | 90 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1655 |  | 1836 | -181 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [DIR] [RO] | RURE212 _RTRGJ22 _1:line | -785 |  | -890 | -105 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -785 |  | -890 | -105 | 88 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1618 |  | 1836 | -218 | 88 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -767 |  | -999 | -232 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [DIR] [RO] | RRESI22 _RTIMI22 _2:line | 725 |  | 960 | -235 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [OPP] [RO] | RRESI12 _RTIMI12 _1:line | 723 |  | 960 | -237 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c1 [OPP] [RO] | RPDF212 _RRESI12 _1:line | 714 |  | 970 | -256 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c2 [OPP] [RO] | RPDF222 _RRESI22 _1:line | 712 |  | 970 | -258 | 73 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1427 |  | -2000 | -573 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1418 |  | -2000 | -582 | 71 | []

## 1430Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2396
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 | 1836 | 1836 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1822 | 1836 | 1836 | -14 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 | 1836 | 1836 | -93 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 | 1836 | 1836 | -152 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 | 1836 | 1836 | -160 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 | 1836 | 1836 | -170 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1661 | 1836 | 1836 | -175 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1628 | 1836 | 1836 | -208 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | -752 | -890 | -890 | -138 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -752 | -890 | -890 | -138 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1584 | -2000 | -2000 | -416 | 79 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1573 | -2000 | -2000 | -427 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -738 | -999 | -999 | -261 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [OPP] [RO] | RRESI22 _RTIMI22 _2:line | 707 | 960 | 960 | -253 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 705 | 960 | 960 | -255 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 697 | 970 | 970 | -273 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c2 [DIR] [RO] | RPDF222 _RRESI22 _1:line | 695 | 970 | 970 | -275 | 72 | []

## 1430Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2396
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 |  | 1836 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1822 |  | 1836 | -14 | 99 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 |  | 1836 | -93 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 |  | 1836 | -152 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 |  | 1836 | -160 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1666 |  | 1836 | -170 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1661 |  | 1836 | -175 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1628 |  | 1836 | -208 | 89 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | -752 |  | -890 | -138 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -752 |  | -890 | -138 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1584 |  | -2000 | -416 | 79 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1573 |  | -2000 | -427 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -738 |  | -999 | -261 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c2 [OPP] [RO] | RRESI22 _RTIMI22 _2:line | 707 |  | 960 | -253 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Resita-Timisoara c1 [DIR] [RO] | RRESI12 _RTIMI12 _1:line | 705 |  | 960 | -255 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c1 [DIR] [RO] | RPDF212 _RRESI12 _1:line | 697 |  | 970 | -273 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Portile de Fier-Resita c2 [DIR] [RO] | RPDF222 _RRESI22 _1:line | 695 |  | 970 | -275 | 72 | []

## 1530Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2520
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1830 | 1836 | 1836 | -6 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1818 | 1836 | 1836 | -18 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1728 | 1836 | 1836 | -108 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 | 1836 | 1836 | -111 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 | 1836 | 1836 | -136 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 | 1836 | 1836 | -144 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 | 1836 | 1836 | -160 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1657 | 1836 | 1836 | -179 | 90 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1725 | -2000 | -2000 | -275 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1713 | -2000 | -2000 | -287 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 635 | 890 | 890 | -255 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -635 | -890 | -890 | -255 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2520
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1830 |  | 1836 | -6 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1818 |  | 1836 | -18 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1728 |  | 1836 | -108 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1725 |  | 1836 | -111 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 |  | 1836 | -136 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1692 |  | 1836 | -144 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1676 |  | 1836 | -160 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1657 |  | 1836 | -179 | 90 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1725 |  | -2000 | -275 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1713 |  | -2000 | -287 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Urechesti-Targu Jiu Nord [OPP] [RO] | RURE212 _RTRGJ22 _1:line | 635 |  | 890 | -255 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] Paroseni-Targu Jiu Nord [DIR] [RO] | RPARO22 _RTRGJ22 _1:line | -635 |  | -890 | -255 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2512
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1830 | 1836 | 1836 | -6 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1820 | 1836 | 1836 | -16 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 | 1836 | 1836 | -79 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1744 | 1836 | 1836 | -92 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1716 | 1836 | 1836 | -120 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 | 1836 | 1836 | -125 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1695 | 1836 | 1836 | -141 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1675 | 1836 | 1836 | -161 | 91 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1773 | 2000 | 2000 | -227 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1699 | -2000 | -2000 | -301 | 85 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1688 | -2000 | -2000 | -312 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1626 | 2000 | 2000 | -374 | 81 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1609 | 2000 | 2000 | -391 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1532 | 2000 | 2000 | -468 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1520 | 2000 | 2000 | -480 | 76 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1516 | 2000 | 2000 | -484 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1507 | 2000 | 2000 | -493 | 75 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1493 | 2000 | 2000 | -507 | 75 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1464 | 2000 | 2000 | -536 | 73 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1458 | 2000 | 2000 | -542 | 73 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1431 | 2000 | 2000 | -569 | 72 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1406 | 2000 | 2000 | -594 | 70 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -877 | -1248 | -1248 | -372 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2512
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1830 |  | 1836 | -6 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1820 |  | 1836 | -16 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1757 |  | 1836 | -79 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1744 |  | 1836 | -92 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1716 |  | 1836 | -120 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1711 |  | 1836 | -125 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1695 |  | 1836 | -141 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1675 |  | 1836 | -161 | 91 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1773 |  | 2000 | -227 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1699 |  | -2000 | -301 | 85 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1688 |  | -2000 | -312 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1626 |  | 2000 | -374 | 81 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1609 |  | 2000 | -391 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1532 |  | 2000 | -468 | 77 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1520 |  | 2000 | -480 | 76 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1516 |  | 2000 | -484 | 76 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1507 |  | 2000 | -493 | 75 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1493 |  | 2000 | -507 | 75 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1464 |  | 2000 | -536 | 73 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1458 |  | 2000 | -542 | 73 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1431 |  | 2000 | -569 | 72 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1406 |  | 2000 | -594 | 70 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -877 |  | -1248 | -372 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2558
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1830 | 1836 | 1836 | -6 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1811 | 1836 | 1836 | -25 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1762 | 1836 | 1836 | -74 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 | 1836 | 1836 | -93 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1893 | 2000 | 2000 | -107 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 | 1836 | 1836 | -121 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1714 | 1836 | 1836 | -122 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 | 1836 | 1836 | -136 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1682 | 1836 | 1836 | -154 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1781 | 2000 | 2000 | -219 | 89 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1780 | 2000 | 2000 | -220 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1762 | -2000 | -2000 | -238 | 88 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1750 | -2000 | -2000 | -250 | 88 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1685 | 2000 | 2000 | -315 | 84 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1675 | 2000 | 2000 | -325 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1656 | 2000 | 2000 | -344 | 83 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1643 | 2000 | 2000 | -357 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1643 | 2000 | 2000 | -357 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1635 | 2000 | 2000 | -365 | 82 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1632 | 2000 | 2000 | -368 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1605 | 2000 | 2000 | -395 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1604 | 2000 | 2000 | -396 | 80 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1586 | 2000 | 2000 | -414 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1541 | 2000 | 2000 | -459 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1508 | 2000 | 2000 | -492 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1491 | 2000 | 2000 | -509 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -908 | -1248 | -1248 | -341 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -893 | -1248 | -1248 | -356 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -891 | -1248 | -1248 | -357 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -885 | -1248 | -1248 | -364 | 71 | []

## 1730Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2558
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1830 |  | 1836 | -6 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1811 |  | 1836 | -25 | 99 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1762 |  | 1836 | -74 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 |  | 1836 | -93 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1893 |  | 2000 | -107 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 |  | 1836 | -121 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1714 |  | 1836 | -122 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 |  | 1836 | -136 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1682 |  | 1836 | -154 | 92 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1781 |  | 2000 | -219 | 89 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1780 |  | 2000 | -220 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1762 |  | -2000 | -238 | 88 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1750 |  | -2000 | -250 | 88 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1685 |  | 2000 | -315 | 84 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1675 |  | 2000 | -325 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1656 |  | 2000 | -344 | 83 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1643 |  | 2000 | -357 | 82 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1643 |  | 2000 | -357 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1635 |  | 2000 | -365 | 82 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1632 |  | 2000 | -368 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1605 |  | 2000 | -395 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1604 |  | 2000 | -396 | 80 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1586 |  | 2000 | -414 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1541 |  | 2000 | -459 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1508 |  | 2000 | -492 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1491 |  | 2000 | -509 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -908 |  | -1248 | -341 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -893 |  | -1248 | -356 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -891 |  | -1248 | -357 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -885 |  | -1248 | -364 | 71 | []

## 1830Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2451
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1830 | 1836 | 1836 | -6 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1808 | 1836 | 1836 | -28 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1768 | 1836 | 1836 | -68 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 | 1836 | 1836 | -93 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 | 1836 | 1836 | -121 | 93 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1867 | 2000 | 2000 | -133 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1714 | 1836 | 1836 | -122 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 | 1836 | 1836 | -136 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 | 1836 | 1836 | -159 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1818 | -2000 | -2000 | -182 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1795 | 2000 | 2000 | -205 | 90 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1715 | -2000 | -2000 | -285 | 86 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1688 | 2000 | 2000 | -312 | 84 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1680 | 2000 | 2000 | -320 | 84 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1675 | 2000 | 2000 | -325 | 84 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1668 | -2000 | -2000 | -332 | 83 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1664 | -2000 | -2000 | -336 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1652 | -2000 | -2000 | -348 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1644 | -2000 | -2000 | -356 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1628 | 2000 | 2000 | -372 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1619 | -2000 | -2000 | -381 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1614 | -2000 | -2000 | -386 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1604 | -2000 | -2000 | -396 | 80 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1570 | 2000 | 2000 | -430 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1552 | 2000 | 2000 | -448 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1536 | 2000 | 2000 | -464 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -915 | -1248 | -1248 | -334 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -910 | -1248 | -1248 | -338 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -910 | -1248 | -1248 | -338 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -900 | -1248 | -1248 | -349 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -898 | -1248 | -1248 | -350 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -892 | -1248 | -1248 | -357 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2451
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1830 |  | 1836 | -6 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1808 |  | 1836 | -28 | 98 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1768 |  | 1836 | -68 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1743 |  | 1836 | -93 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1715 |  | 1836 | -121 | 93 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1867 |  | 2000 | -133 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1714 |  | 1836 | -122 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1700 |  | 1836 | -136 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1677 |  | 1836 | -159 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1818 |  | -2000 | -182 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1795 |  | 2000 | -205 | 90 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1715 |  | -2000 | -285 | 86 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1688 |  | 2000 | -312 | 84 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1680 |  | 2000 | -320 | 84 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1675 |  | 2000 | -325 | 84 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1668 |  | -2000 | -332 | 83 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1664 |  | -2000 | -336 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1652 |  | -2000 | -348 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1644 |  | -2000 | -356 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1628 |  | 2000 | -372 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1619 |  | -2000 | -381 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1614 |  | -2000 | -386 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1604 |  | -2000 | -396 | 80 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1570 |  | 2000 | -430 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1552 |  | 2000 | -448 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1536 |  | 2000 | -464 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -915 |  | -1248 | -334 | 73 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -910 |  | -1248 | -338 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -910 |  | -1248 | -338 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -900 |  | -1248 | -349 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -898 |  | -1248 | -350 | 72 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -892 |  | -1248 | -357 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2995
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 | 1836 | 1836 | -1 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -958 | -999 | -999 | -41 | 96 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1901 | 2000 | 2000 | -99 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1872 | 2000 | 2000 | -128 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1855 | 2000 | 2000 | -145 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 | 1836 | 1836 | -140 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1824 | 2000 | 2000 | -176 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1667 | 1836 | 1836 | -169 | 91 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1784 | 2000 | 2000 | -216 | 89 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1782 | 2000 | 2000 | -218 | 89 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1776 | 2000 | 2000 | -224 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1615 | 1836 | 1836 | -221 | 88 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1756 | 2000 | 2000 | -244 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1609 | 1836 | 1836 | -227 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1749 | 2000 | 2000 | -251 | 87 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1741 | 2000 | 2000 | -259 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1739 | 2000 | 2000 | -261 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1595 | 1836 | 1836 | -241 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1592 | 1836 | 1836 | -244 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1730 | 2000 | 2000 | -270 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1588 | 1836 | 1836 | -248 | 86 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1724 | 2000 | 2000 | -276 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | -1368 | -1600 | -1600 | -232 | 86 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1691 | -2000 | -2000 | -309 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1551 | 1836 | 1836 | -285 | 84 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1688 | 2000 | 2000 | -312 | 84 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1679 | -2000 | -2000 | -321 | 84 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1593 | 2000 | 2000 | -407 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1575 | 2000 | 2000 | -425 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -940 | -1248 | -1248 | -308 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -937 | -1248 | -1248 | -312 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -936 | -1248 | -1248 | -313 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -927 | -1248 | -1248 | -322 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -927 | -1248 | -1248 | -322 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -920 | -1248 | -1248 | -328 | 74 | []

## 1930Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2995
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1835 |  | 1836 | -1 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -958 |  | -999 | -41 | 96 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1901 |  | 2000 | -99 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1872 |  | 2000 | -128 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1855 |  | 2000 | -145 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1696 |  | 1836 | -140 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1824 |  | 2000 | -176 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1667 |  | 1836 | -169 | 91 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1784 |  | 2000 | -216 | 89 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1782 |  | 2000 | -218 | 89 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1776 |  | 2000 | -224 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1615 |  | 1836 | -221 | 88 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1756 |  | 2000 | -244 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1609 |  | 1836 | -227 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1749 |  | 2000 | -251 | 87 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1741 |  | 2000 | -259 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1739 |  | 2000 | -261 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1595 |  | 1836 | -241 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1592 |  | 1836 | -244 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1730 |  | 2000 | -270 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1588 |  | 1836 | -248 | 86 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1724 |  | 2000 | -276 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | -1368 |  | -1600 | -232 | 86 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1691 |  | -2000 | -309 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1551 |  | 1836 | -285 | 84 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1688 |  | 2000 | -312 | 84 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1679 |  | -2000 | -321 | 84 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1593 |  | 2000 | -407 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1575 |  | 2000 | -425 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -940 |  | -1248 | -308 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -937 |  | -1248 | -312 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -936 |  | -1248 | -313 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -927 |  | -1248 | -322 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -927 |  | -1248 | -322 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -920 |  | -1248 | -328 | 74 | []

## 2030Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3020
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 | 1836 | 1836 | -2 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -955 | -999 | -999 | -44 | 96 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1894 | 2000 | 2000 | -106 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1884 | 2000 | 2000 | -116 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1864 | 2000 | 2000 | -136 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1863 | 2000 | 2000 | -137 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 | 1836 | 1836 | -152 | 92 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1811 | 2000 | 2000 | -189 | 91 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1811 | 2000 | 2000 | -189 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1656 | 1836 | 1836 | -180 | 90 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1800 | 2000 | 2000 | -200 | 90 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1785 | 2000 | 2000 | -215 | 89 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1779 | 2000 | 2000 | -221 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1779 | 2000 | 2000 | -221 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1756 | 2000 | 2000 | -244 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 | 1836 | 1836 | -230 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1747 | 2000 | 2000 | -253 | 87 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1742 | 2000 | 2000 | -258 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1599 | 1836 | 1836 | -237 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | -1387 | -1600 | -1600 | -213 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1584 | 1836 | 1836 | -252 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1582 | 1836 | 1836 | -254 | 86 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1722 | 2000 | 2000 | -278 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1579 | 1836 | 1836 | -257 | 86 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1718 | -2000 | -2000 | -282 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1705 | -2000 | -2000 | -295 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1542 | 1836 | 1836 | -294 | 84 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1615 | 2000 | 2000 | -385 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1596 | 2000 | 2000 | -404 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -947 | -1248 | -1248 | -301 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -944 | -1248 | -1248 | -304 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -943 | -1248 | -1248 | -306 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -934 | -1248 | -1248 | -315 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -934 | -1248 | -1248 | -315 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -928 | -1248 | -1248 | -321 | 74 | []

## 2030Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3020
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1834 |  | 1836 | -2 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -955 |  | -999 | -44 | 96 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1894 |  | 2000 | -106 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1884 |  | 2000 | -116 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1864 |  | 2000 | -136 | 93 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1863 |  | 2000 | -137 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 |  | 1836 | -152 | 92 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1811 |  | 2000 | -189 | 91 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1811 |  | 2000 | -189 | 91 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1656 |  | 1836 | -180 | 90 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1800 |  | 2000 | -200 | 90 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1785 |  | 2000 | -215 | 89 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1779 |  | 2000 | -221 | 89 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1779 |  | 2000 | -221 | 89 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1756 |  | 2000 | -244 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 |  | 1836 | -230 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1747 |  | 2000 | -253 | 87 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1742 |  | 2000 | -258 | 87 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1599 |  | 1836 | -237 | 87 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | -1387 |  | -1600 | -213 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1584 |  | 1836 | -252 | 86 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1582 |  | 1836 | -254 | 86 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1722 |  | 2000 | -278 | 86 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1579 |  | 1836 | -257 | 86 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1718 |  | -2000 | -282 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1705 |  | -2000 | -295 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1542 |  | 1836 | -294 | 84 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1615 |  | 2000 | -385 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1596 |  | 2000 | -404 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -947 |  | -1248 | -301 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -944 |  | -1248 | -304 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -943 |  | -1248 | -306 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -934 |  | -1248 | -315 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -934 |  | -1248 | -315 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -928 |  | -1248 | -321 | 74 | []

## 2130Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2935
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 | 1836 | 1836 | -5 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -994 | -999 | -999 | -5 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1883 | 2000 | 2000 | -117 | 94 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1877 | 2000 | 2000 | -123 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1872 | 2000 | 2000 | -128 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1854 | 2000 | 2000 | -146 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 | 1836 | 1836 | -138 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 | 1836 | 1836 | -166 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1789 | 2000 | 2000 | -211 | 89 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1779 | 2000 | 2000 | -221 | 89 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1778 | 2000 | 2000 | -222 | 89 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1766 | 2000 | 2000 | -234 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1621 | 1836 | 1836 | -215 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1618 | 1836 | 1836 | -218 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1758 | 2000 | 2000 | -242 | 88 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1755 | 2000 | 2000 | -245 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1598 | 1836 | 1836 | -238 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1595 | 1836 | 1836 | -241 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1737 | 2000 | 2000 | -263 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1590 | 1836 | 1836 | -246 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1728 | 2000 | 2000 | -272 | 86 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1724 | 2000 | 2000 | -276 | 86 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1700 | 2000 | 2000 | -300 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | -1356 | -1600 | -1600 | -244 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1553 | 1836 | 1836 | -283 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1623 | -2000 | -2000 | -377 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1611 | -2000 | -2000 | -389 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1610 | 2000 | 2000 | -390 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1593 | 2000 | 2000 | -407 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -937 | -1248 | -1248 | -311 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -934 | -1248 | -1248 | -314 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -933 | -1248 | -1248 | -316 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -924 | -1248 | -1248 | -325 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -924 | -1248 | -1248 | -325 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -918 | -1248 | -1248 | -331 | 73 | []

## 2130Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2935
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1831 |  | 1836 | -5 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -994 |  | -999 | -5 | 100 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1883 |  | 2000 | -117 | 94 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1877 |  | 2000 | -123 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1872 |  | 2000 | -128 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1854 |  | 2000 | -146 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1698 |  | 1836 | -138 | 92 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1670 |  | 1836 | -166 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1789 |  | 2000 | -211 | 89 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1779 |  | 2000 | -221 | 89 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1778 |  | 2000 | -222 | 89 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1766 |  | 2000 | -234 | 88 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1621 |  | 1836 | -215 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1618 |  | 1836 | -218 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1758 |  | 2000 | -242 | 88 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1755 |  | 2000 | -245 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1598 |  | 1836 | -238 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1595 |  | 1836 | -241 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1737 |  | 2000 | -263 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1590 |  | 1836 | -246 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1728 |  | 2000 | -272 | 86 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1724 |  | 2000 | -276 | 86 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1700 |  | 2000 | -300 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | -1356 |  | -1600 | -244 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1553 |  | 1836 | -283 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1623 |  | -2000 | -377 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1611 |  | -2000 | -389 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1610 |  | 2000 | -390 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1593 |  | 2000 | -407 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -937 |  | -1248 | -311 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -934 |  | -1248 | -314 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -933 |  | -1248 | -316 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -924 |  | -1248 | -325 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -924 |  | -1248 | -325 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -918 |  | -1248 | -331 | 73 | []

## 2230Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2733
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -998 | -999 | -999 | -1 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1766 | 1836 | 1836 | -70 | 96 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1709 | 1836 | 1836 | -127 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 | 1836 | 1836 | -152 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1616 | 1836 | 1836 | -220 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1607 | 1836 | 1836 | -229 | 88 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1743 | 2000 | 2000 | -257 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1595 | 1836 | 1836 | -241 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1592 | 1836 | 1836 | -244 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1735 | 2000 | 2000 | -265 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1586 | 1836 | 1836 | -250 | 86 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1720 | 2000 | 2000 | -280 | 86 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1706 | 2000 | 2000 | -294 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1548 | 1836 | 1836 | -288 | 84 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1650 | 2000 | 2000 | -350 | 83 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1647 | 2000 | 2000 | -353 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1647 | 2000 | 2000 | -353 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1631 | 2000 | 2000 | -369 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1629 | 2000 | 2000 | -371 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1626 | 2000 | 2000 | -374 | 81 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1622 | 2000 | 2000 | -378 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1612 | 2000 | 2000 | -388 | 81 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1606 | 2000 | 2000 | -394 | 80 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1582 | 2000 | 2000 | -418 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | -1227 | -1600 | -1600 | -373 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1517 | -2000 | -2000 | -483 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1504 | -2000 | -2000 | -496 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1483 | 2000 | 2000 | -517 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1467 | 2000 | 2000 | -533 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -897 | -1248 | -1248 | -351 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -894 | -1248 | -1248 | -354 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -893 | -1248 | -1248 | -355 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -884 | -1248 | -1248 | -364 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -884 | -1248 | -1248 | -364 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -878 | -1248 | -1248 | -371 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2733
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -998 |  | -999 | -1 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1766 |  | 1836 | -70 | 96 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1709 |  | 1836 | -127 | 93 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1684 |  | 1836 | -152 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1616 |  | 1836 | -220 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1607 |  | 1836 | -229 | 88 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1743 |  | 2000 | -257 | 87 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1595 |  | 1836 | -241 | 87 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1592 |  | 1836 | -244 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1735 |  | 2000 | -265 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1586 |  | 1836 | -250 | 86 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1720 |  | 2000 | -280 | 86 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1706 |  | 2000 | -294 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1548 |  | 1836 | -288 | 84 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1650 |  | 2000 | -350 | 83 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1647 |  | 2000 | -353 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1647 |  | 2000 | -353 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1631 |  | 2000 | -369 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1629 |  | 2000 | -371 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1626 |  | 2000 | -374 | 81 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1622 |  | 2000 | -378 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1612 |  | 2000 | -388 | 81 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1606 |  | 2000 | -394 | 80 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1582 |  | 2000 | -418 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | -1227 |  | -1600 | -373 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1517 |  | -2000 | -483 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1504 |  | -2000 | -496 | 75 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1483 |  | 2000 | -517 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1467 |  | 2000 | -533 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -897 |  | -1248 | -351 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -894 |  | -1248 | -354 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -893 |  | -1248 | -355 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -884 |  | -1248 | -364 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -884 |  | -1248 | -364 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -878 |  | -1248 | -371 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2839
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -999 | -999 | -999 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1805 | 1836 | 1836 | -31 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 | 1836 | 1836 | -114 | 94 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 | 1836 | 1836 | -132 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1790 | 2000 | 2000 | -210 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1636 | 1836 | 1836 | -200 | 89 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1781 | 2000 | 2000 | -219 | 89 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1777 | 2000 | 2000 | -223 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1760 | 2000 | 2000 | -240 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1613 | 1836 | 1836 | -223 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1613 | 1836 | 1836 | -223 | 88 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 | 1836 | 1836 | -230 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 | 1836 | 1836 | -236 | 87 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1709 | 2000 | 2000 | -291 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 | 1836 | 1836 | -268 | 85 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1706 | 2000 | 2000 | -294 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1702 | 2000 | 2000 | -298 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1688 | 2000 | 2000 | -312 | 84 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1684 | 2000 | 2000 | -316 | 84 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1684 | 2000 | 2000 | -316 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1673 | 2000 | 2000 | -327 | 84 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1665 | 2000 | 2000 | -335 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1660 | 2000 | 2000 | -340 | 83 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1634 | 2000 | 2000 | -366 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | -1273 | -1600 | -1600 | -327 | 80 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1591 | -2000 | -2000 | -409 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1578 | -2000 | -2000 | -422 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1529 | 2000 | 2000 | -471 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1512 | 2000 | 2000 | -488 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -905 | -1248 | -1248 | -343 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -902 | -1248 | -1248 | -347 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -901 | -1248 | -1248 | -348 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -892 | -1248 | -1248 | -357 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -891 | -1248 | -1248 | -357 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -885 | -1248 | -1248 | -363 | 71 | []

## 2330Curative
Detailed results
Generated at: | 2024-04-21 19:05
Business day: | 22.04.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2839
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 ON_2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -999 |  | -999 | 0 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1805 |  | 1836 | -31 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1722 |  | 1836 | -114 | 94 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1704 |  | 1836 | -132 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1790 |  | 2000 | -210 | 89 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1636 |  | 1836 | -200 | 89 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1781 |  | 2000 | -219 | 89 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1777 |  | 2000 | -223 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1760 |  | 2000 | -240 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1613 |  | 1836 | -223 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1613 |  | 1836 | -223 | 88 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1606 |  | 1836 | -230 | 87 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1600 |  | 1836 | -236 | 87 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1709 |  | 2000 | -291 | 85 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1836 | -268 | 85 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1706 |  | 2000 | -294 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1702 |  | 2000 | -298 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1688 |  | 2000 | -312 | 84 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1684 |  | 2000 | -316 | 84 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1684 |  | 2000 | -316 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1673 |  | 2000 | -327 | 84 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1665 |  | 2000 | -335 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1660 |  | 2000 | -340 | 83 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1634 |  | 2000 | -366 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | -1273 |  | -1600 | -327 | 80 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1591 |  | -2000 | -409 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1578 |  | -2000 | -422 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1529 |  | 2000 | -471 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1512 |  | 2000 | -488 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -905 |  | -1248 | -343 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -902 |  | -1248 | -347 | 72 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -901 |  | -1248 | -348 | 72 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -892 |  | -1248 | -357 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -891 |  | -1248 | -357 | 71 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -885 |  | -1248 | -363 | 71 | []