## 1230Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2276
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1593 | 1600 | 1600 | -7 | 100 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1476 | 1600 | 1600 | -124 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1448 | 1600 | 1600 | -152 | 91 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1418 | 1600 | 1600 | -182 | 89 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1418 | 1600 | 1600 | -182 | 89 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1394 | 1600 | 1600 | -206 | 87 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1356 | 1600 | 1600 | -244 | 85 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1350 | 1600 | 1600 | -250 | 84 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1318 | 1600 | 1600 | -282 | 82 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1294 | 1600 | 1600 | -306 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1277 | 1600 | 1600 | -323 | 80 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1252 | 1600 | 1600 | -348 | 78 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BC | Base Case | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1189 | 1600 | 1600 | -411 | 74 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1173 | 1600 | 1600 | -427 | 73 | []

## 1230Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2276
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1593 |  | 1600 | -7 | 100 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1476 |  | 1600 | -124 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1448 |  | 1600 | -152 | 91 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1418 |  | 1600 | -182 | 89 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1418 |  | 1600 | -182 | 89 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1394 |  | 1600 | -206 | 87 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1356 |  | 1600 | -244 | 85 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1350 |  | 1600 | -250 | 84 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1318 |  | 1600 | -282 | 82 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1294 |  | 1600 | -306 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1277 |  | 1600 | -323 | 80 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1267 |  | 1600 | -333 | 79 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1261 |  | 1600 | -339 | 79 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1253 |  | 1600 | -347 | 78 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1252 |  | 1600 | -348 | 78 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1248 |  | 1600 | -352 | 78 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1245 |  | 1600 | -355 | 78 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1244 |  | 1600 | -356 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1243 |  | 1600 | -357 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1242 |  | 1600 | -358 | 78 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1239 |  | 1600 | -361 | 77 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1236 |  | 1600 | -364 | 77 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1234 |  | 1600 | -366 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1234 |  | 1600 | -366 | 77 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1234 |  | 1600 | -366 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1234 |  | 1600 | -366 | 77 | []
BC | Base Case | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1233 |  | 1600 | -367 | 77 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1232 |  | 1600 | -368 | 77 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1232 |  | 1600 | -368 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1231 |  | 1600 | -369 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1226 |  | 1600 | -374 | 77 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1189 |  | 1600 | -411 | 74 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1173 |  | 1600 | -427 | 73 | []

## 1330Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2292
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 | 1600 | 1600 | -5 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1454 | 1600 | 1600 | -146 | 91 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1405 | 1600 | 1600 | -195 | 88 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1377 | 1600 | 1600 | -223 | 86 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1377 | 1600 | 1600 | -223 | 86 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1347 | 1600 | 1600 | -253 | 84 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1304 | 1600 | 1600 | -296 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1292 | 1600 | 1600 | -308 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1207 | 1600 | 1600 | -393 | 75 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1202 | 1600 | 1600 | -398 | 75 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1198 | 1600 | 1600 | -402 | 75 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1195 | 1600 | 1600 | -405 | 75 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1190 | 1600 | 1600 | -410 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
BC | Base Case | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1186 | 1600 | 1600 | -414 | 74 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1186 | 1600 | 1600 | -414 | 74 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1181 | 1600 | 1600 | -419 | 74 | []

## 1330Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2292
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 |  | 1600 | -5 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1454 |  | 1600 | -146 | 91 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1405 |  | 1600 | -195 | 88 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1377 |  | 1600 | -223 | 86 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1377 |  | 1600 | -223 | 86 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1347 |  | 1600 | -253 | 84 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1304 |  | 1600 | -296 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1292 |  | 1600 | -308 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1260 |  | 1600 | -340 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1241 |  | 1600 | -359 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1225 |  | 1600 | -375 | 77 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1222 |  | 1600 | -378 | 76 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1211 |  | 1600 | -389 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1207 |  | 1600 | -393 | 75 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1206 |  | 1600 | -394 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1202 |  | 1600 | -398 | 75 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1201 |  | 1600 | -399 | 75 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1199 |  | 1600 | -401 | 75 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1198 |  | 1600 | -402 | 75 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1195 |  | 1600 | -405 | 75 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1194 |  | 1600 | -406 | 75 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1190 |  | 1600 | -410 | 74 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1188 |  | 1600 | -412 | 74 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1188 |  | 1600 | -412 | 74 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1188 |  | 1600 | -412 | 74 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1188 |  | 1600 | -412 | 74 | []
BC | Base Case | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1187 |  | 1600 | -413 | 74 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1186 |  | 1600 | -414 | 74 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1186 |  | 1600 | -414 | 74 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1185 |  | 1600 | -415 | 74 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1181 |  | 1600 | -419 | 74 | []

## 1430Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2288
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1597 | 1600 | 1600 | -3 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1457 | 1600 | 1600 | -143 | 91 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1364 | 1600 | 1600 | -236 | 85 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1355 | 1600 | 1600 | -245 | 85 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1355 | 1600 | 1600 | -245 | 85 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1322 | 1600 | 1600 | -278 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1274 | 1600 | 1600 | -326 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 | 1600 | 1600 | -370 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 76 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1198 | 1600 | 1600 | -402 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1196 | 1600 | 1600 | -404 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1177 | 1600 | 1600 | -423 | 74 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1177 | 1600 | 1600 | -423 | 74 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1173 | 1600 | 1600 | -427 | 73 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1170 | 1600 | 1600 | -430 | 73 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1168 | 1600 | 1600 | -432 | 73 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
BC | Base Case | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1157 | 1600 | 1600 | -443 | 72 | []

## 1430Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2288
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1597 |  | 1600 | -3 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1457 |  | 1600 | -143 | 91 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1364 |  | 1600 | -236 | 85 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1355 |  | 1600 | -245 | 85 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1355 |  | 1600 | -245 | 85 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1322 |  | 1600 | -278 | 83 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1274 |  | 1600 | -326 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1254 |  | 1600 | -346 | 78 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 |  | 1600 | -370 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1228 |  | 1600 | -372 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1210 |  | 1600 | -390 | 76 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 76 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1198 |  | 1600 | -402 | 75 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1196 |  | 1600 | -404 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1183 |  | 1600 | -417 | 74 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1183 |  | 1600 | -417 | 74 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1181 |  | 1600 | -419 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1178 |  | 1600 | -422 | 74 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1177 |  | 1600 | -423 | 74 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1177 |  | 1600 | -423 | 74 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1173 |  | 1600 | -427 | 73 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1170 |  | 1600 | -430 | 73 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1168 |  | 1600 | -432 | 73 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1166 |  | 1600 | -434 | 73 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1164 |  | 1600 | -436 | 73 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1164 |  | 1600 | -436 | 73 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1163 |  | 1600 | -437 | 73 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1163 |  | 1600 | -437 | 73 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1163 |  | 1600 | -437 | 73 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1163 |  | 1600 | -437 | 73 | []
BC | Base Case | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1163 |  | 1600 | -437 | 73 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1161 |  | 1600 | -439 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1157 |  | 1600 | -443 | 72 | []

## 1530Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2327
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1593 | 1600 | 1600 | -7 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1464 | 1600 | 1600 | -136 | 92 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1271 | 1600 | 1600 | -329 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1259 | 1600 | 1600 | -341 | 79 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1156 | 1600 | 1600 | -444 | 72 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1129 | 1600 | 1600 | -471 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2327
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1593 |  | 1600 | -7 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1464 |  | 1600 | -136 | 92 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1271 |  | 1600 | -329 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1259 |  | 1600 | -341 | 79 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1258 |  | 1600 | -342 | 79 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1235 |  | 1600 | -365 | 77 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1213 |  | 1600 | -387 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1158 |  | 1600 | -442 | 72 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1156 |  | 1600 | -444 | 72 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1129 |  | 1600 | -471 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2442
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1596 | 1600 | 1600 | -4 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1491 | 1600 | 1600 | -109 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 | 1600 | 1600 | -233 | 85 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1341 | 1600 | 1600 | -259 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1197 | 1600 | 1600 | -403 | 75 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1191 | 1600 | 1600 | -409 | 74 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1186 | 1600 | 1600 | -414 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1178 | 1600 | 1600 | -422 | 74 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1169 | 1600 | 1600 | -431 | 73 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1168 | 1600 | 1600 | -432 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1150 | 1600 | 1600 | -450 | 72 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1146 | 1600 | 1600 | -454 | 72 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1137 | 1600 | 1600 | -463 | 71 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1136 | 1600 | 1600 | -464 | 71 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1135 | 1600 | 1600 | -465 | 71 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1131 | 1600 | 1600 | -469 | 71 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1131 | 1600 | 1600 | -469 | 71 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1129 | 1600 | 1600 | -471 | 71 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1121 | 1600 | 1600 | -479 | 70 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1120 | 1600 | 1600 | -480 | 70 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1120 | 1600 | 1600 | -480 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2442
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1596 |  | 1600 | -4 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1491 |  | 1600 | -109 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 |  | 1600 | -233 | 85 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1341 |  | 1600 | -259 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 |  | 1600 | -385 | 76 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1197 |  | 1600 | -403 | 75 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1191 |  | 1600 | -409 | 74 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1186 |  | 1600 | -414 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1178 |  | 1600 | -422 | 74 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1169 |  | 1600 | -431 | 73 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1168 |  | 1600 | -432 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1150 |  | 1600 | -450 | 72 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1146 |  | 1600 | -454 | 72 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1137 |  | 1600 | -463 | 71 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1136 |  | 1600 | -464 | 71 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1135 |  | 1600 | -465 | 71 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1131 |  | 1600 | -469 | 71 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1131 |  | 1600 | -469 | 71 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1129 |  | 1600 | -471 | 71 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1121 |  | 1600 | -479 | 70 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [AL-GR] 400 kV Zemplak-Kardia | XZE_KA11_GKARDI15_1:line | 1120 |  | 1600 | -480 | 70 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1120 |  | 1600 | -480 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2556
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1598 | 1600 | 1600 | -2 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1493 | 1600 | 1600 | -107 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1392 | 1600 | 1600 | -208 | 87 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1374 | 1600 | 1600 | -226 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 | 1600 | 1600 | -380 | 76 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1209 | 1600 | 1600 | -391 | 76 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1198 | 1600 | 1600 | -402 | 75 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1185 | 1600 | 1600 | -415 | 74 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1170 | 1600 | 1600 | -430 | 73 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1170 | 1600 | 1600 | -430 | 73 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1168 | 1600 | 1600 | -432 | 73 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1165 | 1600 | 1600 | -435 | 73 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1164 | 1600 | 1600 | -436 | 73 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1161 | 1600 | 1600 | -439 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1159 | 1600 | 1600 | -441 | 72 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1149 | 1600 | 1600 | -451 | 72 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1148 | 1600 | 1600 | -452 | 72 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 | 1600 | 1600 | -455 | 72 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1139 | 1600 | 1600 | -461 | 71 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1133 | 1600 | 1600 | -467 | 71 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1128 | 1600 | 1600 | -472 | 70 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1127 | 1600 | 1600 | -473 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2556
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1598 |  | 1600 | -2 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1493 |  | 1600 | -107 | 93 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1392 |  | 1600 | -208 | 87 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1374 |  | 1600 | -226 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1220 |  | 1600 | -380 | 76 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1209 |  | 1600 | -391 | 76 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 76 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1198 |  | 1600 | -402 | 75 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1185 |  | 1600 | -415 | 74 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1170 |  | 1600 | -430 | 73 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1170 |  | 1600 | -430 | 73 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1168 |  | 1600 | -432 | 73 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1165 |  | 1600 | -435 | 73 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1164 |  | 1600 | -436 | 73 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1161 |  | 1600 | -439 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1159 |  | 1600 | -441 | 72 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1149 |  | 1600 | -451 | 72 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1148 |  | 1600 | -452 | 72 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 |  | 1600 | -455 | 72 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1139 |  | 1600 | -461 | 71 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1133 |  | 1600 | -467 | 71 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1128 |  | 1600 | -472 | 70 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1127 |  | 1600 | -473 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2543
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1593 | 1600 | 1600 | -7 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1502 | 1600 | 1600 | -98 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1400 | 1600 | 1600 | -200 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 | 1600 | 1600 | -302 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 | 1600 | 1600 | -304 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1281 | 1600 | 1600 | -319 | 80 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 | 1600 | 1600 | -322 | 80 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1249 | 1600 | 1600 | -351 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1227 | 1600 | 1600 | -373 | 77 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1225 | 1600 | 1600 | -375 | 77 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1202 | 1600 | 1600 | -398 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1188 | 1600 | 1600 | -412 | 74 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1187 | 1600 | 1600 | -413 | 74 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1186 | 1600 | 1600 | -414 | 74 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1186 | 1600 | 1600 | -414 | 74 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1182 | 1600 | 1600 | -418 | 74 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1165 | 1600 | 1600 | -435 | 73 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1165 | 1600 | 1600 | -435 | 73 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1164 | 1600 | 1600 | -436 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1162 | 1600 | 1600 | -438 | 73 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1154 | 1600 | 1600 | -446 | 72 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 | 1600 | 1600 | -455 | 72 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1134 | 1600 | 1600 | -466 | 71 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1121 | 1600 | 1600 | -479 | 70 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1121 | 1600 | 1600 | -479 | 70 | []

## 1830Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2543
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1593 |  | 1600 | -7 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1502 |  | 1600 | -98 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1400 |  | 1600 | -200 | 87 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 |  | 1600 | -302 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 |  | 1600 | -304 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1281 |  | 1600 | -319 | 80 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 |  | 1600 | -322 | 80 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1249 |  | 1600 | -351 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1227 |  | 1600 | -373 | 77 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1225 |  | 1600 | -375 | 77 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1202 |  | 1600 | -398 | 75 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1188 |  | 1600 | -412 | 74 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1187 |  | 1600 | -413 | 74 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1186 |  | 1600 | -414 | 74 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1186 |  | 1600 | -414 | 74 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1182 |  | 1600 | -418 | 74 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1165 |  | 1600 | -435 | 73 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1165 |  | 1600 | -435 | 73 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1164 |  | 1600 | -436 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1162 |  | 1600 | -438 | 73 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1154 |  | 1600 | -446 | 72 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 |  | 1600 | -455 | 72 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1134 |  | 1600 | -466 | 71 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1121 |  | 1600 | -479 | 70 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1121 |  | 1600 | -479 | 70 | []

## 1930Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2789
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1600 | 1600 | 1600 | 0 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1562 | 1600 | 1600 | -38 | 98 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1522 | 1600 | 1600 | -78 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1495 | 1600 | 1600 | -105 | 93 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1471 | 1600 | 1600 | -129 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1446 | 1600 | 1600 | -154 | 90 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1434 | 1600 | 1600 | -166 | 90 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1407 | 1600 | 1600 | -193 | 88 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1404 | 1600 | 1600 | -196 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1373 | 1600 | 1600 | -227 | 86 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1357 | 1600 | 1600 | -243 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1351 | 1600 | 1600 | -249 | 84 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1329 | 1600 | 1600 | -271 | 83 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1327 | 1600 | 1600 | -273 | 83 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 | 1600 | 1600 | -276 | 83 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1323 | 1600 | 1600 | -277 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1323 | 1600 | 1600 | -277 | 83 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1319 | 1600 | 1600 | -281 | 82 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 | 1600 | 1600 | -297 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 | 1600 | 1600 | -298 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 | 1600 | 1600 | -299 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1297 | 1600 | 1600 | -303 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1294 | 1600 | 1600 | -306 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1292 | 1600 | 1600 | -308 | 81 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 | 1600 | 1600 | -317 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1233 | 1600 | 1600 | -367 | 77 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1189 | 1600 | 1600 | -411 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 | 1600 | 1600 | -455 | 72 | []

## 1930Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2789
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1600 |  | 1600 | 0 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1562 |  | 1600 | -38 | 98 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1522 |  | 1600 | -78 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1495 |  | 1600 | -105 | 93 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1471 |  | 1600 | -129 | 92 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1446 |  | 1600 | -154 | 90 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1434 |  | 1600 | -166 | 90 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1407 |  | 1600 | -193 | 88 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1404 |  | 1600 | -196 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1373 |  | 1600 | -227 | 86 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1357 |  | 1600 | -243 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1351 |  | 1600 | -249 | 84 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1329 |  | 1600 | -271 | 83 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1327 |  | 1600 | -273 | 83 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 |  | 1600 | -276 | 83 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1323 |  | 1600 | -277 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1323 |  | 1600 | -277 | 83 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1319 |  | 1600 | -281 | 82 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 |  | 1600 | -297 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 |  | 1600 | -298 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 |  | 1600 | -299 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1297 |  | 1600 | -303 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1294 |  | 1600 | -306 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1292 |  | 1600 | -308 | 81 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 |  | 1600 | -317 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1233 |  | 1600 | -367 | 77 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1189 |  | 1600 | -411 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 |  | 1600 | -455 | 72 | []

## 2030Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2834
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1599 | 1600 | 1600 | -1 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1568 | 1600 | 1600 | -32 | 98 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1533 | 1600 | 1600 | -67 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1523 | 1600 | 1600 | -77 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1502 | 1600 | 1600 | -98 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1452 | 1600 | 1600 | -148 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1435 | 1600 | 1600 | -165 | 90 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1409 | 1600 | 1600 | -191 | 88 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1405 | 1600 | 1600 | -195 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1379 | 1600 | 1600 | -221 | 86 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 | 1600 | 1600 | -242 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1353 | 1600 | 1600 | -247 | 85 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1329 | 1600 | 1600 | -271 | 83 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1329 | 1600 | 1600 | -271 | 83 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1327 | 1600 | 1600 | -273 | 83 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1326 | 1600 | 1600 | -274 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1326 | 1600 | 1600 | -274 | 83 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1322 | 1600 | 1600 | -278 | 83 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1305 | 1600 | 1600 | -295 | 82 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1304 | 1600 | 1600 | -296 | 82 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 | 1600 | 1600 | -297 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1299 | 1600 | 1600 | -301 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1297 | 1600 | 1600 | -303 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1294 | 1600 | 1600 | -306 | 81 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 | 1600 | 1600 | -315 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1233 | 1600 | 1600 | -367 | 77 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1192 | 1600 | 1600 | -408 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1142 | 1600 | 1600 | -458 | 71 | []

## 2030Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2834
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1599 |  | 1600 | -1 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1568 |  | 1600 | -32 | 98 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1533 |  | 1600 | -67 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1523 |  | 1600 | -77 | 95 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1502 |  | 1600 | -98 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1452 |  | 1600 | -148 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1435 |  | 1600 | -165 | 90 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1409 |  | 1600 | -191 | 88 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1405 |  | 1600 | -195 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1379 |  | 1600 | -221 | 86 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 |  | 1600 | -242 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1353 |  | 1600 | -247 | 85 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1329 |  | 1600 | -271 | 83 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1329 |  | 1600 | -271 | 83 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1327 |  | 1600 | -273 | 83 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1326 |  | 1600 | -274 | 83 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1326 |  | 1600 | -274 | 83 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1322 |  | 1600 | -278 | 83 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1305 |  | 1600 | -295 | 82 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1304 |  | 1600 | -296 | 82 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 |  | 1600 | -297 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1299 |  | 1600 | -301 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1297 |  | 1600 | -303 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1294 |  | 1600 | -306 | 81 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1285 |  | 1600 | -315 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1233 |  | 1600 | -367 | 77 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1192 |  | 1600 | -408 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1142 |  | 1600 | -458 | 71 | []

## 2130Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2841
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1598 | 1600 | 1600 | -2 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1535 | 1600 | 1600 | -65 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1520 | 1600 | 1600 | -80 | 95 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1499 | 1600 | 1600 | -101 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1460 | 1600 | 1600 | -140 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1413 | 1600 | 1600 | -187 | 88 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1391 | 1600 | 1600 | -209 | 87 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1384 | 1600 | 1600 | -216 | 86 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1364 | 1600 | 1600 | -236 | 85 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 | 1600 | 1600 | -255 | 84 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1339 | 1600 | 1600 | -261 | 84 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1319 | 1600 | 1600 | -281 | 82 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 | 1600 | 1600 | -302 | 81 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 | 1600 | 1600 | -305 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 | 1600 | 1600 | -307 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1292 | 1600 | 1600 | -308 | 81 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1292 | 1600 | 1600 | -308 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1288 | 1600 | 1600 | -312 | 80 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 | 1600 | 1600 | -328 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1270 | 1600 | 1600 | -330 | 79 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1270 | 1600 | 1600 | -330 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 | 1600 | 1600 | -332 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 | 1600 | 1600 | -360 | 78 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1209 | 1600 | 1600 | -391 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1200 | 1600 | 1600 | -400 | 75 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1152 | 1600 | 1600 | -448 | 72 | []

## 2130Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2841
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1598 |  | 1600 | -2 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1535 |  | 1600 | -65 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1520 |  | 1600 | -80 | 95 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1499 |  | 1600 | -101 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1460 |  | 1600 | -140 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1413 |  | 1600 | -187 | 88 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1391 |  | 1600 | -209 | 87 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1384 |  | 1600 | -216 | 86 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1364 |  | 1600 | -236 | 85 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 |  | 1600 | -255 | 84 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1339 |  | 1600 | -261 | 84 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1319 |  | 1600 | -281 | 82 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 |  | 1600 | -302 | 81 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 |  | 1600 | -305 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 |  | 1600 | -307 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1292 |  | 1600 | -308 | 81 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1292 |  | 1600 | -308 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1288 |  | 1600 | -312 | 80 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 |  | 1600 | -328 | 79 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1270 |  | 1600 | -330 | 79 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1270 |  | 1600 | -330 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 |  | 1600 | -332 | 79 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 |  | 1600 | -360 | 78 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1209 |  | 1600 | -391 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1200 |  | 1600 | -400 | 75 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1152 |  | 1600 | -448 | 72 | []

## 2230Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2722
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1596 | 1600 | 1600 | -4 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1526 | 1600 | 1600 | -74 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1498 | 1600 | 1600 | -102 | 94 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1464 | 1600 | 1600 | -136 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1405 | 1600 | 1600 | -195 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1359 | 1600 | 1600 | -241 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1359 | 1600 | 1600 | -241 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1349 | 1600 | 1600 | -251 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 | 1600 | 1600 | -276 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1316 | 1600 | 1600 | -284 | 82 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 | 1600 | 1600 | -297 | 81 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1279 | 1600 | 1600 | -321 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1270 | 1600 | 1600 | -330 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1257 | 1600 | 1600 | -343 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1256 | 1600 | 1600 | -344 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1234 | 1600 | 1600 | -366 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1225 | 1600 | 1600 | -375 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1157 | 1600 | 1600 | -443 | 72 | []

## 2230Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2722
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1596 |  | 1600 | -4 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1526 |  | 1600 | -74 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1498 |  | 1600 | -102 | 94 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1464 |  | 1600 | -136 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1405 |  | 1600 | -195 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1359 |  | 1600 | -241 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1359 |  | 1600 | -241 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1349 |  | 1600 | -251 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 |  | 1600 | -276 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1316 |  | 1600 | -284 | 82 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 |  | 1600 | -297 | 81 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1279 |  | 1600 | -321 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1270 |  | 1600 | -330 | 79 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1257 |  | 1600 | -343 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1256 |  | 1600 | -344 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1234 |  | 1600 | -366 | 77 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1225 |  | 1600 | -375 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 |  | 1600 | -385 | 76 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1157 |  | 1600 | -443 | 72 | []

## 2330Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2697
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1592 | 1600 | 1600 | -8 | 99 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1532 | 1600 | 1600 | -68 | 96 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1502 | 1600 | 1600 | -98 | 94 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1474 | 1600 | 1600 | -126 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1412 | 1600 | 1600 | -188 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1371 | 1600 | 1600 | -229 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1368 | 1600 | 1600 | -232 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1361 | 1600 | 1600 | -239 | 85 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1340 | 1600 | 1600 | -260 | 84 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1326 | 1600 | 1600 | -274 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 | 1600 | 1600 | -290 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1289 | 1600 | 1600 | -311 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 | 1600 | 1600 | -332 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1265 | 1600 | 1600 | -335 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 | 1600 | 1600 | -370 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1166 | 1600 | 1600 | -434 | 73 | []

## 2330Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2697
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1592 |  | 1600 | -8 | 99 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1532 |  | 1600 | -68 | 96 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1502 |  | 1600 | -98 | 94 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1474 |  | 1600 | -126 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1412 |  | 1600 | -188 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1371 |  | 1600 | -229 | 86 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1368 |  | 1600 | -232 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1361 |  | 1600 | -239 | 85 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1340 |  | 1600 | -260 | 84 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1326 |  | 1600 | -274 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1310 |  | 1600 | -290 | 82 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1289 |  | 1600 | -311 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1277 |  | 1600 | -323 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1268 |  | 1600 | -332 | 79 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 |  | 1600 | -334 | 79 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1265 |  | 1600 | -335 | 79 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1230 |  | 1600 | -370 | 77 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1166 |  | 1600 | -434 | 73 | []