## 1230Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2633
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1592 | 1600 | 1600 | -8 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1525 | 1600 | 1600 | -75 | 95 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1511 | 1600 | 1600 | -89 | 94 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1500 | 1600 | 1600 | -100 | 94 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1466 | 1600 | 1600 | -134 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1452 | 1600 | 1600 | -148 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1450 | 1600 | 1600 | -150 | 91 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1396 | 1600 | 1600 | -204 | 87 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1376 | 1600 | 1600 | -224 | 86 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1375 | 1600 | 1600 | -225 | 86 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1371 | 1600 | 1600 | -229 | 86 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 | 1600 | 1600 | -242 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1350 | 1600 | 1600 | -250 | 84 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 | 1600 | 1600 | -256 | 84 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 | 1600 | 1600 | -256 | 84 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1341 | 1600 | 1600 | -259 | 84 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1341 | 1600 | 1600 | -259 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1341 | 1600 | 1600 | -259 | 84 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1337 | 1600 | 1600 | -263 | 84 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1334 | 1600 | 1600 | -266 | 83 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1328 | 1600 | 1600 | -272 | 83 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1322 | 1600 | 1600 | -278 | 83 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1321 | 1600 | 1600 | -279 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1313 | 1600 | 1600 | -287 | 82 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1304 | 1600 | 1600 | -296 | 82 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1299 | 1600 | 1600 | -301 | 81 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1299 | 1600 | 1600 | -301 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 | 1600 | 1600 | -302 | 81 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 | 1600 | 1600 | -304 | 81 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 | 1600 | 1600 | -316 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1275 | 1600 | 1600 | -325 | 80 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1250 | 1600 | 1600 | -350 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1151 | 1600 | 1600 | -449 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1151 | 1600 | 1600 | -449 | 72 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1147 | 1600 | 1600 | -453 | 72 | []

## 1230Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2633
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1592 |  | 1600 | -8 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1525 |  | 1600 | -75 | 95 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1511 |  | 1600 | -89 | 94 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1500 |  | 1600 | -100 | 94 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1466 |  | 1600 | -134 | 92 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1452 |  | 1600 | -148 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1450 |  | 1600 | -150 | 91 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1396 |  | 1600 | -204 | 87 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1376 |  | 1600 | -224 | 86 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1375 |  | 1600 | -225 | 86 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1371 |  | 1600 | -229 | 86 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 |  | 1600 | -242 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1350 |  | 1600 | -250 | 84 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 |  | 1600 | -256 | 84 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 |  | 1600 | -256 | 84 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1341 |  | 1600 | -259 | 84 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1341 |  | 1600 | -259 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1341 |  | 1600 | -259 | 84 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1337 |  | 1600 | -263 | 84 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1334 |  | 1600 | -266 | 83 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1328 |  | 1600 | -272 | 83 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1322 |  | 1600 | -278 | 83 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1321 |  | 1600 | -279 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1313 |  | 1600 | -287 | 82 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1304 |  | 1600 | -296 | 82 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1299 |  | 1600 | -301 | 81 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1299 |  | 1600 | -301 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 |  | 1600 | -302 | 81 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 |  | 1600 | -304 | 81 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1284 |  | 1600 | -316 | 80 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1275 |  | 1600 | -325 | 80 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1250 |  | 1600 | -350 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1236 |  | 1600 | -364 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1151 |  | 1600 | -449 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1151 |  | 1600 | -449 | 72 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1147 |  | 1600 | -453 | 72 | []

## 1330Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2681
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1598 | 1600 | 1600 | -2 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1533 | 1600 | 1600 | -67 | 96 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1515 | 1600 | 1600 | -85 | 95 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1476 | 1600 | 1600 | -124 | 92 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1459 | 1600 | 1600 | -141 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1454 | 1600 | 1600 | -146 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1453 | 1600 | 1600 | -147 | 91 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1398 | 1600 | 1600 | -202 | 87 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1376 | 1600 | 1600 | -224 | 86 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1373 | 1600 | 1600 | -227 | 86 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 | 1600 | 1600 | -233 | 85 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1356 | 1600 | 1600 | -244 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1350 | 1600 | 1600 | -250 | 84 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1348 | 1600 | 1600 | -252 | 84 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1346 | 1600 | 1600 | -254 | 84 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 | 1600 | 1600 | -255 | 84 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 | 1600 | 1600 | -256 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1342 | 1600 | 1600 | -258 | 84 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1341 | 1600 | 1600 | -259 | 84 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1332 | 1600 | 1600 | -268 | 83 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1327 | 1600 | 1600 | -273 | 83 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1327 | 1600 | 1600 | -273 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1315 | 1600 | 1600 | -285 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1315 | 1600 | 1600 | -285 | 82 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1313 | 1600 | 1600 | -287 | 82 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1310 | 1600 | 1600 | -290 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1308 | 1600 | 1600 | -292 | 82 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 | 1600 | 1600 | -299 | 81 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1301 | 1600 | 1600 | -299 | 81 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1300 | 1600 | 1600 | -300 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1282 | 1600 | 1600 | -318 | 80 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 | 1600 | 1600 | -322 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1152 | 1600 | 1600 | -448 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1147 | 1600 | 1600 | -453 | 72 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1144 | 1600 | 1600 | -456 | 71 | []

## 1330Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2681
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1598 |  | 1600 | -2 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1533 |  | 1600 | -67 | 96 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1515 |  | 1600 | -85 | 95 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1476 |  | 1600 | -124 | 92 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1459 |  | 1600 | -141 | 91 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1454 |  | 1600 | -146 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1453 |  | 1600 | -147 | 91 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1398 |  | 1600 | -202 | 87 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1376 |  | 1600 | -224 | 86 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1373 |  | 1600 | -227 | 86 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 |  | 1600 | -233 | 85 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1356 |  | 1600 | -244 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1350 |  | 1600 | -250 | 84 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1348 |  | 1600 | -252 | 84 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1346 |  | 1600 | -254 | 84 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 |  | 1600 | -255 | 84 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 |  | 1600 | -256 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1342 |  | 1600 | -258 | 84 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1341 |  | 1600 | -259 | 84 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1332 |  | 1600 | -268 | 83 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1327 |  | 1600 | -273 | 83 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1327 |  | 1600 | -273 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1315 |  | 1600 | -285 | 82 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1315 |  | 1600 | -285 | 82 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1313 |  | 1600 | -287 | 82 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1310 |  | 1600 | -290 | 82 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1308 |  | 1600 | -292 | 82 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 |  | 1600 | -299 | 81 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1301 |  | 1600 | -299 | 81 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1300 |  | 1600 | -300 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1282 |  | 1600 | -318 | 80 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 |  | 1600 | -322 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1258 |  | 1600 | -342 | 79 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1234 |  | 1600 | -366 | 77 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1152 |  | 1600 | -448 | 72 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1147 |  | 1600 | -453 | 72 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1144 |  | 1600 | -456 | 71 | []

## 1430Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2731
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1600 | 1600 | 1600 | 0 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1540 | 1600 | 1600 | -60 | 96 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1530 | 1600 | 1600 | -70 | 96 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1468 | 1600 | 1600 | -132 | 92 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1466 | 1600 | 1600 | -134 | 92 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1462 | 1600 | 1600 | -138 | 91 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1406 | 1600 | 1600 | -194 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1402 | 1600 | 1600 | -198 | 88 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1391 | 1600 | 1600 | -209 | 87 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1370 | 1600 | 1600 | -230 | 86 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 | 1600 | 1600 | -233 | 85 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 | 1600 | 1600 | -242 | 85 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1356 | 1600 | 1600 | -244 | 85 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1353 | 1600 | 1600 | -247 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1353 | 1600 | 1600 | -247 | 85 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1351 | 1600 | 1600 | -249 | 84 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1350 | 1600 | 1600 | -250 | 84 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1349 | 1600 | 1600 | -251 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1346 | 1600 | 1600 | -254 | 84 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1342 | 1600 | 1600 | -258 | 84 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1335 | 1600 | 1600 | -265 | 83 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1335 | 1600 | 1600 | -265 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1323 | 1600 | 1600 | -277 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1322 | 1600 | 1600 | -278 | 83 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1311 | 1600 | 1600 | -289 | 82 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1305 | 1600 | 1600 | -295 | 82 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 | 1600 | 1600 | -299 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 | 1600 | 1600 | -304 | 81 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1275 | 1600 | 1600 | -325 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1274 | 1600 | 1600 | -326 | 80 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1270 | 1600 | 1600 | -330 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1163 | 1600 | 1600 | -437 | 73 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1158 | 1600 | 1600 | -442 | 72 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1126 | 1600 | 1600 | -474 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2731
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1600 |  | 1600 | 0 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1540 |  | 1600 | -60 | 96 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1530 |  | 1600 | -70 | 96 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1468 |  | 1600 | -132 | 92 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1466 |  | 1600 | -134 | 92 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1462 |  | 1600 | -138 | 91 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1406 |  | 1600 | -194 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1402 |  | 1600 | -198 | 88 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1391 |  | 1600 | -209 | 87 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1370 |  | 1600 | -230 | 86 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 |  | 1600 | -233 | 85 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 |  | 1600 | -242 | 85 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1356 |  | 1600 | -244 | 85 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1353 |  | 1600 | -247 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1353 |  | 1600 | -247 | 85 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1351 |  | 1600 | -249 | 84 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1350 |  | 1600 | -250 | 84 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1349 |  | 1600 | -251 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1346 |  | 1600 | -254 | 84 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1342 |  | 1600 | -258 | 84 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1335 |  | 1600 | -265 | 83 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1335 |  | 1600 | -265 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1323 |  | 1600 | -277 | 83 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1322 |  | 1600 | -278 | 83 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1311 |  | 1600 | -289 | 82 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1305 |  | 1600 | -295 | 82 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 |  | 1600 | -299 | 81 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 |  | 1600 | -304 | 81 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1275 |  | 1600 | -325 | 80 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1274 |  | 1600 | -326 | 80 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1270 |  | 1600 | -330 | 79 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1269 |  | 1600 | -331 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1251 |  | 1600 | -349 | 78 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1209 |  | 1600 | -391 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1163 |  | 1600 | -437 | 73 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1158 |  | 1600 | -442 | 72 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1126 |  | 1600 | -474 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2793
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1597 | 1600 | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1563 | 1600 | 1600 | -37 | 98 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1537 | 1600 | 1600 | -63 | 96 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1472 | 1600 | 1600 | -128 | 92 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1462 | 1600 | 1600 | -138 | 91 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1450 | 1600 | 1600 | -150 | 91 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1420 | 1600 | 1600 | -180 | 89 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1405 | 1600 | 1600 | -195 | 88 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1405 | 1600 | 1600 | -195 | 88 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 | 1600 | 1600 | -233 | 85 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1365 | 1600 | 1600 | -235 | 85 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1365 | 1600 | 1600 | -235 | 85 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1364 | 1600 | 1600 | -236 | 85 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1364 | 1600 | 1600 | -236 | 85 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1363 | 1600 | 1600 | -237 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1360 | 1600 | 1600 | -240 | 85 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 | 1600 | 1600 | -242 | 85 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 | 1600 | 1600 | -242 | 85 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1357 | 1600 | 1600 | -243 | 85 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1354 | 1600 | 1600 | -246 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1348 | 1600 | 1600 | -252 | 84 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1347 | 1600 | 1600 | -253 | 84 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1346 | 1600 | 1600 | -254 | 84 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1335 | 1600 | 1600 | -265 | 83 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1319 | 1600 | 1600 | -281 | 82 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1318 | 1600 | 1600 | -282 | 82 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1298 | 1600 | 1600 | -302 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 | 1600 | 1600 | -305 | 81 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1181 | 1600 | 1600 | -419 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1179 | 1600 | 1600 | -421 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1153 | 1600 | 1600 | -447 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1151 | 1600 | 1600 | -449 | 72 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1136 | 1600 | 1600 | -464 | 71 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1135 | 1600 | 1600 | -465 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2793
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1597 |  | 1600 | -3 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1563 |  | 1600 | -37 | 98 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1537 |  | 1600 | -63 | 96 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1472 |  | 1600 | -128 | 92 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1462 |  | 1600 | -138 | 91 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1450 |  | 1600 | -150 | 91 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1420 |  | 1600 | -180 | 89 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1405 |  | 1600 | -195 | 88 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1405 |  | 1600 | -195 | 88 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 |  | 1600 | -233 | 85 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1365 |  | 1600 | -235 | 85 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1365 |  | 1600 | -235 | 85 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1364 |  | 1600 | -236 | 85 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1364 |  | 1600 | -236 | 85 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1363 |  | 1600 | -237 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1360 |  | 1600 | -240 | 85 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 |  | 1600 | -242 | 85 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 |  | 1600 | -242 | 85 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1357 |  | 1600 | -243 | 85 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1354 |  | 1600 | -246 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1348 |  | 1600 | -252 | 84 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1347 |  | 1600 | -253 | 84 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1346 |  | 1600 | -254 | 84 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1335 |  | 1600 | -265 | 83 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1319 |  | 1600 | -281 | 82 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1318 |  | 1600 | -282 | 82 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1298 |  | 1600 | -302 | 81 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 |  | 1600 | -305 | 81 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1239 |  | 1600 | -361 | 77 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1209 |  | 1600 | -391 | 76 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1209 |  | 1600 | -391 | 76 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1193 |  | 1600 | -407 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1181 |  | 1600 | -419 | 74 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1179 |  | 1600 | -421 | 74 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1153 |  | 1600 | -447 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1151 |  | 1600 | -449 | 72 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1136 |  | 1600 | -464 | 71 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1135 |  | 1600 | -465 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2884
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1594 | 1600 | 1600 | -6 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1580 | 1600 | 1600 | -20 | 99 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1534 | 1600 | 1600 | -66 | 96 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1523 | 1600 | 1600 | -77 | 95 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1465 | 1600 | 1600 | -135 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1458 | 1600 | 1600 | -142 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1455 | 1600 | 1600 | -145 | 91 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1428 | 1600 | 1600 | -172 | 89 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1409 | 1600 | 1600 | -191 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1407 | 1600 | 1600 | -193 | 88 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1370 | 1600 | 1600 | -230 | 86 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 | 1600 | 1600 | -233 | 85 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 | 1600 | 1600 | -233 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1366 | 1600 | 1600 | -234 | 85 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1364 | 1600 | 1600 | -236 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1363 | 1600 | 1600 | -237 | 85 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1362 | 1600 | 1600 | -238 | 85 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1362 | 1600 | 1600 | -238 | 85 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1361 | 1600 | 1600 | -239 | 85 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 | 1600 | 1600 | -242 | 85 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1355 | 1600 | 1600 | -245 | 85 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1354 | 1600 | 1600 | -246 | 85 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1353 | 1600 | 1600 | -247 | 85 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1347 | 1600 | 1600 | -253 | 84 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1336 | 1600 | 1600 | -264 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 | 1600 | 1600 | -276 | 83 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1305 | 1600 | 1600 | -295 | 82 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1176 | 1600 | 1600 | -424 | 73 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1140 | 1600 | 1600 | -460 | 71 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1130 | 1600 | 1600 | -470 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2884
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1594 |  | 1600 | -6 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1580 |  | 1600 | -20 | 99 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1534 |  | 1600 | -66 | 96 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1523 |  | 1600 | -77 | 95 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1465 |  | 1600 | -135 | 92 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1458 |  | 1600 | -142 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1455 |  | 1600 | -145 | 91 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1428 |  | 1600 | -172 | 89 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1409 |  | 1600 | -191 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1407 |  | 1600 | -193 | 88 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1370 |  | 1600 | -230 | 86 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 |  | 1600 | -233 | 85 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1367 |  | 1600 | -233 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1366 |  | 1600 | -234 | 85 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1364 |  | 1600 | -236 | 85 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1363 |  | 1600 | -237 | 85 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1362 |  | 1600 | -238 | 85 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1362 |  | 1600 | -238 | 85 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1361 |  | 1600 | -239 | 85 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 |  | 1600 | -242 | 85 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1355 |  | 1600 | -245 | 85 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1354 |  | 1600 | -246 | 85 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1353 |  | 1600 | -247 | 85 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1347 |  | 1600 | -253 | 84 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1336 |  | 1600 | -264 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1324 |  | 1600 | -276 | 83 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1305 |  | 1600 | -295 | 82 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1215 |  | 1600 | -385 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1176 |  | 1600 | -424 | 73 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1175 |  | 1600 | -425 | 73 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1165 |  | 1600 | -435 | 73 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1164 |  | 1600 | -436 | 73 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1140 |  | 1600 | -460 | 71 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1130 |  | 1600 | -470 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2869
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1593 | 1600 | 1600 | -7 | 100 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1584 | 1600 | 1600 | -16 | 99 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1560 | 1600 | 1600 | -40 | 98 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1523 | 1600 | 1600 | -77 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1498 | 1600 | 1600 | -102 | 94 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1454 | 1600 | 1600 | -146 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1443 | 1600 | 1600 | -157 | 90 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1409 | 1600 | 1600 | -191 | 88 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1406 | 1600 | 1600 | -194 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1403 | 1600 | 1600 | -197 | 88 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1378 | 1600 | 1600 | -222 | 86 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1370 | 1600 | 1600 | -230 | 86 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1366 | 1600 | 1600 | -234 | 85 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1364 | 1600 | 1600 | -236 | 85 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1362 | 1600 | 1600 | -238 | 85 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1362 | 1600 | 1600 | -238 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1361 | 1600 | 1600 | -239 | 85 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1361 | 1600 | 1600 | -239 | 85 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 | 1600 | 1600 | -242 | 85 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 | 1600 | 1600 | -242 | 85 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1357 | 1600 | 1600 | -243 | 85 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1349 | 1600 | 1600 | -251 | 84 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1347 | 1600 | 1600 | -253 | 84 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 | 1600 | 1600 | -255 | 84 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 | 1600 | 1600 | -256 | 84 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1336 | 1600 | 1600 | -264 | 83 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1316 | 1600 | 1600 | -284 | 82 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1206 | 1600 | 1600 | -394 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1141 | 1600 | 1600 | -459 | 71 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1139 | 1600 | 1600 | -461 | 71 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1123 | 1600 | 1600 | -477 | 70 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1123 | 1600 | 1600 | -477 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2869
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1593 |  | 1600 | -7 | 100 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1584 |  | 1600 | -16 | 99 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1560 |  | 1600 | -40 | 98 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1523 |  | 1600 | -77 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1498 |  | 1600 | -102 | 94 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1454 |  | 1600 | -146 | 91 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1443 |  | 1600 | -157 | 90 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1409 |  | 1600 | -191 | 88 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1406 |  | 1600 | -194 | 88 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1403 |  | 1600 | -197 | 88 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1378 |  | 1600 | -222 | 86 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1370 |  | 1600 | -230 | 86 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1366 |  | 1600 | -234 | 85 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1364 |  | 1600 | -236 | 85 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1362 |  | 1600 | -238 | 85 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1362 |  | 1600 | -238 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1361 |  | 1600 | -239 | 85 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1361 |  | 1600 | -239 | 85 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 |  | 1600 | -242 | 85 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 |  | 1600 | -242 | 85 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1357 |  | 1600 | -243 | 85 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1349 |  | 1600 | -251 | 84 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1347 |  | 1600 | -253 | 84 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 |  | 1600 | -255 | 84 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 |  | 1600 | -256 | 84 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1336 |  | 1600 | -264 | 83 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1316 |  | 1600 | -284 | 82 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1206 |  | 1600 | -394 | 75 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1141 |  | 1600 | -459 | 71 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1139 |  | 1600 | -461 | 71 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1123 |  | 1600 | -477 | 70 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [BG-GR] 400 kV Blagoevgrad - Thessaloniki | XBG_TH11_GTHESS13_1:line | 1123 |  | 1600 | -477 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2832
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 | 1600 | 1600 | -5 | 100 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1578 | 1600 | 1600 | -22 | 99 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1564 | 1600 | 1600 | -36 | 98 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1562 | 1600 | 1600 | -38 | 98 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1496 | 1600 | 1600 | -104 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1483 | 1600 | 1600 | -117 | 93 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1433 | 1600 | 1600 | -167 | 90 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1410 | 1600 | 1600 | -190 | 88 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1397 | 1600 | 1600 | -203 | 87 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1384 | 1600 | 1600 | -216 | 87 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1380 | 1600 | 1600 | -220 | 86 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1360 | 1600 | 1600 | -240 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1355 | 1600 | 1600 | -245 | 85 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1350 | 1600 | 1600 | -250 | 84 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1350 | 1600 | 1600 | -250 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1349 | 1600 | 1600 | -251 | 84 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1349 | 1600 | 1600 | -251 | 84 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 | 1600 | 1600 | -255 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 | 1600 | 1600 | -255 | 84 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 | 1600 | 1600 | -255 | 84 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 | 1600 | 1600 | -256 | 84 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 | 1600 | 1600 | -256 | 84 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1343 | 1600 | 1600 | -257 | 84 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1343 | 1600 | 1600 | -257 | 84 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1343 | 1600 | 1600 | -257 | 84 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1330 | 1600 | 1600 | -270 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1307 | 1600 | 1600 | -293 | 82 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 | 1600 | 1600 | -317 | 80 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1184 | 1600 | 1600 | -416 | 74 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS15_1:line | 1143 | 1600 | 1600 | -457 | 71 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS15_1:line | 1142 | 1600 | 1600 | -458 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2832
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 |  | 1600 | -5 | 100 | []
IT_GR_CO_00001 | N-1 400 kV Galatina-Arachthos | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1578 |  | 1600 | -22 | 99 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1564 |  | 1600 | -36 | 98 | []
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1562 |  | 1600 | -38 | 98 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1496 |  | 1600 | -104 | 94 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1483 |  | 1600 | -117 | 93 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1433 |  | 1600 | -167 | 90 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1410 |  | 1600 | -190 | 88 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1397 |  | 1600 | -203 | 87 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1384 |  | 1600 | -216 | 87 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1380 |  | 1600 | -220 | 86 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1360 |  | 1600 | -240 | 85 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1355 |  | 1600 | -245 | 85 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1350 |  | 1600 | -250 | 84 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1350 |  | 1600 | -250 | 84 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1349 |  | 1600 | -251 | 84 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1349 |  | 1600 | -251 | 84 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 |  | 1600 | -255 | 84 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 |  | 1600 | -255 | 84 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1345 |  | 1600 | -255 | 84 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 |  | 1600 | -256 | 84 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1344 |  | 1600 | -256 | 84 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1343 |  | 1600 | -257 | 84 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1343 |  | 1600 | -257 | 84 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1343 |  | 1600 | -257 | 84 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1330 |  | 1600 | -270 | 83 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1307 |  | 1600 | -293 | 82 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 |  | 1600 | -317 | 80 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 |  | 1600 | -385 | 76 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1184 |  | 1600 | -416 | 74 | []
MK_GR_CO_00001 | N-1 400 kV Bitola-Meliti | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS15_1:line | 1143 |  | 1600 | -457 | 71 | []
GR_CO_00003 | N-1 400 kV Meliti-Amideo ck.2 | [MK-GR] 400 kV Dubrovo-Thessaloniki | XTH_DU11_GTHESS15_1:line | 1142 |  | 1600 | -458 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2690
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 | 1600 | 1600 | -5 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1509 | 1600 | 1600 | -91 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1471 | 1600 | 1600 | -129 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1412 | 1600 | 1600 | -188 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1359 | 1600 | 1600 | -241 | 85 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1299 | 1600 | 1600 | -301 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1282 | 1600 | 1600 | -318 | 80 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1276 | 1600 | 1600 | -324 | 80 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1271 | 1600 | 1600 | -329 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1249 | 1600 | 1600 | -351 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1246 | 1600 | 1600 | -354 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 | 1600 | 1600 | -360 | 78 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1238 | 1600 | 1600 | -362 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1202 | 1600 | 1600 | -398 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1155 | 1600 | 1600 | -445 | 72 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1153 | 1600 | 1600 | -447 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1142 | 1600 | 1600 | -458 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2690
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 |  | 1600 | -5 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1509 |  | 1600 | -91 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1471 |  | 1600 | -129 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1412 |  | 1600 | -188 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1359 |  | 1600 | -241 | 85 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1299 |  | 1600 | -301 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1282 |  | 1600 | -318 | 80 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1277 |  | 1600 | -323 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1276 |  | 1600 | -324 | 80 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1271 |  | 1600 | -329 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1249 |  | 1600 | -351 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1246 |  | 1600 | -354 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 |  | 1600 | -360 | 78 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1238 |  | 1600 | -362 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1215 |  | 1600 | -385 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1202 |  | 1600 | -398 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1155 |  | 1600 | -445 | 72 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1153 |  | 1600 | -447 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1142 |  | 1600 | -458 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2655
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1597 | 1600 | 1600 | -3 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1507 | 1600 | 1600 | -93 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1467 | 1600 | 1600 | -133 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1406 | 1600 | 1600 | -194 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1351 | 1600 | 1600 | -249 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1294 | 1600 | 1600 | -306 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1280 | 1600 | 1600 | -320 | 80 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1274 | 1600 | 1600 | -326 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1273 | 1600 | 1600 | -327 | 80 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1247 | 1600 | 1600 | -353 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1246 | 1600 | 1600 | -354 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 | 1600 | 1600 | -360 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1235 | 1600 | 1600 | -365 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1212 | 1600 | 1600 | -388 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1157 | 1600 | 1600 | -443 | 72 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1153 | 1600 | 1600 | -447 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 | 1600 | 1600 | -455 | 72 | []

## 2030Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2655
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1597 |  | 1600 | -3 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1507 |  | 1600 | -93 | 94 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1467 |  | 1600 | -133 | 92 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1406 |  | 1600 | -194 | 88 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1351 |  | 1600 | -249 | 84 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1294 |  | 1600 | -306 | 81 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1280 |  | 1600 | -320 | 80 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1274 |  | 1600 | -326 | 80 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1273 |  | 1600 | -327 | 80 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 |  | 1600 | -334 | 79 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1247 |  | 1600 | -353 | 78 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1246 |  | 1600 | -354 | 78 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1240 |  | 1600 | -360 | 78 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1235 |  | 1600 | -365 | 77 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1212 |  | 1600 | -388 | 76 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1157 |  | 1600 | -443 | 72 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1153 |  | 1600 | -447 | 72 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1145 |  | 1600 | -455 | 72 | []

## 2130Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2665
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 | 1600 | 1600 | -5 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1513 | 1600 | 1600 | -87 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1506 | 1600 | 1600 | -94 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1449 | 1600 | 1600 | -151 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1386 | 1600 | 1600 | -214 | 87 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1332 | 1600 | 1600 | -268 | 83 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1321 | 1600 | 1600 | -279 | 83 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1307 | 1600 | 1600 | -293 | 82 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 | 1600 | 1600 | -299 | 81 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 | 1600 | 1600 | -300 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 | 1600 | 1600 | -305 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1280 | 1600 | 1600 | -320 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 | 1600 | 1600 | -322 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1276 | 1600 | 1600 | -324 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1276 | 1600 | 1600 | -324 | 80 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1276 | 1600 | 1600 | -324 | 80 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1275 | 1600 | 1600 | -325 | 80 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1275 | 1600 | 1600 | -325 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1274 | 1600 | 1600 | -326 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1273 | 1600 | 1600 | -327 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1271 | 1600 | 1600 | -329 | 79 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1269 | 1600 | 1600 | -331 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1249 | 1600 | 1600 | -351 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1179 | 1600 | 1600 | -421 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1172 | 1600 | 1600 | -428 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1171 | 1600 | 1600 | -429 | 73 | []

## 2130Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2665
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 |  | 1600 | -5 | 100 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1513 |  | 1600 | -87 | 95 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1506 |  | 1600 | -94 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1449 |  | 1600 | -151 | 91 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1386 |  | 1600 | -214 | 87 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1332 |  | 1600 | -268 | 83 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1321 |  | 1600 | -279 | 83 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1307 |  | 1600 | -293 | 82 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1301 |  | 1600 | -299 | 81 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 |  | 1600 | -300 | 81 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 |  | 1600 | -305 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1280 |  | 1600 | -320 | 80 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1278 |  | 1600 | -322 | 80 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1277 |  | 1600 | -323 | 80 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1276 |  | 1600 | -324 | 80 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1276 |  | 1600 | -324 | 80 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1276 |  | 1600 | -324 | 80 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1275 |  | 1600 | -325 | 80 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1275 |  | 1600 | -325 | 80 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1274 |  | 1600 | -326 | 80 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1273 |  | 1600 | -327 | 80 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1271 |  | 1600 | -329 | 79 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1269 |  | 1600 | -331 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1249 |  | 1600 | -351 | 78 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1179 |  | 1600 | -421 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1172 |  | 1600 | -428 | 73 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1171 |  | 1600 | -429 | 73 | []

## 2230Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2747
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1592 | 1600 | 1600 | -8 | 99 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1531 | 1600 | 1600 | -69 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1498 | 1600 | 1600 | -102 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1487 | 1600 | 1600 | -113 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1430 | 1600 | 1600 | -170 | 89 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1369 | 1600 | 1600 | -231 | 86 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 | 1600 | 1600 | -242 | 85 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1343 | 1600 | 1600 | -257 | 84 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1338 | 1600 | 1600 | -262 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1333 | 1600 | 1600 | -267 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1312 | 1600 | 1600 | -288 | 82 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1307 | 1600 | 1600 | -293 | 82 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1306 | 1600 | 1600 | -294 | 82 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1304 | 1600 | 1600 | -296 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 | 1600 | 1600 | -297 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 | 1600 | 1600 | -298 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 | 1600 | 1600 | -300 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 | 1600 | 1600 | -300 | 81 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1299 | 1600 | 1600 | -301 | 81 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1299 | 1600 | 1600 | -301 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 | 1600 | 1600 | -302 | 81 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1297 | 1600 | 1600 | -303 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1297 | 1600 | 1600 | -303 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 | 1600 | 1600 | -317 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 | 1600 | 1600 | -328 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1269 | 1600 | 1600 | -331 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1191 | 1600 | 1600 | -409 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1185 | 1600 | 1600 | -415 | 74 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1179 | 1600 | 1600 | -421 | 74 | []

## 2230Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2747
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1592 |  | 1600 | -8 | 99 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1531 |  | 1600 | -69 | 96 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1498 |  | 1600 | -102 | 94 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1487 |  | 1600 | -113 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1430 |  | 1600 | -170 | 89 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1369 |  | 1600 | -231 | 86 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1358 |  | 1600 | -242 | 85 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1343 |  | 1600 | -257 | 84 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1338 |  | 1600 | -262 | 84 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1333 |  | 1600 | -267 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1312 |  | 1600 | -288 | 82 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1307 |  | 1600 | -293 | 82 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1306 |  | 1600 | -294 | 82 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1304 |  | 1600 | -296 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 |  | 1600 | -297 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 |  | 1600 | -298 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 |  | 1600 | -300 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 |  | 1600 | -300 | 81 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1299 |  | 1600 | -301 | 81 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1299 |  | 1600 | -301 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 |  | 1600 | -302 | 81 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1297 |  | 1600 | -303 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1297 |  | 1600 | -303 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1283 |  | 1600 | -317 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1272 |  | 1600 | -328 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1269 |  | 1600 | -331 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 |  | 1600 | -334 | 79 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1191 |  | 1600 | -409 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1185 |  | 1600 | -415 | 74 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1179 |  | 1600 | -421 | 74 | []

## 2330Preventive
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2761
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 | 1600 | 1600 | -5 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1526 | 1600 | 1600 | -74 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1489 | 1600 | 1600 | -111 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1485 | 1600 | 1600 | -115 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1422 | 1600 | 1600 | -178 | 89 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1361 | 1600 | 1600 | -239 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1352 | 1600 | 1600 | -248 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1332 | 1600 | 1600 | -268 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1330 | 1600 | 1600 | -270 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1329 | 1600 | 1600 | -271 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 | 1600 | 1600 | -297 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 | 1600 | 1600 | -298 | 81 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 | 1600 | 1600 | -300 | 81 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 | 1600 | 1600 | -302 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1297 | 1600 | 1600 | -303 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 | 1600 | 1600 | -304 | 81 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 | 1600 | 1600 | -305 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 | 1600 | 1600 | -305 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1294 | 1600 | 1600 | -306 | 81 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1294 | 1600 | 1600 | -306 | 81 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 | 1600 | 1600 | -307 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 | 1600 | 1600 | -307 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1290 | 1600 | 1600 | -310 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1274 | 1600 | 1600 | -326 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1182 | 1600 | 1600 | -418 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1178 | 1600 | 1600 | -422 | 74 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1174 | 1600 | 1600 | -426 | 73 | []

## 2330Curative
Detailed results
Generated at: | 2024-04-22 07:49
Business day: | 22.04.2024
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2761
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
AL_GR_CO_00001 | N-1 400 kV Zemplak-Kardia | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1595 |  | 1600 | -5 | 100 | []
MK_GR_CO_00002 | N-1 400 kV Dubrovo-Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1526 |  | 1600 | -74 | 95 | []
AL_CO_00002 | N-1 400 kV Elbasan 2-Zemlak | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1489 |  | 1600 | -111 | 93 | []
BG_GR_CO_00001 | N-1 400 kV Blagoevgrad - Thessaloniki | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1485 |  | 1600 | -115 | 93 | []
GR_CO_00001 | N-1 400 kV Filippoi-Nea Santa ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1422 |  | 1600 | -178 | 89 | []
GR_CO_00002 | N-1 400 kV Filippoi-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1361 |  | 1600 | -239 | 85 | []
GR_CO_00004 | N-1 400 kV Amideo-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1352 |  | 1600 | -248 | 85 | []
TR_GR_CO_00001 | N-1 400 kV Babaeski-N Santa | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1332 |  | 1600 | -268 | 83 | []
MK_KS_CO_00001 | N-1 400 kV Skopje 5 âUrosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1330 |  | 1600 | -270 | 83 | []
BG_GR_CO_00002 | N-1 400kV MARITSA IZTOK-NEA SANTA-CK-1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1329 |  | 1600 | -271 | 83 | []
AL_CO_00001 | N-1 400 kV Elbasan 2-Tirana 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1303 |  | 1600 | -297 | 81 | []
TR_CO_00001 | N-1 400 kV Habitabat NGCC -Babaeski | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1302 |  | 1600 | -298 | 81 | []
BG_CO_00009 | N-1 400kV Maritsa Iztok 2Â - Maritsa Iztok 3 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1300 |  | 1600 | -300 | 81 | []
RS_MK_00001 | N-1 400 kV Vranje 4 -Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1298 |  | 1600 | -302 | 81 | []
BC | Base Case | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1297 |  | 1600 | -303 | 81 | []
RS_CO_00003 | N-1 400 kV Vranje 4 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1296 |  | 1600 | -304 | 81 | []
BG_CO_00005, BG_CO_00007 | N-1 400kV Vetren - Chervena Mogila , N-1 400kV Maritsa Iztok - Plovdiv ck. 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 |  | 1600 | -305 | 81 | []
BG_TR_CO_00001 | N-1 400kV Maritsa 3 - Hamitabat 1 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1295 |  | 1600 | -305 | 81 | []
BG_CO_00006, BG_CO_00008 | N-1 400kV Plovdiv - Vetren , N-1 400kV Plovdiv - Vetren | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1294 |  | 1600 | -306 | 81 | []
BG_TR_CO_00002 | N-1 400kV Maritsa 3 - Hamitabat 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1294 |  | 1600 | -306 | 81 | []
GR_CO_00005 | N-1 400 kV Thessaloniki-Lagadas ck.2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 |  | 1600 | -307 | 81 | []
RS_KS_CO_00002 | N-1 400 kV Kosovo B-Nis 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1293 |  | 1600 | -307 | 81 | []
RS_CO_00004 | N-1 400 kV Nis 2 âLeskovac 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1290 |  | 1600 | -310 | 81 | []
KS_CO_00001 | N-1 400 kV Kosovo B-Urosevac | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1274 |  | 1600 | -326 | 80 | []
MK_CO_00003 | N-1 400 kV Skopje 4 âSkopje 5 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1266 |  | 1600 | -334 | 79 | []
AL_ME_CO_00001 | N-1 400 kV Tirana 2âPodgorica 2 | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
BG_RS_CO_00001 | N-1 400kV Sofia Zapad - Nis Â | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
MK_CO_00002 | N-1 400 kV Dubrovo âStip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1182 |  | 1600 | -418 | 74 | []
MK_CO_00001 | N-1 400 kV Bitola-Dubrovo | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1178 |  | 1600 | -422 | 74 | []
BG_MK_CO_00001 | N-1 400kV Chervena Mogila - Stip | [MK-GR] 400 kV Bitola-Meliti | XFL_BI11_GMELIT11_1:line | -1174 |  | 1600 | -426 | 73 | []