## 0030Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3442
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1561 | 1570 | 1570 | -9 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1561 | 1570 | 1570 | -9 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1557 | 1570 | 1570 | -13 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1499 | 1570 | 1570 | -71 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1469 | 1570 | 1570 | -101 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1468 | 1570 | 1570 | -102 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 | 1570 | 1570 | -105 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 | 1570 | 1570 | -116 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1450 | 1570 | 1570 | -120 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1824 | 2000 | 2000 | -176 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1775 | -2000 | -2000 | -225 | 89 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1759 | -2000 | -2000 | -241 | 88 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1751 | -2000 | -2000 | -249 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1737 | 2000 | 2000 | -263 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1725 | -2000 | -2000 | -275 | 86 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1719 | -2000 | -2000 | -281 | 86 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | 1713 | 2001 | 2001 | -288 | 86 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1711 | -2000 | -2000 | -289 | 86 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1699 | 2000 | 2000 | -301 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1699 | -2000 | -2000 | -301 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 | -2000 | -2000 | -305 | 85 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1696 | 2001 | 2001 | -305 | 85 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 | -2000 | -2000 | -305 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 | -2000 | -2000 | -305 | 85 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1694 | -2000 | -2000 | -306 | 85 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1690 | -2000 | -2000 | -310 | 85 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1684 | -2000 | -2000 | -316 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -975 | -1248 | -1248 | -274 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -973 | -1248 | -1248 | -275 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -777 | -999 | -999 | -222 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -970 | -1248 | -1248 | -278 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -965 | -1248 | -1248 | -284 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -963 | -1248 | -1248 | -286 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -958 | -1248 | -1248 | -290 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1494 | 2000 | 2000 | -506 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1469 | 2000 | 2000 | -531 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1137 | 1601 | 1601 | -464 | 71 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1137 | 1601 | 1601 | -464 | 71 | []

## 0030Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3442
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1561 |  | 1570 | -9 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1561 |  | 1570 | -9 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1557 |  | 1570 | -13 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1499 |  | 1570 | -71 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1469 |  | 1570 | -101 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1468 |  | 1570 | -102 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 |  | 1570 | -105 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1570 | -116 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1450 |  | 1570 | -120 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1824 |  | 2000 | -176 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1775 |  | -2000 | -225 | 89 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1759 |  | -2000 | -241 | 88 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1751 |  | -2000 | -249 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1737 |  | 2000 | -263 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1725 |  | -2000 | -275 | 86 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1719 |  | -2000 | -281 | 86 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | 1713 |  | 2001 | -288 | 86 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1711 |  | -2000 | -289 | 86 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1699 |  | 2000 | -301 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1699 |  | -2000 | -301 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 |  | -2000 | -305 | 85 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1696 |  | 2001 | -305 | 85 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 |  | -2000 | -305 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 |  | -2000 | -305 | 85 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1694 |  | -2000 | -306 | 85 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1690 |  | -2000 | -310 | 85 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1684 |  | -2000 | -316 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -975 |  | -1248 | -274 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -973 |  | -1248 | -275 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -777 |  | -999 | -222 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -970 |  | -1248 | -278 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -965 |  | -1248 | -284 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -963 |  | -1248 | -286 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -958 |  | -1248 | -290 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1494 |  | 2000 | -506 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1469 |  | 2000 | -531 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1140 |  | 1600 | -460 | 71 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1140 |  | 1600 | -460 | 71 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1137 |  | 1601 | -464 | 71 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1137 |  | 1601 | -464 | 71 | []

## 0130Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3473
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1554 | 1570 | 1570 | -16 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1543 | 1570 | 1570 | -27 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1495 | 1570 | 1570 | -75 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1462 | 1570 | 1570 | -108 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1461 | 1570 | 1570 | -109 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 | 1570 | 1570 | -110 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1451 | 1570 | 1570 | -119 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1446 | 1570 | 1570 | -124 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1816 | 2000 | 2000 | -184 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1772 | -2000 | -2000 | -228 | 89 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1747 | -2000 | -2000 | -253 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1742 | -2000 | -2000 | -258 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1728 | -2000 | -2000 | -272 | 86 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1721 | -2000 | -2000 | -279 | 86 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1710 | -2000 | -2000 | -290 | 86 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 | -2000 | -2000 | -305 | 85 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1695 | 2001 | 2001 | -306 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1693 | -2000 | -2000 | -307 | 85 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1691 | -2000 | -2000 | -309 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1689 | -2000 | -2000 | -311 | 84 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 | -2000 | -2000 | -312 | 84 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 | -2000 | -2000 | -312 | 84 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1686 | -2000 | -2000 | -314 | 84 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1679 | -2000 | -2000 | -321 | 84 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1678 | 2001 | 2001 | -323 | 84 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1677 | -2000 | -2000 | -323 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -997 | -1248 | -1248 | -251 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -996 | -1248 | -1248 | -253 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -993 | -1248 | -1248 | -256 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -987 | -1248 | -1248 | -261 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -985 | -1248 | -1248 | -263 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -981 | -1248 | -1248 | -268 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1489 | 2000 | 2000 | -511 | 74 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1186 | 1600 | 1600 | -414 | 74 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1186 | 1600 | 1600 | -414 | 74 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1183 | 1601 | 1601 | -418 | 74 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1183 | 1601 | 1601 | -418 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1463 | 2000 | 2000 | -537 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -726 | -999 | -999 | -273 | 73 | []

## 0130Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3473
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1554 |  | 1570 | -16 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1543 |  | 1570 | -27 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1495 |  | 1570 | -75 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1462 |  | 1570 | -108 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1461 |  | 1570 | -109 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 |  | 1570 | -110 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1451 |  | 1570 | -119 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1446 |  | 1570 | -124 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1816 |  | 2000 | -184 | 91 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1772 |  | -2000 | -228 | 89 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1747 |  | -2000 | -253 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1742 |  | -2000 | -258 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1728 |  | -2000 | -272 | 86 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1721 |  | -2000 | -279 | 86 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1710 |  | -2000 | -290 | 86 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1695 |  | -2000 | -305 | 85 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1695 |  | 2001 | -306 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1693 |  | -2000 | -307 | 85 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1691 |  | -2000 | -309 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1689 |  | -2000 | -311 | 84 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 |  | -2000 | -312 | 84 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 |  | -2000 | -312 | 84 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1686 |  | -2000 | -314 | 84 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1679 |  | -2000 | -321 | 84 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1678 |  | 2001 | -323 | 84 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1677 |  | -2000 | -323 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -997 |  | -1248 | -251 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -996 |  | -1248 | -253 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -993 |  | -1248 | -256 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -987 |  | -1248 | -261 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -985 |  | -1248 | -263 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -981 |  | -1248 | -268 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1489 |  | 2000 | -511 | 74 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1186 |  | 1600 | -414 | 74 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1186 |  | 1600 | -414 | 74 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1183 |  | 1601 | -418 | 74 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1183 |  | 1601 | -418 | 74 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1463 |  | 2000 | -537 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -726 |  | -999 | -273 | 73 | []

## 0230Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3475
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1570 | 1570 | 1570 | 0 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1570 | 1570 | 1570 | 0 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1561 | 1570 | 1570 | -9 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1555 | 1570 | 1570 | -15 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1504 | 1570 | 1570 | -66 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1473 | 1570 | 1570 | -97 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1471 | 1570 | 1570 | -99 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1468 | 1570 | 1570 | -102 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 | 1570 | 1570 | -105 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 | 1570 | 1570 | -116 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1835 | 2000 | 2000 | -165 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1796 | -2000 | -2000 | -204 | 90 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1794 | -2000 | -2000 | -206 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1788 | -2000 | -2000 | -212 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1774 | -2000 | -2000 | -226 | 89 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1763 | -2000 | -2000 | -237 | 88 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1750 | -2000 | -2000 | -250 | 88 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1733 | -2000 | -2000 | -267 | 87 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1728 | -2000 | -2000 | -272 | 86 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1727 | -2000 | -2000 | -273 | 86 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1727 | -2000 | -2000 | -273 | 86 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1727 | -2000 | -2000 | -273 | 86 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1720 | -2000 | -2000 | -280 | 86 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1715 | -2000 | -2000 | -285 | 86 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1715 | 2001 | 2001 | -286 | 86 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1713 | -2000 | -2000 | -287 | 86 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1698 | 2001 | 2001 | -303 | 85 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1697 | -2000 | -2000 | -303 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -996 | -1248 | -1248 | -252 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -995 | -1248 | -1248 | -254 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -992 | -1248 | -1248 | -257 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -986 | -1248 | -1248 | -262 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -788 | -999 | -999 | -211 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -984 | -1248 | -1248 | -264 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -980 | -1248 | -1248 | -269 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1523 | 2000 | 2000 | -477 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1498 | 2000 | 2000 | -502 | 75 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1168 | 1600 | 1600 | -432 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1168 | 1600 | 1600 | -432 | 73 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1163 | 1601 | 1601 | -438 | 73 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1163 | 1601 | 1601 | -438 | 73 | []

## 0230Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3475
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1570 |  | 1570 | 0 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1570 |  | 1570 | 0 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1561 |  | 1570 | -9 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1555 |  | 1570 | -15 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1504 |  | 1570 | -66 | 96 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1473 |  | 1570 | -97 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1471 |  | 1570 | -99 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1468 |  | 1570 | -102 | 94 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 |  | 1570 | -105 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1570 | -116 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1835 |  | 2000 | -165 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1796 |  | -2000 | -204 | 90 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1794 |  | -2000 | -206 | 90 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1788 |  | -2000 | -212 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1774 |  | -2000 | -226 | 89 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1763 |  | -2000 | -237 | 88 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1750 |  | -2000 | -250 | 88 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1733 |  | -2000 | -267 | 87 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1728 |  | -2000 | -272 | 86 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1727 |  | -2000 | -273 | 86 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1727 |  | -2000 | -273 | 86 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1727 |  | -2000 | -273 | 86 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1720 |  | -2000 | -280 | 86 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1715 |  | -2000 | -285 | 86 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1715 |  | 2001 | -286 | 86 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1713 |  | -2000 | -287 | 86 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1698 |  | 2001 | -303 | 85 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1697 |  | -2000 | -303 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -996 |  | -1248 | -252 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -995 |  | -1248 | -254 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -992 |  | -1248 | -257 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -986 |  | -1248 | -262 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -788 |  | -999 | -211 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -984 |  | -1248 | -264 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -980 |  | -1248 | -269 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1523 |  | 2000 | -477 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1498 |  | 2000 | -502 | 75 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1168 |  | 1600 | -432 | 73 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1168 |  | 1600 | -432 | 73 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1163 |  | 1601 | -438 | 73 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1163 |  | 1601 | -438 | 73 | []

## 0330Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3418
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1554 | 1570 | 1570 | -16 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1549 | 1570 | 1570 | -21 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1501 | 1570 | 1570 | -69 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1464 | 1570 | 1570 | -106 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1462 | 1570 | 1570 | -108 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1461 | 1570 | 1570 | -109 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 | 1570 | 1570 | -118 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 | 1570 | 1570 | -118 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1793 | 2000 | 2000 | -207 | 90 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1757 | -2000 | -2000 | -243 | 88 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1754 | -2000 | -2000 | -246 | 88 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1752 | -2000 | -2000 | -248 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1734 | -2000 | -2000 | -266 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1730 | -2000 | -2000 | -270 | 87 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1710 | -2000 | -2000 | -290 | 86 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1695 | -2000 | -2000 | -305 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1694 | -2000 | -2000 | -306 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1691 | -2000 | -2000 | -309 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1690 | -2000 | -2000 | -310 | 85 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1690 | -2000 | -2000 | -310 | 85 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1687 | -2000 | -2000 | -313 | 84 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1683 | -2000 | -2000 | -317 | 84 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | -1665 | 2001 | 2001 | -336 | 83 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1664 | -2000 | -2000 | -336 | 83 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1648 | 2001 | 2001 | -353 | 82 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1647 | -2000 | -2000 | -353 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1007 | -1248 | -1248 | -242 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1005 | -1248 | -1248 | -243 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1002 | -1248 | -1248 | -246 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -996 | -1248 | -1248 | -252 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -994 | -1248 | -1248 | -254 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -990 | -1248 | -1248 | -259 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -781 | -999 | -999 | -218 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1492 | 2000 | 2000 | -508 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1466 | 2000 | 2000 | -534 | 73 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1152 | 1600 | 1600 | -448 | 72 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1152 | 1600 | 1600 | -448 | 72 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1147 | 1601 | 1601 | -454 | 72 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1147 | 1601 | 1601 | -454 | 72 | []

## 0330Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3418
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1554 |  | 1570 | -16 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1549 |  | 1570 | -21 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1501 |  | 1570 | -69 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1464 |  | 1570 | -106 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1462 |  | 1570 | -108 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1461 |  | 1570 | -109 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1570 | -118 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1570 | -118 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1793 |  | 2000 | -207 | 90 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1757 |  | -2000 | -243 | 88 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1754 |  | -2000 | -246 | 88 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1752 |  | -2000 | -248 | 88 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1734 |  | -2000 | -266 | 87 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1730 |  | -2000 | -270 | 87 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1710 |  | -2000 | -290 | 86 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1695 |  | -2000 | -305 | 85 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1694 |  | -2000 | -306 | 85 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1691 |  | -2000 | -309 | 85 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1690 |  | -2000 | -310 | 85 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1690 |  | -2000 | -310 | 85 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1687 |  | -2000 | -313 | 84 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1683 |  | -2000 | -317 | 84 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | -1665 |  | 2001 | -336 | 83 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1664 |  | -2000 | -336 | 83 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1648 |  | 2001 | -353 | 82 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1647 |  | -2000 | -353 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1007 |  | -1248 | -242 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1005 |  | -1248 | -243 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1002 |  | -1248 | -246 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -996 |  | -1248 | -252 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -994 |  | -1248 | -254 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -990 |  | -1248 | -259 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -781 |  | -999 | -218 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1492 |  | 2000 | -508 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1466 |  | 2000 | -534 | 73 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1152 |  | 1600 | -448 | 72 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1152 |  | 1600 | -448 | 72 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1147 |  | 1601 | -454 | 72 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1147 |  | 1601 | -454 | 72 | []

## 0430Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3363
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1563 | 1570 | 1570 | -7 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1557 | 1570 | 1570 | -13 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 | 1570 | 1570 | -63 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1470 | 1570 | 1570 | -100 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1469 | 1570 | 1570 | -101 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1467 | 1570 | 1570 | -103 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1459 | 1570 | 1570 | -111 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1457 | 1570 | 1570 | -113 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1761 | 2000 | 2000 | -239 | 88 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1733 | -2000 | -2000 | -267 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1730 | -2000 | -2000 | -270 | 87 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1721 | -2000 | -2000 | -279 | 86 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1711 | -2000 | -2000 | -289 | 86 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1704 | -2000 | -2000 | -296 | 85 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1686 | -2000 | -2000 | -314 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1671 | -2000 | -2000 | -329 | 84 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1669 | -2000 | -2000 | -331 | 83 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1665 | -2000 | -2000 | -335 | 83 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1664 | -2000 | -2000 | -336 | 83 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1664 | -2000 | -2000 | -336 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1664 | -2000 | -2000 | -336 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1659 | -2000 | -2000 | -341 | 83 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1640 | 2001 | 2001 | -361 | 82 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1639 | -2000 | -2000 | -361 | 82 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1624 | 2001 | 2001 | -377 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1622 | -2000 | -2000 | -378 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1007 | -1248 | -1248 | -242 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1005 | -1248 | -1248 | -243 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1002 | -1248 | -1248 | -246 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -996 | -1248 | -1248 | -252 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -995 | -1248 | -1248 | -254 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -990 | -1248 | -1248 | -259 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -776 | -999 | -999 | -223 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1470 | 2000 | 2000 | -530 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1445 | 2000 | 2000 | -555 | 72 | []

## 0430Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3363
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI1-KOZLODUI | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1563 |  | 1570 | -7 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1557 |  | 1570 | -13 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 |  | 1570 | -63 | 96 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1470 |  | 1570 | -100 | 94 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1469 |  | 1570 | -101 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1467 |  | 1570 | -103 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1459 |  | 1570 | -111 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1457 |  | 1570 | -113 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1761 |  | 2000 | -239 | 88 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1733 |  | -2000 | -267 | 87 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1730 |  | -2000 | -270 | 87 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1721 |  | -2000 | -279 | 86 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1711 |  | -2000 | -289 | 86 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1704 |  | -2000 | -296 | 85 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1686 |  | -2000 | -314 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1671 |  | -2000 | -329 | 84 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1669 |  | -2000 | -331 | 83 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1665 |  | -2000 | -335 | 83 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1664 |  | -2000 | -336 | 83 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1664 |  | -2000 | -336 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1664 |  | -2000 | -336 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1659 |  | -2000 | -341 | 83 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1640 |  | 2001 | -361 | 82 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1639 |  | -2000 | -361 | 82 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1624 |  | 2001 | -377 | 81 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1622 |  | -2000 | -378 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1007 |  | -1248 | -242 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1005 |  | -1248 | -243 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -1002 |  | -1248 | -246 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -996 |  | -1248 | -252 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -995 |  | -1248 | -254 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -990 |  | -1248 | -259 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -776 |  | -999 | -223 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1470 |  | 2000 | -530 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1445 |  | 2000 | -555 | 72 | []

## 0530Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3011
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1556 | 1570 | 1570 | -14 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 | 1570 | 1570 | -63 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 | 1570 | 1570 | -63 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1475 | 1570 | 1570 | -95 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1444 | 1570 | 1570 | -126 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1440 | 1570 | 1570 | -130 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1436 | 1570 | 1570 | -134 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1436 | 1570 | 1570 | -134 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1420 | 1570 | 1570 | -150 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -836 | -999 | -999 | -163 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1631 | -2000 | -2000 | -369 | 82 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1630 | -2000 | -2000 | -370 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1598 | -2000 | -2000 | -402 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1574 | -2000 | -2000 | -426 | 79 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1562 | -2000 | -2000 | -438 | 78 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1561 | -2000 | -2000 | -439 | 78 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1546 | -2000 | -2000 | -454 | 77 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1538 | -2000 | -2000 | -462 | 77 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1537 | -2000 | -2000 | -463 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1530 | -2000 | -2000 | -470 | 77 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1530 | -2000 | -2000 | -470 | 77 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1530 | -2000 | -2000 | -470 | 77 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1530 | -2000 | -2000 | -470 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -947 | -1248 | -1248 | -301 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -946 | -1248 | -1248 | -303 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -943 | -1248 | -1248 | -306 | 76 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1508 | -2000 | -2000 | -492 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -937 | -1248 | -1248 | -311 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -935 | -1248 | -1248 | -313 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -931 | -1248 | -1248 | -318 | 75 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1470 | 2001 | 2001 | -531 | 73 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1469 | -2000 | -2000 | -531 | 73 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1455 | 2001 | 2001 | -546 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1454 | -2000 | -2000 | -546 | 73 | []

## 0530Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3011
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1556 |  | 1570 | -14 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 |  | 1570 | -63 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1507 |  | 1570 | -63 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1475 |  | 1570 | -95 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1570 | -126 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1440 |  | 1570 | -130 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1436 |  | 1570 | -134 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1436 |  | 1570 | -134 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1420 |  | 1570 | -150 | 90 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -836 |  | -999 | -163 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1631 |  | -2000 | -369 | 82 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1630 |  | -2000 | -370 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1598 |  | -2000 | -402 | 80 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1574 |  | -2000 | -426 | 79 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1562 |  | -2000 | -438 | 78 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1561 |  | -2000 | -439 | 78 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1546 |  | -2000 | -454 | 77 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1538 |  | -2000 | -462 | 77 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1537 |  | -2000 | -463 | 77 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1530 |  | -2000 | -470 | 77 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1530 |  | -2000 | -470 | 77 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1530 |  | -2000 | -470 | 77 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1530 |  | -2000 | -470 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -947 |  | -1248 | -301 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -946 |  | -1248 | -303 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -943 |  | -1248 | -306 | 76 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1508 |  | -2000 | -492 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -937 |  | -1248 | -311 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -935 |  | -1248 | -313 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -931 |  | -1248 | -318 | 75 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1470 |  | 2001 | -531 | 73 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1469 |  | -2000 | -531 | 73 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1455 |  | 2001 | -546 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1454 |  | -2000 | -546 | 73 | []

## 0630Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2555
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1552 | 1570 | 1570 | -18 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1474 | 1570 | 1570 | -96 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1474 | 1570 | 1570 | -96 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 | 1570 | 1570 | -105 | 93 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -922 | -999 | -999 | -77 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 | 1570 | 1570 | -139 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1426 | 1570 | 1570 | -144 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 | 1570 | 1570 | -146 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1420 | 1570 | 1570 | -150 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1402 | 1570 | 1570 | -168 | 89 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -923 | -1248 | -1248 | -325 | 74 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1477 | -2000 | -2000 | -523 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -922 | -1248 | -1248 | -327 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -919 | -1248 | -1248 | -329 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -913 | -1248 | -1248 | -335 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -912 | -1248 | -1248 | -337 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -907 | -1248 | -1248 | -341 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1425 | -2000 | -2000 | -575 | 71 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1412 | -2000 | -2000 | -588 | 71 | []

## 0630Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2555
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1552 |  | 1570 | -18 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1474 |  | 1570 | -96 | 94 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1474 |  | 1570 | -96 | 94 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 |  | 1570 | -105 | 93 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -922 |  | -999 | -77 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 |  | 1570 | -139 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1426 |  | 1570 | -144 | 91 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 |  | 1570 | -146 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1420 |  | 1570 | -150 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1402 |  | 1570 | -168 | 89 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -923 |  | -1248 | -325 | 74 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1477 |  | -2000 | -523 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -922 |  | -1248 | -327 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -919 |  | -1248 | -329 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -913 |  | -1248 | -335 | 73 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -912 |  | -1248 | -337 | 73 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -907 |  | -1248 | -341 | 73 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1425 |  | -2000 | -575 | 71 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1412 |  | -2000 | -588 | 71 | []

## 0730Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2393
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -932 | -999 | -999 | -67 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 | 1570 | 1570 | -114 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 | 1570 | 1570 | -116 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 | 1570 | 1570 | -116 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 | 1570 | 1570 | -139 | 91 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1428 | 1570 | 1570 | -142 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 | 1570 | 1570 | -146 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1391 | 1570 | 1570 | -179 | 89 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -885 | -1248 | -1248 | -364 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -883 | -1248 | -1248 | -366 | 71 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1411 | -2000 | -2000 | -589 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -880 | -1248 | -1248 | -368 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -874 | -1248 | -1248 | -374 | 70 | []

## 0730Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2393
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -932 |  | -999 | -67 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 |  | 1570 | -114 | 93 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1570 | -116 | 93 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1570 | -116 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 |  | 1570 | -139 | 91 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1428 |  | 1570 | -142 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 |  | 1570 | -146 | 91 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1391 |  | 1570 | -179 | 89 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -885 |  | -1248 | -364 | 71 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -883 |  | -1248 | -366 | 71 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1411 |  | -2000 | -589 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -880 |  | -1248 | -368 | 71 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -874 |  | -1248 | -374 | 70 | []

## 0830Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 1911
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -925 | -999 | -999 | -74 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1418 | 1570 | 1570 | -152 | 90 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1388 | 1570 | 1570 | -182 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1385 | 1570 | 1570 | -185 | 88 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1385 | 1570 | 1570 | -185 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1383 | 1570 | 1570 | -187 | 88 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1381 | 1570 | 1570 | -189 | 88 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1351 | 1570 | 1570 | -219 | 86 | []

## 0830Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 1911
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -925 |  | -999 | -74 | 93 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1418 |  | 1570 | -152 | 90 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1388 |  | 1570 | -182 | 88 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1385 |  | 1570 | -185 | 88 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1385 |  | 1570 | -185 | 88 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1383 |  | 1570 | -187 | 88 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1381 |  | 1570 | -189 | 88 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1351 |  | 1570 | -219 | 86 | []

## 0930Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3212
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1558 | 1570 | 1570 | -12 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1549 | 1570 | 1570 | -21 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1549 | 1570 | 1570 | -21 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1483 | 1570 | 1570 | -87 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1443 | 1570 | 1570 | -127 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1442 | 1570 | 1570 | -128 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1441 | 1570 | 1570 | -129 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1437 | 1570 | 1570 | -133 | 92 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1000 | -1248 | -1248 | -248 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -999 | -1248 | -1248 | -250 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -996 | -1248 | -1248 | -253 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -990 | -1248 | -1248 | -258 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -988 | -1248 | -1248 | -260 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -984 | -1248 | -1248 | -264 | 79 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1565 | -2000 | -2000 | -435 | 78 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1553 | 2000 | 2000 | -447 | 78 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1552 | -2000 | -2000 | -448 | 78 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1524 | -2000 | -2000 | -476 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1504 | -2000 | -2000 | -496 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1503 | -2000 | -2000 | -497 | 75 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1494 | -2000 | -2000 | -506 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1489 | -2000 | -2000 | -511 | 74 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1475 | -2000 | -2000 | -525 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1475 | -2000 | -2000 | -525 | 74 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | 1472 | 2001 | 2001 | -529 | 74 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1471 | -2000 | -2000 | -529 | 74 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1471 | -2000 | -2000 | -529 | 74 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1470 | -2000 | -2000 | -530 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1470 | -2000 | -2000 | -530 | 73 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1464 | -2000 | -2000 | -536 | 73 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | 1456 | 2001 | 2001 | -545 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1454 | -2000 | -2000 | -546 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -702 | -999 | -999 | -297 | 70 | []

## 0930Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3212
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1558 |  | 1570 | -12 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1549 |  | 1570 | -21 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1549 |  | 1570 | -21 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1483 |  | 1570 | -87 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1443 |  | 1570 | -127 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1442 |  | 1570 | -128 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1441 |  | 1570 | -129 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1437 |  | 1570 | -133 | 92 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1000 |  | -1248 | -248 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -999 |  | -1248 | -250 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -996 |  | -1248 | -253 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -990 |  | -1248 | -258 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -988 |  | -1248 | -260 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -984 |  | -1248 | -264 | 79 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1565 |  | -2000 | -435 | 78 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1553 |  | 2000 | -447 | 78 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1552 |  | -2000 | -448 | 78 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1524 |  | -2000 | -476 | 76 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1504 |  | -2000 | -496 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1503 |  | -2000 | -497 | 75 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1494 |  | -2000 | -506 | 75 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1489 |  | -2000 | -511 | 74 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1475 |  | -2000 | -525 | 74 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1475 |  | -2000 | -525 | 74 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | 1472 |  | 2001 | -529 | 74 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1471 |  | -2000 | -529 | 74 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1471 |  | -2000 | -529 | 74 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1470 |  | -2000 | -530 | 74 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1470 |  | -2000 | -530 | 73 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1464 |  | -2000 | -536 | 73 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | 1456 |  | 2001 | -545 | 73 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1454 |  | -2000 | -546 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -702 |  | -999 | -297 | 70 | []

## 1030Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3445
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1541 | 1570 | 1570 | -29 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1526 | 1570 | 1570 | -44 | 97 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1481 | 1570 | 1570 | -89 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1448 | 1570 | 1570 | -122 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1432 | 1570 | 1570 | -138 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 | 1570 | 1570 | -139 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1427 | 1570 | 1570 | -143 | 91 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1726 | 2000 | 2000 | -274 | 86 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1059 | -1248 | -1248 | -189 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1058 | -1248 | -1248 | -190 | 85 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1055 | -1248 | -1248 | -194 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1050 | -1248 | -1248 | -199 | 84 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1680 | -2000 | -2000 | -320 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1047 | -1248 | -1248 | -201 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1043 | -1248 | -1248 | -205 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1643 | -2000 | -2000 | -357 | 82 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1628 | -2000 | -2000 | -372 | 81 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1615 | 2001 | 2001 | -386 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1614 | -2000 | -2000 | -386 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1612 | -2000 | -2000 | -388 | 81 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1609 | -2000 | -2000 | -391 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1605 | -2000 | -2000 | -395 | 80 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1598 | 2001 | 2001 | -403 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1597 | -2000 | -2000 | -403 | 80 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1591 | -2000 | -2000 | -409 | 80 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1580 | -2000 | -2000 | -420 | 79 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1580 | -2000 | -2000 | -420 | 79 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1579 | -2000 | -2000 | -421 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1578 | -2000 | -2000 | -422 | 79 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1577 | -2000 | -2000 | -423 | 79 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1567 | -2000 | -2000 | -433 | 78 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1208 | 1601 | 1601 | -393 | 75 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1208 | 1601 | 1601 | -393 | 75 | []

## 1030Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3445
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1541 |  | 1570 | -29 | 98 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1526 |  | 1570 | -44 | 97 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1481 |  | 1570 | -89 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1448 |  | 1570 | -122 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1432 |  | 1570 | -138 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 |  | 1570 | -139 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1570 | -143 | 91 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1726 |  | 2000 | -274 | 86 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1059 |  | -1248 | -189 | 85 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1058 |  | -1248 | -190 | 85 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1055 |  | -1248 | -194 | 84 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1050 |  | -1248 | -199 | 84 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1680 |  | -2000 | -320 | 84 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1047 |  | -1248 | -201 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1043 |  | -1248 | -205 | 84 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1643 |  | -2000 | -357 | 82 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1628 |  | -2000 | -372 | 81 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1615 |  | 2001 | -386 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1614 |  | -2000 | -386 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1612 |  | -2000 | -388 | 81 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1609 |  | -2000 | -391 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1605 |  | -2000 | -395 | 80 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1598 |  | 2001 | -403 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1597 |  | -2000 | -403 | 80 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1591 |  | -2000 | -409 | 80 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1580 |  | -2000 | -420 | 79 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1580 |  | -2000 | -420 | 79 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1579 |  | -2000 | -421 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1578 |  | -2000 | -422 | 79 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1577 |  | -2000 | -423 | 79 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1567 |  | -2000 | -433 | 78 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1212 |  | 1600 | -388 | 76 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1212 |  | 1600 | -388 | 76 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1208 |  | 1601 | -393 | 75 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1208 |  | 1601 | -393 | 75 | []

## 1130Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2611
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1551 | 1570 | 1570 | -19 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1499 | 1570 | 1570 | -71 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1499 | 1570 | 1570 | -71 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1462 | 1570 | 1570 | -108 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1423 | 1570 | 1570 | -147 | 91 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1420 | 1570 | 1570 | -150 | 90 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1418 | 1570 | 1570 | -152 | 90 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1412 | 1570 | 1570 | -158 | 90 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -932 | -1248 | -1248 | -316 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -931 | -1248 | -1248 | -318 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -928 | -1248 | -1248 | -321 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -922 | -1248 | -1248 | -326 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -920 | -1248 | -1248 | -328 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -916 | -1248 | -1248 | -332 | 73 | []

## 1130Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2611
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1551 |  | 1570 | -19 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1499 |  | 1570 | -71 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1499 |  | 1570 | -71 | 95 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1462 |  | 1570 | -108 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1423 |  | 1570 | -147 | 91 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1420 |  | 1570 | -150 | 90 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1418 |  | 1570 | -152 | 90 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1412 |  | 1570 | -158 | 90 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -932 |  | -1248 | -316 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -931 |  | -1248 | -318 | 75 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -928 |  | -1248 | -321 | 74 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -922 |  | -1248 | -326 | 74 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -920 |  | -1248 | -328 | 74 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -916 |  | -1248 | -332 | 73 | []

## 1230Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2687
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1552 | 1570 | 1570 | -18 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1514 | 1570 | 1570 | -56 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1514 | 1570 | 1570 | -56 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1472 | 1570 | 1570 | -98 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1434 | 1570 | 1570 | -136 | 91 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1429 | 1570 | 1570 | -141 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1427 | 1570 | 1570 | -143 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1421 | 1570 | 1570 | -149 | 91 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -950 | -1248 | -1248 | -299 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -948 | -1248 | -1248 | -301 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -945 | -1248 | -1248 | -303 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -939 | -1248 | -1248 | -309 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -938 | -1248 | -1248 | -311 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -933 | -1248 | -1248 | -315 | 75 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1406 | -2000 | -2000 | -594 | 70 | []

## 1230Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2687
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1552 |  | 1570 | -18 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1514 |  | 1570 | -56 | 96 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1514 |  | 1570 | -56 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1472 |  | 1570 | -98 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1434 |  | 1570 | -136 | 91 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1429 |  | 1570 | -141 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1570 | -143 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1421 |  | 1570 | -149 | 91 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -950 |  | -1248 | -299 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -948 |  | -1248 | -301 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -945 |  | -1248 | -303 | 76 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -939 |  | -1248 | -309 | 75 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -938 |  | -1248 | -311 | 75 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -933 |  | -1248 | -315 | 75 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1406 |  | -2000 | -594 | 70 | []

## 1330Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 2877
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 | 1570 | 1570 | -35 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1526 | 1570 | 1570 | -44 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1526 | 1570 | 1570 | -44 | 97 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1474 | 1570 | 1570 | -96 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1438 | 1570 | 1570 | -132 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 | 1570 | 1570 | -139 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1430 | 1570 | 1570 | -140 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 | 1570 | 1570 | -146 | 91 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -963 | -1248 | -1248 | -286 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -961 | -1248 | -1248 | -288 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -958 | -1248 | -1248 | -290 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -952 | -1248 | -1248 | -296 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -951 | -1248 | -1248 | -298 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -946 | -1248 | -1248 | -302 | 76 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1487 | -2000 | -2000 | -513 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1455 | -2000 | -2000 | -545 | 73 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1435 | -2000 | -2000 | -565 | 72 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1425 | -2000 | -2000 | -575 | 71 | []

## 1330Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 2877
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 |  | 1570 | -35 | 98 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1526 |  | 1570 | -44 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1526 |  | 1570 | -44 | 97 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1474 |  | 1570 | -96 | 94 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1438 |  | 1570 | -132 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1431 |  | 1570 | -139 | 91 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1430 |  | 1570 | -140 | 91 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1424 |  | 1570 | -146 | 91 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -963 |  | -1248 | -286 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -961 |  | -1248 | -288 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -958 |  | -1248 | -290 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -952 |  | -1248 | -296 | 76 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -951 |  | -1248 | -298 | 76 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -946 |  | -1248 | -302 | 76 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1487 |  | -2000 | -513 | 74 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1455 |  | -2000 | -545 | 73 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1435 |  | -2000 | -565 | 72 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1425 |  | -2000 | -575 | 71 | []

## 1430Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3045
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1546 | 1570 | 1570 | -24 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1546 | 1570 | 1570 | -24 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1539 | 1570 | 1570 | -31 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1486 | 1570 | 1570 | -84 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1450 | 1570 | 1570 | -120 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 | 1570 | 1570 | -125 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1444 | 1570 | 1570 | -126 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1440 | 1570 | 1570 | -130 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1568 | -2000 | -2000 | -432 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -972 | -1248 | -1248 | -277 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -970 | -1248 | -1248 | -278 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -967 | -1248 | -1248 | -281 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1546 | -2000 | -2000 | -454 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -962 | -1248 | -1248 | -287 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -960 | -1248 | -1248 | -289 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -955 | -1248 | -1248 | -293 | 77 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1521 | -2000 | -2000 | -479 | 76 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1513 | -2000 | -2000 | -487 | 76 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1510 | -2000 | -2000 | -490 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1486 | -2000 | -2000 | -514 | 74 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1484 | -2000 | -2000 | -516 | 74 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1473 | -2000 | -2000 | -527 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1473 | -2000 | -2000 | -527 | 74 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1469 | -2000 | -2000 | -531 | 73 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1469 | -2000 | -2000 | -531 | 73 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1468 | -2000 | -2000 | -532 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1460 | -2000 | -2000 | -540 | 73 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1450 | -2000 | -2000 | -550 | 72 | []

## 1430Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3045
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1546 |  | 1570 | -24 | 99 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1546 |  | 1570 | -24 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1539 |  | 1570 | -31 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1486 |  | 1570 | -84 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1450 |  | 1570 | -120 | 92 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1570 | -125 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1570 | -126 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1440 |  | 1570 | -130 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1568 |  | -2000 | -432 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -972 |  | -1248 | -277 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -970 |  | -1248 | -278 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -967 |  | -1248 | -281 | 77 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1546 |  | -2000 | -454 | 77 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -962 |  | -1248 | -287 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -960 |  | -1248 | -289 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -955 |  | -1248 | -293 | 77 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1521 |  | -2000 | -479 | 76 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1513 |  | -2000 | -487 | 76 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1510 |  | -2000 | -490 | 75 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1486 |  | -2000 | -514 | 74 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1484 |  | -2000 | -516 | 74 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1473 |  | -2000 | -527 | 74 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1473 |  | -2000 | -527 | 74 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1469 |  | -2000 | -531 | 73 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1469 |  | -2000 | -531 | 73 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1468 |  | -2000 | -532 | 73 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1460 |  | -2000 | -540 | 73 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1450 |  | -2000 | -550 | 72 | []

## 1530Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3240
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1564 | 1570 | 1570 | -6 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1547 | 1570 | 1570 | -23 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1498 | 1570 | 1570 | -72 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1462 | 1570 | 1570 | -108 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 | 1570 | 1570 | -112 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 | 1570 | 1570 | -114 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1453 | 1570 | 1570 | -117 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1658 | 2000 | 2000 | -342 | 83 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1654 | -2000 | -2000 | -346 | 83 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1629 | -2000 | -2000 | -371 | 81 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 | -2000 | -2000 | -375 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 | -2000 | -2000 | -375 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1613 | -2000 | -2000 | -387 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1005 | -1248 | -1248 | -243 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1004 | -1248 | -1248 | -245 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1001 | -1248 | -1248 | -248 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -995 | -1248 | -1248 | -254 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1592 | -2000 | -2000 | -408 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -993 | -1248 | -1248 | -256 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -988 | -1248 | -1248 | -260 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1576 | -2000 | -2000 | -424 | 79 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1575 | -2000 | -2000 | -425 | 79 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1572 | -2000 | -2000 | -428 | 79 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1572 | -2000 | -2000 | -428 | 79 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1572 | -2000 | -2000 | -428 | 79 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1562 | -2000 | -2000 | -438 | 78 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1553 | -2000 | -2000 | -447 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1521 | -2000 | -2000 | -479 | 76 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1521 | 2001 | 2001 | -480 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1505 | -2000 | -2000 | -495 | 75 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1505 | 2001 | 2001 | -496 | 75 | []

## 1530Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3240
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1564 |  | 1570 | -6 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1547 |  | 1570 | -23 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1498 |  | 1570 | -72 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1462 |  | 1570 | -108 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1458 |  | 1570 | -112 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 |  | 1570 | -114 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1453 |  | 1570 | -117 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1658 |  | 2000 | -342 | 83 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1654 |  | -2000 | -346 | 83 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1629 |  | -2000 | -371 | 81 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 |  | -2000 | -375 | 81 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 |  | -2000 | -375 | 81 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1613 |  | -2000 | -387 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1005 |  | -1248 | -243 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1004 |  | -1248 | -245 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1001 |  | -1248 | -248 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -995 |  | -1248 | -254 | 80 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1592 |  | -2000 | -408 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -993 |  | -1248 | -256 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -988 |  | -1248 | -260 | 79 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1576 |  | -2000 | -424 | 79 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1575 |  | -2000 | -425 | 79 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1572 |  | -2000 | -428 | 79 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1572 |  | -2000 | -428 | 79 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1572 |  | -2000 | -428 | 79 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1562 |  | -2000 | -438 | 78 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1553 |  | -2000 | -447 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1521 |  | -2000 | -479 | 76 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1521 |  | 2001 | -480 | 76 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1505 |  | -2000 | -495 | 75 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1505 |  | 2001 | -496 | 75 | []

## 1630Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3364
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1567 | 1570 | 1570 | -3 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1567 | 1570 | 1570 | -3 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1553 | 1570 | 1570 | -17 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1536 | 1570 | 1570 | -34 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1487 | 1570 | 1570 | -83 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 | 1570 | 1570 | -118 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1449 | 1570 | 1570 | -121 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 | 1570 | 1570 | -125 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 | 1570 | 1570 | -125 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1751 | 2000 | 2000 | -249 | 88 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1713 | -2000 | -2000 | -287 | 86 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1703 | -2000 | -2000 | -297 | 85 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 | -2000 | -2000 | -312 | 84 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 | -2000 | -2000 | -312 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1675 | -2000 | -2000 | -325 | 84 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1659 | -2000 | -2000 | -341 | 83 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1642 | -2000 | -2000 | -358 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1639 | -2000 | -2000 | -361 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1638 | -2000 | -2000 | -362 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1638 | -2000 | -2000 | -362 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1638 | -2000 | -2000 | -362 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1020 | -1248 | -1248 | -229 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1019 | -1248 | -1248 | -230 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1015 | -1248 | -1248 | -233 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 | -2000 | -2000 | -375 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1010 | -1248 | -1248 | -239 | 81 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1617 | -2000 | -2000 | -383 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1615 | -2000 | -2000 | -385 | 81 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | -1616 | 2001 | 2001 | -385 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1008 | -1248 | -1248 | -241 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1003 | -1248 | -1248 | -245 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1599 | -2000 | -2000 | -401 | 80 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1599 | 2001 | 2001 | -402 | 80 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1449 | 2000 | 2000 | -551 | 72 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1424 | 2000 | 2000 | -576 | 71 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1134 | 1601 | 1601 | -467 | 71 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1134 | 1601 | 1601 | -467 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3364
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1570 | -3 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1570 | -3 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1553 |  | 1570 | -17 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1536 |  | 1570 | -34 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1487 |  | 1570 | -83 | 95 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1570 | -118 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1449 |  | 1570 | -121 | 92 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1570 | -125 | 92 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1570 | -125 | 92 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1751 |  | 2000 | -249 | 88 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1713 |  | -2000 | -287 | 86 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1703 |  | -2000 | -297 | 85 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 |  | -2000 | -312 | 84 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1688 |  | -2000 | -312 | 84 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1675 |  | -2000 | -325 | 84 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1659 |  | -2000 | -341 | 83 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1642 |  | -2000 | -358 | 82 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1639 |  | -2000 | -361 | 82 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1638 |  | -2000 | -362 | 82 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1638 |  | -2000 | -362 | 82 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1638 |  | -2000 | -362 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1020 |  | -1248 | -229 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1019 |  | -1248 | -230 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1015 |  | -1248 | -233 | 81 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1625 |  | -2000 | -375 | 81 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1010 |  | -1248 | -239 | 81 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1617 |  | -2000 | -383 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1615 |  | -2000 | -385 | 81 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | -1616 |  | 2001 | -385 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1008 |  | -1248 | -241 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -1003 |  | -1248 | -245 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1599 |  | -2000 | -401 | 80 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1599 |  | 2001 | -402 | 80 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1449 |  | 2000 | -551 | 72 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1140 |  | 1600 | -460 | 71 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1140 |  | 1600 | -460 | 71 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1424 |  | 2000 | -576 | 71 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1134 |  | 1601 | -467 | 71 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1134 |  | 1601 | -467 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3458
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1562 | 1570 | 1570 | -8 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1553 | 1570 | 1570 | -17 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1497 | 1570 | 1570 | -73 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1467 | 1570 | 1570 | -103 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 | 1570 | 1570 | -105 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1463 | 1570 | 1570 | -107 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1861 | 2000 | 2000 | -139 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1448 | 1570 | 1570 | -122 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1838 | -2000 | -2000 | -162 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1837 | -2000 | -2000 | -163 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1832 | -2000 | -2000 | -168 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1820 | -2000 | -2000 | -180 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1811 | -2000 | -2000 | -189 | 91 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1783 | -2000 | -2000 | -217 | 89 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1779 | -2000 | -2000 | -221 | 89 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1771 | -2000 | -2000 | -229 | 89 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1769 | -2000 | -2000 | -231 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1769 | -2000 | -2000 | -231 | 88 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1749 | -2000 | -2000 | -251 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1739 | -2000 | -2000 | -261 | 87 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1735 | -2000 | -2000 | -265 | 87 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1699 | 2001 | 2001 | -302 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1698 | -2000 | -2000 | -302 | 85 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1682 | 2001 | 2001 | -319 | 84 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1681 | -2000 | -2000 | -319 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -987 | -1248 | -1248 | -262 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -985 | -1248 | -1248 | -263 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -982 | -1248 | -1248 | -266 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1572 | 2000 | 2000 | -428 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -977 | -1248 | -1248 | -272 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -975 | -1248 | -1248 | -274 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -778 | -999 | -999 | -221 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -970 | -1248 | -1248 | -278 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1546 | 2000 | 2000 | -454 | 77 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1177 | 1601 | 1601 | -424 | 73 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1177 | 1601 | 1601 | -424 | 73 | []

## 1730Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3458
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1562 |  | 1570 | -8 | 100 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1553 |  | 1570 | -17 | 99 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1497 |  | 1570 | -73 | 95 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1467 |  | 1570 | -103 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1465 |  | 1570 | -105 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1463 |  | 1570 | -107 | 93 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1861 |  | 2000 | -139 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1448 |  | 1570 | -122 | 92 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1838 |  | -2000 | -162 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1837 |  | -2000 | -163 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1832 |  | -2000 | -168 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1820 |  | -2000 | -180 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1811 |  | -2000 | -189 | 91 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1783 |  | -2000 | -217 | 89 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1779 |  | -2000 | -221 | 89 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1771 |  | -2000 | -229 | 89 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1769 |  | -2000 | -231 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1769 |  | -2000 | -231 | 88 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1749 |  | -2000 | -251 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1739 |  | -2000 | -261 | 87 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1735 |  | -2000 | -265 | 87 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1699 |  | 2001 | -302 | 85 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1698 |  | -2000 | -302 | 85 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1682 |  | 2001 | -319 | 84 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1681 |  | -2000 | -319 | 84 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -987 |  | -1248 | -262 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -985 |  | -1248 | -263 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -982 |  | -1248 | -266 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1572 |  | 2000 | -428 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -977 |  | -1248 | -272 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -975 |  | -1248 | -274 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -778 |  | -999 | -221 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -970 |  | -1248 | -278 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1546 |  | 2000 | -454 | 77 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1182 |  | 1600 | -418 | 74 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1182 |  | 1600 | -418 | 74 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1177 |  | 1601 | -424 | 73 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1177 |  | 1601 | -424 | 73 | []

## 1830Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3347
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1550 | 1570 | 1570 | -20 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1550 | 1570 | 1570 | -20 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1542 | 1570 | 1570 | -28 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1488 | 1570 | 1570 | -82 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1459 | 1570 | 1570 | -111 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 | 1570 | 1570 | -116 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 | 1570 | 1570 | -118 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1451 | 1570 | 1570 | -119 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1435 | 1570 | 1570 | -135 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1764 | -2000 | -2000 | -236 | 88 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1752 | -2000 | -2000 | -248 | 88 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1745 | -2000 | -2000 | -255 | 87 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1736 | 2000 | 2000 | -264 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1734 | -2000 | -2000 | -266 | 87 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1700 | -2000 | -2000 | -300 | 85 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1696 | -2000 | -2000 | -304 | 85 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1684 | -2000 | -2000 | -316 | 84 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1679 | -2000 | -2000 | -321 | 84 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1678 | -2000 | -2000 | -322 | 84 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1678 | -2000 | -2000 | -322 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1668 | -2000 | -2000 | -332 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1658 | -2000 | -2000 | -342 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1652 | -2000 | -2000 | -348 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -805 | -999 | -999 | -194 | 81 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1599 | 2001 | 2001 | -402 | 80 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1598 | -2000 | -2000 | -402 | 80 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1583 | 2001 | 2001 | -418 | 79 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1582 | -2000 | -2000 | -418 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -973 | -1248 | -1248 | -276 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -971 | -1248 | -1248 | -277 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -968 | -1248 | -1248 | -280 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -963 | -1248 | -1248 | -286 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -961 | -1248 | -1248 | -288 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -956 | -1248 | -1248 | -292 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1492 | 2000 | 2000 | -508 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1468 | 2000 | 2000 | -532 | 73 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1154 | 1600 | 1600 | -446 | 72 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1154 | 1600 | 1600 | -446 | 72 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1148 | 1601 | 1601 | -453 | 72 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1148 | 1601 | 1601 | -453 | 72 | []

## 1830Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3347
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1550 |  | 1570 | -20 | 99 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1550 |  | 1570 | -20 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1542 |  | 1570 | -28 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1488 |  | 1570 | -82 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1459 |  | 1570 | -111 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1570 | -116 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1570 | -118 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1451 |  | 1570 | -119 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1570 | -135 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1764 |  | -2000 | -236 | 88 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1752 |  | -2000 | -248 | 88 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1745 |  | -2000 | -255 | 87 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1736 |  | 2000 | -264 | 87 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1734 |  | -2000 | -266 | 87 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1700 |  | -2000 | -300 | 85 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1696 |  | -2000 | -304 | 85 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1684 |  | -2000 | -316 | 84 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1679 |  | -2000 | -321 | 84 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1678 |  | -2000 | -322 | 84 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1678 |  | -2000 | -322 | 84 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1668 |  | -2000 | -332 | 83 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1658 |  | -2000 | -342 | 83 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1652 |  | -2000 | -348 | 83 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -805 |  | -999 | -194 | 81 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1599 |  | 2001 | -402 | 80 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1598 |  | -2000 | -402 | 80 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [DIR] [BG] | VDOBRU11_XDO_MG11_1:line | -1583 |  | 2001 | -418 | 79 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1582 |  | -2000 | -418 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -973 |  | -1248 | -276 | 78 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -971 |  | -1248 | -277 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -968 |  | -1248 | -280 | 78 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -963 |  | -1248 | -286 | 77 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -961 |  | -1248 | -288 | 77 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -956 |  | -1248 | -292 | 77 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1492 |  | 2000 | -508 | 75 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1468 |  | 2000 | -532 | 73 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1154 |  | 1600 | -446 | 72 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1154 |  | 1600 | -446 | 72 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1148 |  | 1601 | -453 | 72 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1148 |  | 1601 | -453 | 72 | []

## 1930Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3613
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1980 | 2000 | 2000 | -20 | 99 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1948 | -2000 | -2000 | -52 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1496 | 1570 | 1570 | -74 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1496 | 1570 | 1570 | -74 | 95 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1897 | -2000 | -2000 | -103 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1897 | -2000 | -2000 | -103 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1892 | -2000 | -2000 | -108 | 95 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1476 | 1570 | 1570 | -94 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1880 | -2000 | -2000 | -120 | 94 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1861 | -2000 | -2000 | -139 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 | 1570 | 1570 | -114 | 93 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1848 | -2000 | -2000 | -152 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1845 | -2000 | -2000 | -155 | 92 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1845 | -2000 | -2000 | -155 | 92 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1845 | -2000 | -2000 | -155 | 92 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1824 | -2000 | -2000 | -176 | 91 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | -1822 | 2001 | 2001 | -179 | 91 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1821 | -2000 | -2000 | -179 | 91 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1815 | -2000 | -2000 | -185 | 91 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1811 | -2000 | -2000 | -189 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1418 | 1570 | 1570 | -152 | 90 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1805 | 2001 | 2001 | -196 | 90 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1804 | -2000 | -2000 | -196 | 90 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1387 | 1570 | 1570 | -183 | 88 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1384 | 1570 | 1570 | -186 | 88 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1384 | 1570 | 1570 | -186 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1374 | 1570 | 1570 | -196 | 88 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1369 | 1570 | 1570 | -201 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1310 | 1600 | 1600 | -290 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1310 | 1600 | 1600 | -290 | 82 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1633 | 2000 | 2000 | -367 | 82 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1305 | 1601 | 1601 | -296 | 82 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1305 | 1601 | 1601 | -296 | 82 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1606 | 2000 | 2000 | -394 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -991 | -1248 | -1248 | -258 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -990 | -1248 | -1248 | -259 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -986 | -1248 | -1248 | -262 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -982 | -1248 | -1248 | -267 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -979 | -1248 | -1248 | -269 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -975 | -1248 | -1248 | -273 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -763 | -999 | -999 | -236 | 76 | []
RO_CO_00040 | N-1 CernavodÄ - Medgidia Sud | [RO-RO] Medgidia Sud - Rahman [OPP] [RO] | RRAHM41 _RMEDG41 _1:line | 1156 | 1600 | 1600 | -444 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1149 | 1600 | 1600 | -451 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1149 | 1600 | 1600 | -451 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1144 | 1601 | 1601 | -457 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1144 | 1601 | 1601 | -457 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3613
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1980 |  | 2000 | -20 | 99 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1948 |  | -2000 | -52 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1496 |  | 1570 | -74 | 95 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1496 |  | 1570 | -74 | 95 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1897 |  | -2000 | -103 | 95 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1897 |  | -2000 | -103 | 95 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1892 |  | -2000 | -108 | 95 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1476 |  | 1570 | -94 | 94 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1880 |  | -2000 | -120 | 94 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1861 |  | -2000 | -139 | 93 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 |  | 1570 | -114 | 93 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1848 |  | -2000 | -152 | 92 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1845 |  | -2000 | -155 | 92 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1845 |  | -2000 | -155 | 92 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1845 |  | -2000 | -155 | 92 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1824 |  | -2000 | -176 | 91 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | -1822 |  | 2001 | -179 | 91 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1821 |  | -2000 | -179 | 91 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1815 |  | -2000 | -185 | 91 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1811 |  | -2000 | -189 | 91 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1418 |  | 1570 | -152 | 90 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1805 |  | 2001 | -196 | 90 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1804 |  | -2000 | -196 | 90 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1387 |  | 1570 | -183 | 88 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1384 |  | 1570 | -186 | 88 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1384 |  | 1570 | -186 | 88 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1374 |  | 1570 | -196 | 88 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1369 |  | 1570 | -201 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1310 |  | 1600 | -290 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1310 |  | 1600 | -290 | 82 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1633 |  | 2000 | -367 | 82 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1305 |  | 1601 | -296 | 82 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1305 |  | 1601 | -296 | 82 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1606 |  | 2000 | -394 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -991 |  | -1248 | -258 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -990 |  | -1248 | -259 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -986 |  | -1248 | -262 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -982 |  | -1248 | -267 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF212 _3:trf | -979 |  | -1248 | -269 | 78 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -975 |  | -1248 | -273 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -763 |  | -999 | -236 | 76 | []
RO_CO_00040 | N-1 CernavodÄ - Medgidia Sud | [RO-RO] Medgidia Sud - Rahman [OPP] [RO] | RRAHM41 _RMEDG41 _1:line | 1156 |  | 1600 | -444 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1149 |  | 1600 | -451 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1149 |  | 1600 | -451 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1144 |  | 1601 | -457 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [DIR] [BG] | VAECKO11_XKO_TI11_1:line | -1144 |  | 1601 | -457 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3665
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1981 | 2000 | 2000 | -19 | 99 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1945 | -2000 | -2000 | -55 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 | 1570 | 1570 | -43 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 | 1570 | 1570 | -43 | 97 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1492 | 1570 | 1570 | -78 | 95 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1480 | 1570 | 1570 | -90 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1865 | -2000 | -2000 | -135 | 93 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1864 | -2000 | -2000 | -136 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1863 | -2000 | -2000 | -137 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1851 | -2000 | -2000 | -149 | 93 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1840 | -2000 | -2000 | -160 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1442 | 1570 | 1570 | -128 | 92 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1830 | 2001 | 2001 | -171 | 91 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1829 | -2000 | -2000 | -171 | 91 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1824 | -2000 | -2000 | -176 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1823 | -2000 | -2000 | -177 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1822 | -2000 | -2000 | -178 | 91 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1822 | -2000 | -2000 | -178 | 91 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1812 | 2001 | 2001 | -189 | 91 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1811 | -2000 | -2000 | -189 | 91 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1809 | -2000 | -2000 | -191 | 90 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1799 | -2000 | -2000 | -201 | 90 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1410 | 1570 | 1570 | -160 | 90 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1409 | 1570 | 1570 | -161 | 90 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1795 | -2000 | -2000 | -205 | 90 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1408 | 1570 | 1570 | -162 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1397 | 1570 | 1570 | -173 | 89 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1389 | 1570 | 1570 | -181 | 88 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1340 | 1600 | 1600 | -260 | 84 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1340 | 1600 | 1600 | -260 | 84 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1335 | 1601 | 1601 | -266 | 83 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1335 | 1601 | 1601 | -266 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1024 | -1248 | -1248 | -225 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1022 | -1248 | -1248 | -226 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1019 | -1248 | -1248 | -229 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1014 | -1248 | -1248 | -234 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1012 | -1248 | -1248 | -237 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1008 | -1248 | -1248 | -241 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1609 | 2000 | 2000 | -391 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1581 | 2000 | 2000 | -419 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
RO_CO_00040 | N-1 CernavodÄ - Medgidia Sud | [RO-RO] Medgidia Sud - Rahman [OPP] [RO] | RRAHM41 _RMEDG41 _1:line | 1174 | 1600 | 1600 | -426 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1170 | 1601 | 1601 | -431 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1170 | 1601 | 1601 | -431 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -724 | -999 | -999 | -275 | 73 | []

## 2030Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3665
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1981 |  | 2000 | -19 | 99 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1945 |  | -2000 | -55 | 97 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 |  | 1570 | -43 | 97 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1527 |  | 1570 | -43 | 97 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1492 |  | 1570 | -78 | 95 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1480 |  | 1570 | -90 | 94 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1865 |  | -2000 | -135 | 93 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1864 |  | -2000 | -136 | 93 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1863 |  | -2000 | -137 | 93 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1851 |  | -2000 | -149 | 93 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1840 |  | -2000 | -160 | 92 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1442 |  | 1570 | -128 | 92 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1830 |  | 2001 | -171 | 91 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1829 |  | -2000 | -171 | 91 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1824 |  | -2000 | -176 | 91 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1823 |  | -2000 | -177 | 91 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1822 |  | -2000 | -178 | 91 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1822 |  | -2000 | -178 | 91 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1812 |  | 2001 | -189 | 91 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1811 |  | -2000 | -189 | 91 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1809 |  | -2000 | -191 | 90 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1799 |  | -2000 | -201 | 90 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1410 |  | 1570 | -160 | 90 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1409 |  | 1570 | -161 | 90 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | -1795 |  | -2000 | -205 | 90 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1408 |  | 1570 | -162 | 90 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1397 |  | 1570 | -173 | 89 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1389 |  | 1570 | -181 | 88 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1340 |  | 1600 | -260 | 84 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1340 |  | 1600 | -260 | 84 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1335 |  | 1601 | -266 | 83 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1335 |  | 1601 | -266 | 83 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1024 |  | -1248 | -225 | 82 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -1022 |  | -1248 | -226 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1019 |  | -1248 | -229 | 82 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1014 |  | -1248 | -234 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1012 |  | -1248 | -237 | 81 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -1008 |  | -1248 | -241 | 81 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1609 |  | 2000 | -391 | 80 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [OPP] [RO] | RMED141 _RCERN41 _1:line | 1581 |  | 2000 | -419 | 79 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1175 |  | 1600 | -425 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1175 |  | 1600 | -425 | 73 | []
RO_CO_00040 | N-1 CernavodÄ - Medgidia Sud | [RO-RO] Medgidia Sud - Rahman [OPP] [RO] | RRAHM41 _RMEDG41 _1:line | 1174 |  | 1600 | -426 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [DIR] [BG] | VAECKO11_XKO_TI12_1:line | -1170 |  | 1601 | -431 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1170 |  | 1601 | -431 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -724 |  | -999 | -275 | 73 | []

## 2130Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3555
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1545 | 1570 | 1570 | -25 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1534 | 1570 | 1570 | -36 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1494 | 1570 | 1570 | -76 | 95 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1868 | 2000 | 2000 | -132 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1463 | 1570 | 1570 | -107 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 | 1570 | 1570 | -110 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 | 1570 | 1570 | -110 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1446 | 1570 | 1570 | -124 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1838 | -2000 | -2000 | -162 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1443 | 1570 | 1570 | -127 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1791 | -2000 | -2000 | -209 | 90 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1787 | -2000 | -2000 | -213 | 89 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1784 | -2000 | -2000 | -216 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1772 | -2000 | -2000 | -228 | 89 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1756 | -2000 | -2000 | -244 | 88 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1741 | -2000 | -2000 | -259 | 87 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1740 | -2000 | -2000 | -260 | 87 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1739 | -2000 | -2000 | -261 | 87 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1739 | -2000 | -2000 | -261 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1733 | -2000 | -2000 | -267 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1725 | -2000 | -2000 | -275 | 86 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1719 | -2000 | -2000 | -281 | 86 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1716 | -2000 | -2000 | -284 | 86 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1716 | 2001 | 2001 | -285 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1698 | -2000 | -2000 | -302 | 85 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1699 | 2001 | 2001 | -302 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1005 | -1248 | -1248 | -243 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1004 | -1248 | -1248 | -245 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1001 | -1248 | -1248 | -248 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -995 | -1248 | -1248 | -253 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -993 | -1248 | -1248 | -256 | 80 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1268 | 1600 | 1600 | -332 | 79 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1268 | 1600 | 1600 | -332 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -988 | -1248 | -1248 | -260 | 79 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1263 | 1601 | 1601 | -338 | 79 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1263 | 1601 | 1601 | -338 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1537 | 2000 | 2000 | -463 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -766 | -999 | -999 | -234 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1510 | 2000 | 2000 | -490 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1144 | 1600 | 1600 | -456 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1144 | 1600 | 1600 | -456 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1139 | 1601 | 1601 | -462 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1139 | 1601 | 1601 | -462 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3555
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1545 |  | 1570 | -25 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1534 |  | 1570 | -36 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1494 |  | 1570 | -76 | 95 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1868 |  | 2000 | -132 | 93 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1463 |  | 1570 | -107 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 |  | 1570 | -110 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1460 |  | 1570 | -110 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1446 |  | 1570 | -124 | 92 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1838 |  | -2000 | -162 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [DIR] [RO] | RPDFE41 _XPF_DJ11_1:line | 1443 |  | 1570 | -127 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1791 |  | -2000 | -209 | 90 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1787 |  | -2000 | -213 | 89 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1784 |  | -2000 | -216 | 89 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1772 |  | -2000 | -228 | 89 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1756 |  | -2000 | -244 | 88 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1741 |  | -2000 | -259 | 87 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1740 |  | -2000 | -260 | 87 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1739 |  | -2000 | -261 | 87 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1739 |  | -2000 | -261 | 87 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1733 |  | -2000 | -267 | 87 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1725 |  | -2000 | -275 | 86 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1719 |  | -2000 | -281 | 86 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1716 |  | -2000 | -284 | 86 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [OPP] [BG] | VVARNA11_XVA_MG11_1:line | -1716 |  | 2001 | -285 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1698 |  | -2000 | -302 | 85 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1699 |  | 2001 | -302 | 85 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1005 |  | -1248 | -243 | 81 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -1004 |  | -1248 | -245 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -1001 |  | -1248 | -248 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -995 |  | -1248 | -253 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -993 |  | -1248 | -256 | 80 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1268 |  | 1600 | -332 | 79 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1268 |  | 1600 | -332 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [DIR] [RO] | RPDF241 _RPDF222 _2:trf | -988 |  | -1248 | -260 | 79 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1263 |  | 1601 | -338 | 79 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1263 |  | 1601 | -338 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1537 |  | 2000 | -463 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -766 |  | -999 | -234 | 77 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1510 |  | 2000 | -490 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1144 |  | 1600 | -456 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [DIR] [RO] | RTINTB1 _XKO_TI11_1:line | 1144 |  | 1600 | -456 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1139 |  | 1601 | -462 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1139 |  | 1601 | -462 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3591
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1551 | 1570 | 1570 | -19 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1543 | 1570 | 1570 | -27 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1499 | 1570 | 1570 | -71 | 95 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1902 | 2000 | 2000 | -98 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1470 | 1570 | 1570 | -100 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1871 | -2000 | -2000 | -129 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1467 | 1570 | 1570 | -103 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1464 | 1570 | 1570 | -106 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 | 1570 | 1570 | -116 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 | 1570 | 1570 | -125 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1819 | 2000 | 2000 | -181 | 91 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1819 | 2000 | 2000 | -181 | 91 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1812 | 2000 | 2000 | -188 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1802 | 2000 | 2000 | -198 | 90 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1783 | 2000 | 2000 | -217 | 89 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1772 | 2000 | 2000 | -228 | 89 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1770 | 2000 | 2000 | -230 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1769 | 2000 | 2000 | -231 | 88 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1769 | 2000 | 2000 | -231 | 88 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1760 | 2000 | 2000 | -240 | 88 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1751 | 2000 | 2000 | -249 | 88 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | -1748 | 2001 | 2001 | -253 | 87 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1747 | 2000 | 2000 | -253 | 87 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1747 | -2000 | -2000 | -253 | 87 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1730 | 2001 | 2001 | -271 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1729 | -2000 | -2000 | -271 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -840 | -999 | -999 | -159 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1293 | 1600 | 1600 | -307 | 81 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1293 | 1600 | 1600 | -307 | 81 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1288 | 1601 | 1601 | -313 | 80 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1288 | 1601 | 1601 | -313 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -997 | -1248 | -1248 | -252 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -995 | -1248 | -1248 | -253 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -992 | -1248 | -1248 | -256 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -986 | -1248 | -1248 | -262 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -984 | -1248 | -1248 | -264 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -980 | -1248 | -1248 | -268 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1565 | 2000 | 2000 | -435 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1538 | 2000 | 2000 | -462 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1153 | 1601 | 1601 | -448 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1153 | 1601 | 1601 | -448 | 72 | []

## 2230Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3591
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1551 |  | 1570 | -19 | 99 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1543 |  | 1570 | -27 | 98 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1499 |  | 1570 | -71 | 95 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1902 |  | 2000 | -98 | 95 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1470 |  | 1570 | -100 | 94 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | -1871 |  | -2000 | -129 | 94 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1467 |  | 1570 | -103 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1464 |  | 1570 | -106 | 93 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1570 | -116 | 93 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1570 | -125 | 92 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1819 |  | 2000 | -181 | 91 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1819 |  | 2000 | -181 | 91 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1812 |  | 2000 | -188 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1802 |  | 2000 | -198 | 90 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1783 |  | 2000 | -217 | 89 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1772 |  | 2000 | -228 | 89 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1770 |  | 2000 | -230 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1769 |  | 2000 | -231 | 88 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1769 |  | 2000 | -231 | 88 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1760 |  | 2000 | -240 | 88 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1751 |  | 2000 | -249 | 88 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | -1748 |  | 2001 | -253 | 87 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1747 |  | 2000 | -253 | 87 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [OPP] [RO] | RMED141 _XVA_MG11_1:line | -1747 |  | -2000 | -253 | 87 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | -1730 |  | 2001 | -271 | 86 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [OPP] [RO] | RMEDG41 _XDO_MG11_1:line | -1729 |  | -2000 | -271 | 86 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [OPP] [RO] | RARA4D1 _RARAD22 _1:trf | -840 |  | -999 | -159 | 84 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1293 |  | 1600 | -307 | 81 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1293 |  | 1600 | -307 | 81 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1288 |  | 1601 | -313 | 80 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1288 |  | 1601 | -313 | 80 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -997 |  | -1248 | -252 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [OPP] [RO] | RPDFE41 _RPDF222 _1:trf | -995 |  | -1248 | -253 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -992 |  | -1248 | -256 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -986 |  | -1248 | -262 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -984 |  | -1248 | -264 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -980 |  | -1248 | -268 | 78 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1565 |  | 2000 | -435 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1538 |  | 2000 | -462 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1158 |  | 1600 | -442 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [OPP] [RO] | RTINTB1 _XKO_TI12_1:line | 1158 |  | 1600 | -442 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1153 |  | 1601 | -448 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1153 |  | 1601 | -448 | 72 | []

## 2330Preventive
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | PREVENTIVE
TTC [MW]: | 3614
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1543 | 1570 | 1570 | -27 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 | 1570 | 1570 | -35 | 98 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1911 | 2000 | 2000 | -89 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1485 | 1570 | 1570 | -85 | 95 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1873 | 2000 | 2000 | -127 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 | 1570 | 1570 | -114 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1453 | 1570 | 1570 | -117 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 | 1570 | 1570 | -118 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1446 | 1570 | 1570 | -124 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1438 | 1570 | 1570 | -132 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1818 | 2000 | 2000 | -182 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1816 | 2000 | 2000 | -184 | 91 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1812 | 2000 | 2000 | -188 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1804 | 2000 | 2000 | -196 | 90 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1787 | 2000 | 2000 | -213 | 89 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1773 | 2000 | 2000 | -227 | 89 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | 1772 | 2001 | 2001 | -229 | 89 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1771 | 2000 | 2000 | -229 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1770 | -2000 | -2000 | -230 | 89 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1770 | 2000 | 2000 | -230 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1770 | 2000 | 2000 | -230 | 88 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1763 | 2000 | 2000 | -237 | 88 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1754 | 2000 | 2000 | -246 | 88 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | 1753 | 2001 | 2001 | -248 | 88 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1751 | -2000 | -2000 | -249 | 88 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1749 | 2000 | 2000 | -251 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1308 | 1600 | 1600 | -292 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1308 | 1600 | 1600 | -292 | 82 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1305 | 1601 | 1601 | -296 | 82 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1305 | 1601 | 1601 | -296 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -997 | -1248 | -1248 | -252 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -995 | -1248 | -1248 | -253 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -992 | -1248 | -1248 | -256 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -987 | -1248 | -1248 | -261 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -985 | -1248 | -1248 | -264 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -981 | -1248 | -1248 | -268 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1564 | 2000 | 2000 | -436 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1536 | 2000 | 2000 | -464 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -763 | -999 | -999 | -236 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1162 | 1601 | 1601 | -439 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1162 | 1601 | 1601 | -439 | 73 | []

## 2330Curative
Detailed results
Generated at: | 2024-05-09 21:22
Business day: | 11.05.2024
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | 2D
Remedial actions: | true
Evaluation type: | CURATIVE
TTC [MW]: | 3614
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00008 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00009 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO_CO_00001 | N-1 Portile de Fier-Resita | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1543 |  | 1570 | -27 | 98 | []
RO_CO_00029 | N-1 Resita-Timisoara | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1535 |  | 1570 | -35 | 98 | []
RO_CO_00041 | N-1 Medgidia Sud - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1911 |  | 2000 | -89 | 96 | []
RO_CO_00027 | N-1 AT3 Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1485 |  | 1570 | -85 | 95 | []
RO_CO_00011 | N-1 Isaccea - Rahman | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1873 |  | 2000 | -127 | 94 | []
RO_CO_00002 | N-1 Mintia-Arad | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1456 |  | 1570 | -114 | 93 | []
RO-HU_CO_00001 | N-1 Arad-Sandorfalva | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1453 |  | 1570 | -117 | 93 | []
RO-HU_CO_00002 | N-1 Nadab-Bekescsaba | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1570 | -118 | 92 | []
RO-UA_CO_00001 | N-1 Rosiori-Mukacevo | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1446 |  | 1570 | -124 | 92 | []
BC | Base Case | [RO-RS] Portile de Fier-Djerdap [OPP] [RO] | RPDFE41 _XPF_DJ11_1:line | 1438 |  | 1570 | -132 | 92 | []
RO_CO_00012 | N-1 Isaccea - Tulcea Vest | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1818 |  | 2000 | -182 | 91 | []
RO_CO_00013 | N-1 Lacu Sarat - Gura Ialomitei | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1816 |  | 2000 | -184 | 91 | []
RO_CO_00017 | N-1 Constanta Nord- Cernavoda | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1812 |  | 2000 | -188 | 91 | []
RO_CO_00015 | N-1 Tulcea Vest - Tariverde | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1804 |  | 2000 | -196 | 90 | []
RO_CO_00036 | N-1 Medgidia Sud - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1787 |  | 2000 | -213 | 89 | []
RO_CO_00042 | N-1 Isaccea - Vulcanesti | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1773 |  | 2000 | -227 | 89 | []
RO_BG_CO_00004 | N-1 400kV Dobrudja- Medgidia Sud | [BG-RO] Medgidia Sud - Varna [DIR] [BG] | VVARNA11_XVA_MG11_1:line | 1772 |  | 2001 | -229 | 89 | []
RO_CO_00023 | N-1 Gutinas â Smardan | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1771 |  | 2000 | -229 | 89 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-BG] Medgidia Sud - Varna [DIR] [RO] | RMED141 _XVA_MG11_1:line | -1770 |  | -2000 | -230 | 89 | []
BC | Base Case | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1770 |  | 2000 | -230 | 88 | []
RO_CO_00010 | N-1 Isaccea - Stupina | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1770 |  | 2000 | -230 | 88 | []
RO_CO_00018 | N-1 Cernavoda - Pelicanu | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1763 |  | 2000 | -237 | 88 | []
RO_CO_00019 | N-1 Gura Ialomitei - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1754 |  | 2000 | -246 | 88 | []
RO_BG_CO_00003 | N-1 400 kV Medgidia Sud - Varna | [BG-RO] Dobrudja- Medgidia Sud [OPP] [BG] | VDOBRU11_XDO_MG11_1:line | 1753 |  | 2001 | -248 | 88 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-BG] Medgidia Sud - Dobrudja [DIR] [RO] | RMEDG41 _XDO_MG11_1:line | -1751 |  | -2000 | -249 | 88 | []
RO_CO_00037 | N-1 Pelicanu - Bucuresti Sud | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1749 |  | 2000 | -251 | 87 | []
RO-BG_CO_00001 | N-1 Tantareni-Kozlodui 1 | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1308 |  | 1600 | -292 | 82 | []
RO-BG_CO_00002 | N-1 Kozlodui-Tantareni 2 | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1308 |  | 1600 | -292 | 82 | []
RO_BG_CO_00002 | N-1 400kV KOZLODUI-TINTARENI2 | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1305 |  | 1601 | -296 | 82 | []
RO_BG_CO_00001 | N-1 400kV TINTARENI1-KOZLODUI | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1305 |  | 1601 | -296 | 82 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -997 |  | -1248 | -252 | 80 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT1 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF222 _1:trf | -995 |  | -1248 | -253 | 80 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -992 |  | -1248 | -256 | 79 | []
RO_CO_00028 | N-1 AT1 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -987 |  | -1248 | -261 | 79 | []
RO_CO_00034 | N-1 AT2 Portile de Fier | [RO-RO] AT3 Portile de Fier [DIR] [RO] | RPDFE41 _RPDF212 _3:trf | -985 |  | -1248 | -264 | 79 | []
RO_CO_00035 | N-1 AT3 Portile de Fier | [RO-RO] AT2 Portile de Fier [OPP] [RO] | RPDF241 _RPDF222 _2:trf | -981 |  | -1248 | -268 | 79 | []
RO-BG_CO_00005 | N-1 Medgidia Sud-Dobrudja | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1564 |  | 2000 | -436 | 78 | []
RO-BG_CO_00004 | N-1 Medgidia Sud - Varna | [RO-RO] Medgidia Sud- Cernavoda [DIR] [RO] | RMED141 _RCERN41 _1:line | 1536 |  | 2000 | -464 | 77 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-RO] AT3 Arad [DIR] [RO] | RARA4D1 _RARAD22 _1:trf | -763 |  | -999 | -236 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 2 [DIR] [RO] | RTINTB1 _XKO_TI12_1:line | 1165 |  | 1600 | -435 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [RO-BG] Tantareni-Kozlodui 1 [OPP] [RO] | RTINTB1 _XKO_TI11_1:line | 1165 |  | 1600 | -435 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV KOZLODUI-TINTARENI2 [OPP] [BG] | VAECKO11_XKO_TI12_1:line | -1162 |  | 1601 | -439 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 Portile de Fier-Djerdap, N-1 Portile de Fier-Djerdap | [BG-RO] 400kV TINTARENI1-KOZLODUI [OPP] [BG] | VAECKO11_XKO_TI11_1:line | -1162 |  | 1601 | -439 | 73 | []