## 0030
Detailed results
Generated at: | 23/10/2025 20:59:18
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2413.6
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1601 | 1600 | 1 | 100 | 1144 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1403 | 1600 | -197 | 88 | 1005 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1373 | 1600 | -227 | 86 | 984 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1247 | 1600 | -353 | 78 | 889 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1227 | 1600 | -373 | 77 | 862 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1226 | 1600 | -374 | 77 | 862 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 75 | 867 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1196 | 1600 | -404 | 75 | 842 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 838 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1600 | -440 | 72 | 832 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1600 | -446 | 72 | 831 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 826 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 72 | 822 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1139 | 1600 | -461 | 71 | 819 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1125 | 1600 | -475 | 70 | 806 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1124 | 1600 | -476 | 70 | 808 | AC

## 0130
Detailed results
Generated at: | 23/10/2025 20:59:18
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2425.05
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1601 | 1600 | 1 | 100 | 1133 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1399 | 1600 | -201 | 87 | 993 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1600 | -356 | 78 | 876 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1237 | 1600 | -363 | 77 | 863 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1236 | 1600 | -364 | 77 | 862 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 854 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1199 | 1600 | -401 | 75 | 839 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 824 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 818 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 817 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1600 | -458 | 71 | 812 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 808 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1131 | 1600 | -469 | 71 | 805 | AC

## 0230
Detailed results
Generated at: | 23/10/2025 20:59:18
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2491.19
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1594 | 1600 | -6 | 100 | 1128 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1392 | 1600 | -208 | 87 | 988 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1352 | 1600 | -248 | 85 | 962 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 878 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1229 | 1600 | -371 | 77 | 857 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1228 | 1600 | -372 | 77 | 857 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 861 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1189 | 1600 | -411 | 74 | 832 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 819 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 820 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 815 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 72 | 817 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1600 | -467 | 71 | 807 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1600 | -467 | 71 | 807 | AC

## 0330
Detailed results
Generated at: | 23/10/2025 20:59:18
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2543.37
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1602 | 1600 | 2 | 100 | 1135 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1399 | 1600 | -201 | 87 | 994 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1364 | 1600 | -236 | 85 | 970 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1248 | 1600 | -352 | 78 | 880 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1236 | 1600 | -364 | 77 | 863 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1235 | 1600 | -365 | 77 | 862 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1600 | -377 | 76 | 872 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1200 | 1600 | -400 | 75 | 841 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 826 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1156 | 1600 | -444 | 72 | 824 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1600 | -446 | 72 | 821 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1600 | -454 | 72 | 820 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1141 | 1600 | -459 | 71 | 813 | AC

## 0430
Detailed results
Generated at: | 23/10/2025 20:59:18
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2598.16
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1598 | 1600 | -2 | 100 | 1134 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1397 | 1600 | -203 | 87 | 993 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1370 | 1600 | -230 | 86 | 975 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 879 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1600 | -370 | 77 | 877 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1228 | 1600 | -372 | 77 | 858 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1227 | 1600 | -373 | 77 | 858 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1194 | 1600 | -406 | 75 | 837 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 829 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 822 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 821 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 817 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1600 | -458 | 71 | 815 | AC

## 0530
Detailed results
Generated at: | 23/10/2025 20:59:18
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2677.52
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1596 | 1600 | -4 | 100 | 1129 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1391 | 1600 | -209 | 87 | 987 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1370 | 1600 | -230 | 86 | 973 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1252 | 1600 | -348 | 78 | 883 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1600 | -363 | 77 | 880 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1209 | 1600 | -391 | 76 | 844 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1208 | 1600 | -392 | 76 | 843 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 832 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 830 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 828 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 822 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 821 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1151 | 1600 | -449 | 72 | 806 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1138 | 1600 | -462 | 71 | 810 | AC

## 0630
Detailed results
Generated at: | 23/10/2025 20:59:18
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2713.04
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1598 | 1600 | -2 | 100 | 1129 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1396 | 1600 | -204 | 87 | 989 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1382 | 1600 | -218 | 86 | 980 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1270 | 1600 | -330 | 79 | 894 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1600 | -354 | 78 | 885 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 849 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 847 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1185 | 1600 | -415 | 74 | 827 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1184 | 1600 | -416 | 74 | 827 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 836 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 828 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 828 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 72 | 813 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 807 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1134 | 1600 | -466 | 71 | 802 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1129 | 1600 | -471 | 71 | 802 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1127 | 1600 | -473 | 70 | 801 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1124 | 1600 | -476 | 70 | 799 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1600 | -477 | 70 | 798 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1120 | 1600 | -480 | 70 | 796 | AC

## 0730
Detailed results
Generated at: | 23/10/2025 20:59:19
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2700.92
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1599 | 1600 | -1 | 100 | 1126 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1395 | 1600 | -205 | 87 | 985 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1372 | 1600 | -228 | 86 | 971 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1278 | 1600 | -322 | 80 | 897 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1600 | -356 | 78 | 881 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1197 | 1600 | -403 | 75 | 832 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1196 | 1600 | -404 | 75 | 832 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 843 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 841 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 834 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1163 | 1600 | -437 | 73 | 811 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1600 | -439 | 73 | 822 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1600 | -440 | 72 | 821 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1137 | 1600 | -463 | 71 | 805 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1130 | 1600 | -470 | 71 | 797 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1600 | -479 | 70 | 794 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1120 | 1600 | -480 | 70 | 794 | AC

## 0830
Detailed results
Generated at: | 23/10/2025 20:59:19
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2599.81
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1593 | 1600 | -7 | 100 | 1126 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1434 | 1600 | -166 | 90 | 1020 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1356 | 1600 | -244 | 85 | 966 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1241 | 1600 | -359 | 78 | 879 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1600 | -384 | 76 | 867 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1208 | 1600 | -392 | 76 | 863 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1207 | 1600 | -393 | 75 | 858 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1206 | 1600 | -394 | 75 | 858 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 823 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 821 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1600 | -454 | 72 | 816 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1139 | 1600 | -461 | 71 | 815 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 808 | AC

## 0930
Detailed results
Generated at: | 23/10/2025 20:59:19
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2606.61
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1601 | 1600 | 1 | 100 | 1141 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1451 | 1600 | -149 | 91 | 1039 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1388 | 1600 | -212 | 87 | 995 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1278 | 1600 | -322 | 80 | 916 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1235 | 1600 | -365 | 77 | 885 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1235 | 1600 | -365 | 77 | 885 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 872 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 854 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1185 | 1600 | -415 | 74 | 852 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 838 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1159 | 1600 | -441 | 72 | 833 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 827 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1131 | 1600 | -469 | 71 | 812 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1600 | -474 | 70 | 809 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1125 | 1600 | -475 | 70 | 807 | AC

## 1030
Detailed results
Generated at: | 23/10/2025 20:59:19
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2567.44
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1595 | 1600 | -5 | 100 | 1140 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1451 | 1600 | -149 | 91 | 1042 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1397 | 1600 | -203 | 87 | 1003 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1313 | 1600 | -287 | 82 | 943 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1241 | 1600 | -359 | 78 | 891 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1241 | 1600 | -359 | 78 | 891 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1220 | 1600 | -380 | 76 | 878 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 871 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1181 | 1600 | -419 | 74 | 850 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 837 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 840 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 828 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1127 | 1600 | -473 | 70 | 811 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1600 | -478 | 70 | 808 | AC

## 1130
Detailed results
Generated at: | 23/10/2025 20:59:19
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2485.66
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1602 | 1600 | 2 | 100 | 1139 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1459 | 1600 | -141 | 91 | 1043 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1382 | 1600 | -218 | 86 | 989 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1316 | 1600 | -284 | 82 | 941 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1260 | 1600 | -340 | 79 | 900 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1259 | 1600 | -341 | 79 | 899 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1232 | 1600 | -368 | 77 | 882 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 862 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1195 | 1600 | -405 | 75 | 856 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 847 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1600 | -429 | 73 | 840 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 822 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 812 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1600 | -477 | 70 | 805 | AC

## 1230
Detailed results
Generated at: | 23/10/2025 20:59:19
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2578.1
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1603 | 1600 | 3 | 100 | 1140 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1459 | 1600 | -141 | 91 | 1044 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1383 | 1600 | -217 | 86 | 991 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1288 | 1600 | -312 | 81 | 922 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1246 | 1600 | -354 | 78 | 890 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1245 | 1600 | -355 | 78 | 890 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 875 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 861 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1202 | 1600 | -398 | 75 | 862 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 841 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1171 | 1600 | -429 | 73 | 840 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 832 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1136 | 1600 | -464 | 71 | 815 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1600 | -467 | 71 | 813 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1600 | -477 | 70 | 805 | AC

## 1330
Detailed results
Generated at: | 23/10/2025 20:59:19
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2578.1
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1603 | 1600 | 3 | 100 | 1140 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1459 | 1600 | -141 | 91 | 1044 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1383 | 1600 | -217 | 86 | 991 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1288 | 1600 | -312 | 81 | 922 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1246 | 1600 | -354 | 78 | 890 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1245 | 1600 | -355 | 78 | 890 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 875 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 861 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1202 | 1600 | -398 | 75 | 862 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 841 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1171 | 1600 | -429 | 73 | 840 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 832 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 815 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1600 | -467 | 71 | 813 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1600 | -477 | 70 | 805 | AC

## 1430
Detailed results
Generated at: | 23/10/2025 20:59:19
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2725.36
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1597 | 1600 | -3 | 100 | 1135 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1452 | 1600 | -148 | 91 | 1038 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1396 | 1600 | -204 | 87 | 1000 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1269 | 1600 | -331 | 79 | 903 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1600 | -343 | 79 | 902 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 856 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 75 | 856 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 855 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 849 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1171 | 1600 | -429 | 73 | 838 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1170 | 1600 | -430 | 73 | 838 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1165 | 1600 | -435 | 73 | 836 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1600 | -440 | 73 | 833 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 825 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1600 | -467 | 71 | 811 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1125 | 1600 | -475 | 70 | 808 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1600 | -478 | 70 | 806 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1600 | -479 | 70 | 805 | AC

## 1530
Detailed results
Generated at: | 23/10/2025 20:59:19
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2726.9
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1595 | 1600 | -5 | 100 | 1141 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1448 | 1600 | -152 | 90 | 1041 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1415 | 1600 | -185 | 88 | 1019 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1259 | 1600 | -341 | 79 | 908 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1240 | 1600 | -360 | 78 | 890 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 862 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 861 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 861 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 854 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 842 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1152 | 1600 | -448 | 72 | 835 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1600 | -452 | 72 | 828 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1148 | 1600 | -452 | 72 | 830 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI15 1 | 1147 | 1600 | -453 | 72 | 830 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1131 | 1600 | -469 | 71 | 815 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1131 | 1600 | -469 | 71 | 816 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1600 | -474 | 70 | 813 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1600 | -474 | 70 | 813 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1124 | 1600 | -476 | 70 | 811 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1124 | 1600 | -476 | 70 | 811 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1600 | -479 | 70 | 809 | AC

## 1630
Detailed results
Generated at: | 23/10/2025 20:59:19
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2880.27
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1600 | 1600 | 0 | 100 | 1134 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1461 | 1600 | -139 | 91 | 1043 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1412 | 1600 | -188 | 88 | 1007 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1368 | 1600 | -232 | 85 | 972 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1347 | 1600 | -253 | 84 | 964 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1298 | 1600 | -302 | 81 | 927 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1291 | 1600 | -309 | 81 | 925 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1263 | 1600 | -337 | 79 | 904 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1242 | 1600 | -358 | 78 | 889 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 870 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 868 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 861 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 860 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 857 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 854 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1600 | -413 | 74 | 850 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 848 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 847 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 847 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 844 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 844 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 844 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 843 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 843 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 73 | 842 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1600 | -426 | 73 | 841 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 834 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 834 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 833 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 834 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 824 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 824 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 823 | AC

## 1730
Detailed results
Generated at: | 23/10/2025 20:59:19
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2879.19
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1597 | 1600 | -3 | 100 | 1113 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1504 | 1600 | -96 | 94 | 1058 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1496 | 1600 | -104 | 93 | 1048 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1426 | 1600 | -174 | 89 | 1001 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1423 | 1600 | -177 | 89 | 1003 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1392 | 1600 | -208 | 87 | 976 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1382 | 1600 | -218 | 86 | 975 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1328 | 1600 | -272 | 83 | 936 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1310 | 1600 | -290 | 82 | 923 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1307 | 1600 | -293 | 82 | 921 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1283 | 1600 | -317 | 80 | 904 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1272 | 1600 | -328 | 80 | 892 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1263 | 1600 | -337 | 79 | 889 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1256 | 1600 | -344 | 78 | 885 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1255 | 1600 | -345 | 78 | 885 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1600 | -350 | 78 | 881 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1249 | 1600 | -351 | 78 | 880 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1600 | -354 | 78 | 878 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 878 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 878 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1241 | 1600 | -359 | 78 | 874 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1241 | 1600 | -359 | 78 | 874 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1240 | 1600 | -360 | 77 | 874 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 872 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 870 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1600 | -363 | 77 | 871 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1600 | -365 | 77 | 871 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1232 | 1600 | -368 | 77 | 868 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 864 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 860 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 859 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 858 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 858 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 845 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 840 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 820 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 796 | AC

## 1830
Detailed results
Generated at: | 23/10/2025 20:59:20
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2757.59
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1593 | 1600 | -7 | 100 | 1112 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1472 | 1600 | -128 | 92 | 1031 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1439 | 1600 | -161 | 90 | 1001 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1411 | 1600 | -189 | 88 | 986 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1370 | 1600 | -230 | 86 | 961 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1341 | 1600 | -259 | 84 | 937 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1331 | 1600 | -269 | 83 | 935 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1288 | 1600 | -312 | 80 | 903 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1270 | 1600 | -330 | 79 | 891 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1600 | -336 | 79 | 887 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1248 | 1600 | -352 | 78 | 876 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 864 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1600 | -366 | 77 | 865 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 857 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 857 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 857 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 855 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1600 | -383 | 76 | 854 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1600 | -384 | 76 | 853 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 852 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 850 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 849 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 849 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 75 | 847 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 847 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 846 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 843 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 842 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 836 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 834 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1600 | -414 | 74 | 832 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 826 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 827 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 825 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1600 | -439 | 73 | 813 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 788 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1131 | 1600 | -469 | 71 | 792 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1600 | -477 | 70 | 786 | AC

## 1930
Detailed results
Generated at: | 23/10/2025 20:59:20
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2737.06
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1600 | 1600 | 0 | 100 | 1116 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1465 | 1600 | -135 | 92 | 1027 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1430 | 1600 | -170 | 89 | 996 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1412 | 1600 | -188 | 88 | 988 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1357 | 1600 | -243 | 85 | 951 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1325 | 1600 | -275 | 83 | 925 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1315 | 1600 | -285 | 82 | 924 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1279 | 1600 | -321 | 80 | 897 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1600 | -343 | 79 | 882 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1243 | 1600 | -357 | 78 | 873 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 865 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1600 | -370 | 77 | 863 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1600 | -371 | 77 | 858 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 851 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 851 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 850 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 847 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 847 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 846 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 844 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 843 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 843 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 842 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 841 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 840 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 839 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 837 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 833 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 830 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 828 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 825 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 823 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1600 | -426 | 73 | 823 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 805 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1130 | 1600 | -470 | 71 | 792 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1127 | 1600 | -473 | 70 | 789 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1120 | 1600 | -480 | 70 | 780 | AC

## 2030
Detailed results
Generated at: | 23/10/2025 20:59:20
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2756.18
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1596 | 1600 | -4 | 100 | 1114 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1473 | 1600 | -127 | 92 | 1032 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1430 | 1600 | -170 | 89 | 995 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1419 | 1600 | -181 | 89 | 992 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1366 | 1600 | -234 | 85 | 958 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1331 | 1600 | -269 | 83 | 929 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1321 | 1600 | -279 | 83 | 928 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1282 | 1600 | -318 | 80 | 899 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1600 | -334 | 79 | 888 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1600 | -338 | 79 | 885 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1242 | 1600 | -358 | 78 | 871 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1236 | 1600 | -364 | 77 | 867 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1600 | -365 | 77 | 862 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | 860 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 855 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 852 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 852 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 850 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 849 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 848 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 75 | 847 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 847 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 846 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 846 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 845 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 842 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 841 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 837 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 834 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 833 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 826 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 825 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 823 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 811 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 793 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1131 | 1600 | -469 | 71 | 787 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1600 | -479 | 70 | 784 | AC

## 2130
Detailed results
Generated at: | 23/10/2025 20:59:20
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2777.4
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1600 | 1600 | 0 | 100 | 1118 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1458 | 1600 | -142 | 91 | 1023 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1421 | 1600 | -179 | 89 | 995 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1408 | 1600 | -192 | 88 | 981 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1351 | 1600 | -249 | 84 | 948 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1314 | 1600 | -286 | 82 | 919 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1304 | 1600 | -296 | 82 | 917 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1268 | 1600 | -332 | 79 | 889 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1600 | -347 | 78 | 880 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 870 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 864 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 853 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 856 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 855 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 847 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 847 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 844 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 843 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 841 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 840 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 838 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 838 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 838 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 838 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 837 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 834 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1600 | -414 | 74 | 833 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1600 | -414 | 74 | 833 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 829 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 829 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 74 | 825 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 73 | 826 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 819 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 72 | 800 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1125 | 1600 | -475 | 70 | 789 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1600 | -479 | 70 | 782 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1600 | -479 | 70 | 786 | AC

## 2230
Detailed results
Generated at: | 23/10/2025 20:59:20
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2608.27
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1599 | 1600 | -1 | 100 | 1122 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1459 | 1600 | -141 | 91 | 1028 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1426 | 1600 | -174 | 89 | 1003 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1364 | 1600 | -236 | 85 | 955 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1314 | 1600 | -286 | 82 | 927 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1267 | 1600 | -333 | 79 | 891 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 890 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1242 | 1600 | -358 | 78 | 875 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 869 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1600 | -371 | 77 | 867 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 856 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 854 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 846 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 844 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 75 | 841 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 839 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 840 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 839 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 836 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 835 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 835 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 835 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 834 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 833 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 833 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 833 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 831 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 829 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1600 | -426 | 73 | 829 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1600 | -427 | 73 | 828 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1600 | -427 | 73 | 828 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1168 | 1600 | -432 | 73 | 825 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 820 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1600 | -457 | 71 | 806 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1600 | -478 | 70 | 788 | AC

## 2330
Detailed results
Generated at: | 23/10/2025 20:59:20
Business day: | 2025-10-25
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2537.63
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1595 | 1600 | -5 | 100 | 1124 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1436 | 1600 | -164 | 90 | 1015 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1425 | 1600 | -175 | 89 | 1005 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1319 | 1600 | -281 | 82 | 926 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Thessaloniki - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1280 | 1600 | -320 | 80 | 906 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1600 | -375 | 77 | 865 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 863 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1600 | -383 | 76 | 864 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 858 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 851 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 843 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 835 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 830 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 829 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 827 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 827 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 826 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 825 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 825 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1600 | -437 | 73 | 824 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 823 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 822 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1600 | -439 | 73 | 822 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1600 | -440 | 73 | 822 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 821 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 821 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 820 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 821 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 817 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 817 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 816 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 811 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1600 | -460 | 71 | 807 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1600 | -467 | 71 | 802 | AC