## 0030
Detailed results
Generated at: | 06/03/2026 22:40:10
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3492.97
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1842 | 1836 | 6 | 100 | -1282 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1842 | 1836 | 6 | 100 | -1282 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 923 | 960 | -37 | 96 | 372 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1737 | 1836 | -99 | 95 | -1208 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1735 | 1836 | -101 | 95 | -1207 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1735 | 1836 | -101 | 95 | -1207 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1717 | 1836 | -119 | 93 | -1194 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1716 | 1836 | -120 | 93 | -1193 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1713 | 1836 | -123 | 93 | -1192 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1708 | 1836 | -128 | 93 | -1188 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1708 | 1836 | -128 | 93 | -1188 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1624 | 1836 | -212 | 88 | -1128 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1612 | 1836 | -224 | 88 | -1120 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1604 | 1836 | -232 | 87 | -1113 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1593 | 1836 | -243 | 87 | -1104 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1567 | 1890 | -323 | 83 | 1115 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1567 | 1890 | -323 | 83 | 1115 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1567 | 1920 | -353 | 82 | -1087 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1567 | 1920 | -353 | 82 | -1087 | AC

## 0130
Detailed results
Generated at: | 06/03/2026 22:40:10
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3545.77
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1840 | 1836 | 4 | 100 | -1279 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1840 | 1836 | 4 | 100 | -1279 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 939 | 960 | -21 | 98 | 379 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1726 | 1836 | -110 | 94 | -1200 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1721 | 1836 | -115 | 94 | -1195 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1721 | 1836 | -115 | 94 | -1195 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1707 | 1836 | -129 | 93 | -1186 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1706 | 1836 | -130 | 93 | -1185 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1703 | 1836 | -133 | 93 | -1183 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1701 | 1836 | -135 | 93 | -1182 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1697 | 1836 | -139 | 92 | -1179 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1613 | 1836 | -223 | 88 | -1118 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1600 | 1836 | -236 | 87 | -1109 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1595 | 1836 | -241 | 87 | -1106 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1581 | 1836 | -255 | 86 | -1094 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1625 | 1890 | -265 | 86 | 1156 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1625 | 1890 | -265 | 86 | 1156 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1625 | 1920 | -295 | 85 | -1126 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1625 | 1920 | -295 | 85 | -1126 | AC

## 0230
Detailed results
Generated at: | 06/03/2026 22:40:10
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3569.67
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1840 | 1836 | 4 | 100 | -1265 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1840 | 1836 | 4 | 100 | -1265 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 947 | 960 | -13 | 99 | 382 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1723 | 1836 | -113 | 94 | -1183 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1719 | 1836 | -117 | 94 | -1179 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1719 | 1836 | -117 | 94 | -1179 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1704 | 1836 | -132 | 93 | -1169 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1703 | 1836 | -133 | 93 | -1168 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1700 | 1836 | -136 | 93 | -1166 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1699 | 1836 | -137 | 93 | -1166 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1694 | 1836 | -142 | 92 | -1162 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1612 | 1836 | -224 | 88 | -1102 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1650 | 1890 | -240 | 87 | 1174 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1650 | 1890 | -240 | 87 | 1174 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1598 | 1836 | -238 | 87 | -1094 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1594 | 1836 | -242 | 87 | -1090 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1582 | 1836 | -254 | 86 | -1079 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1650 | 1920 | -270 | 86 | -1142 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1650 | 1920 | -270 | 86 | -1142 | AC

## 0330
Detailed results
Generated at: | 06/03/2026 22:40:10
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3806.89
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 983 | 960 | 23 | 102 | 396 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1842 | 1836 | 6 | 100 | -1252 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1842 | 1836 | 6 | 100 | -1252 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1725 | 1836 | -111 | 94 | -1170 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1725 | 1836 | -111 | 94 | -1170 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1720 | 1836 | -116 | 94 | -1167 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1755 | 1890 | -135 | 93 | 1248 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1755 | 1890 | -135 | 93 | 1248 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1699 | 1836 | -137 | 93 | -1152 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1698 | 1836 | -138 | 92 | -1151 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1695 | 1836 | -141 | 92 | -1149 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1693 | 1836 | -143 | 92 | -1147 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1690 | 1836 | -146 | 92 | -1145 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1755 | 1920 | -165 | 91 | -1213 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1755 | 1920 | -165 | 91 | -1213 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1610 | 1836 | -226 | 88 | -1087 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1594 | 1836 | -242 | 87 | -1077 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1583 | 1836 | -253 | 86 | -1068 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1581 | 1836 | -255 | 86 | -1065 | AC

## 0430
Detailed results
Generated at: | 06/03/2026 22:40:10
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3876.49
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 977 | 960 | 17 | 102 | 394 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1824 | 1836 | -12 | 99 | -1237 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1824 | 1836 | -12 | 99 | -1237 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1777 | 1890 | -113 | 94 | 1262 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1777 | 1890 | -113 | 94 | 1262 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1713 | 1836 | -123 | 93 | -1160 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1713 | 1836 | -123 | 93 | -1160 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1703 | 1836 | -133 | 93 | -1153 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1777 | 1920 | -143 | 93 | -1227 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1777 | 1920 | -143 | 93 | -1227 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1682 | 1836 | -154 | 92 | -1138 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1679 | 1836 | -157 | 91 | -1136 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1677 | 1836 | -159 | 91 | -1134 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1674 | 1836 | -162 | 91 | -1132 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1672 | 1836 | -164 | 91 | -1131 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1589 | 1836 | -247 | 87 | -1071 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1578 | 1836 | -258 | 86 | -1064 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1572 | 1836 | -264 | 86 | -1057 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1563 | 1836 | -273 | 85 | -1053 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1327 | 1890 | -563 | 70 | 943 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1327 | 1890 | -563 | 70 | 943 | AC

## 0530
Detailed results
Generated at: | 06/03/2026 22:40:10
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3817.25
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 979 | 960 | 19 | 102 | 395 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1819 | 1836 | -17 | 99 | -1235 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1819 | 1836 | -17 | 99 | -1235 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1712 | 1836 | -124 | 93 | -1161 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1712 | 1836 | -124 | 93 | -1161 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1757 | 1890 | -133 | 93 | 1249 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1757 | 1890 | -133 | 93 | 1249 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1702 | 1836 | -134 | 93 | -1153 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1757 | 1920 | -163 | 92 | -1214 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1757 | 1920 | -163 | 92 | -1214 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1679 | 1836 | -157 | 91 | -1137 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1676 | 1836 | -160 | 91 | -1135 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1671 | 1836 | -165 | 91 | -1131 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1671 | 1836 | -165 | 91 | -1131 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1669 | 1836 | -167 | 91 | -1130 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1586 | 1836 | -250 | 86 | -1070 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1580 | 1836 | -256 | 86 | -1064 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1575 | 1836 | -261 | 86 | -1063 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1559 | 1836 | -277 | 85 | -1052 | AC

## 0630
Detailed results
Generated at: | 06/03/2026 22:40:10
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 4029
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 99 |  | 580 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 55 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 5 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 8 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 5 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 10 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 4 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 8 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 4 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 8 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 7 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 8 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 3 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 6 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 5 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 3 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 9 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 4 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 6 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 14 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 20 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 24 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 18 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 18 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 10 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 48 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 2 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 3 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 2 | 23 |  | 27 | 0 | FALSE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 4 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1829 | 1836 | -7 | 100 | -1260 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1829 | 1836 | -7 | 100 | -1260 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1883 | 1890 | -7 | 100 | 1337 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1883 | 1890 | -7 | 100 | 1337 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1883 | 1920 | -37 | 98 | -1296 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1883 | 1920 | -37 | 98 | -1296 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 940 | 960 | -20 | 98 | 378 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1702 | 1836 | -134 | 93 | -1172 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1702 | 1836 | -134 | 93 | -1172 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1696 | 1836 | -140 | 92 | -1167 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1674 | 1836 | -162 | 91 | -1151 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1673 | 1836 | -163 | 91 | -1150 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1667 | 1836 | -169 | 91 | -1147 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1664 | 1836 | -172 | 91 | -1144 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1657 | 1836 | -179 | 90 | -1139 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1584 | 1836 | -252 | 86 | -1077 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1569 | 1836 | -267 | 85 | -1077 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1565 | 1836 | -271 | 85 | -1072 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1561 | 1836 | -275 | 85 | -1071 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1394 | 1890 | -496 | 74 | 990 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1394 | 1890 | -496 | 74 | 990 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1394 | 1920 | -526 | 73 | -968 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1394 | 1920 | -526 | 73 | -968 | AC

## 0730
Detailed results
Generated at: | 06/03/2026 22:40:10
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3746
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 957 | 960 | -3 | 100 | 386 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1874 | 1890 | -16 | 99 | 1338 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1874 | 1890 | -16 | 99 | 1338 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1874 | 1920 | -46 | 98 | -1298 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1874 | 1920 | -46 | 98 | -1298 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1714 | 1836 | -122 | 93 | -1169 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1714 | 1836 | -122 | 93 | -1169 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1569 | 1836 | -267 | 85 | -1068 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1564 | 1836 | -272 | 85 | -1064 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1564 | 1836 | -272 | 85 | -1064 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1557 | 1836 | -279 | 85 | -1059 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1555 | 1836 | -281 | 85 | -1057 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1553 | 1836 | -283 | 85 | -1056 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1539 | 1836 | -297 | 84 | -1046 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1533 | 1836 | -303 | 83 | -1041 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1460 | 1836 | -376 | 80 | -981 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1449 | 1836 | -387 | 79 | -981 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1836 | -388 | 79 | -980 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1393 | 1836 | -443 | 76 | -937 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1370 | 1890 | -520 | 72 | 978 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1370 | 1890 | -520 | 72 | 978 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1370 | 1920 | -550 | 71 | -957 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1370 | 1920 | -550 | 71 | -957 | AC

## 0830
Detailed results
Generated at: | 06/03/2026 22:40:11
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3685
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 5 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 2 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 0 | 10 |  | 10 | 0 | TRUE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 5 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 8 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 5 | 4 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 10 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 4 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 8 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 4 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 8 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 7 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 9 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 3 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 6 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 5 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 3 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 7 | 1 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 2 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 1 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 7 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 13 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 4 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 4 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 11 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 5 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 44 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 16 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1886 | 1890 | -4 | 100 | 1346 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1886 | 1890 | -4 | 100 | 1346 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1886 | 1920 | -34 | 98 | -1306 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1886 | 1920 | -34 | 98 | -1306 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1722 | 1836 | -114 | 94 | -1176 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1722 | 1836 | -114 | 94 | -1176 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 878 | 960 | -82 | 91 | 354 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1573 | 1836 | -263 | 86 | -1072 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1565 | 1836 | -271 | 85 | -1066 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1563 | 1836 | -273 | 85 | -1064 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1562 | 1836 | -274 | 85 | -1064 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1560 | 1836 | -276 | 85 | -1063 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1560 | 1836 | -276 | 85 | -1063 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1545 | 1836 | -291 | 84 | -1051 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1541 | 1836 | -295 | 84 | -1049 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1836 | -358 | 81 | -996 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1836 | -370 | 80 | -994 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1458 | 1836 | -378 | 79 | -989 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1394 | 1836 | -442 | 76 | -939 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1378 | 1890 | -512 | 73 | 985 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1378 | 1890 | -512 | 73 | 985 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1378 | 1920 | -542 | 72 | -963 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1378 | 1920 | -542 | 72 | -963 | AC

## 0930
Detailed results
Generated at: | 06/03/2026 22:40:11
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3687
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 6 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 2 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 0 | 10 |  | 10 | 0 | TRUE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 5 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 9 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 5 | 32 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 11 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 5 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 9 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 4 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 9 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 8 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 9 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 3 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 7 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 5 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 7 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 3 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 1 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 9 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 16 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 4 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 5 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 12 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 6 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 47 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 11 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 16 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 13 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 7 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 2 |  | 222 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1888 | 1890 | -2 | 100 | 1347 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1888 | 1890 | -2 | 100 | 1347 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1888 | 1920 | -32 | 98 | -1307 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1888 | 1920 | -32 | 98 | -1307 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1716 | 1836 | -120 | 93 | -1179 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1716 | 1836 | -120 | 93 | -1179 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 877 | 960 | -83 | 91 | 352 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1560 | 1836 | -276 | 85 | -1069 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1551 | 1836 | -285 | 84 | -1063 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1550 | 1836 | -286 | 84 | -1062 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1547 | 1836 | -289 | 84 | -1060 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1528 | 1836 | -308 | 83 | -1046 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1522 | 1836 | -314 | 83 | -1042 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1513 | 1836 | -323 | 82 | -1042 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1452 | 1836 | -384 | 79 | -992 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1447 | 1836 | -389 | 79 | -986 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1836 | -418 | 77 | -967 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1401 | 1890 | -489 | 74 | 1000 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1401 | 1890 | -489 | 74 | 1000 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1401 | 1920 | -519 | 73 | -978 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1401 | 1920 | -519 | 73 | -978 | AC

## 1030
Detailed results
Generated at: | 06/03/2026 22:40:11
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3878
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 6 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 2 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 2 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 3 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 2 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 4 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 2 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 3 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 2 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 3 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 3 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 3 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 1 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 6 | 15 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 5 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 3 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 7 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 7 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 7 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 7 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 7 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 2 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 1 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 9 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 16 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 4 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 4 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 12 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 5 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 44 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 17 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 7 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1345 | AC no reactive limits
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1345 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1885 | 1920 | -35 | 98 | -1304 | AC no reactive limits
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1885 | 1920 | -35 | 98 | -1304 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1736 | 1836 | -100 | 95 | -1183 | AC no reactive limits
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1736 | 1836 | -100 | 95 | -1183 | AC no reactive limits
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 871 | 960 | -89 | 91 | 351 | AC no reactive limits
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1606 | 1836 | -230 | 87 | -1089 | AC no reactive limits
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1595 | 1836 | -241 | 87 | -1080 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1595 | 1836 | -241 | 87 | -1088 | AC no reactive limits
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1595 | 1836 | -241 | 87 | -1088 | AC no reactive limits
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1588 | 1836 | -248 | 86 | -1077 | AC no reactive limits
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1587 | 1836 | -249 | 86 | -1074 | AC no reactive limits
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1583 | 1836 | -253 | 86 | -1071 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1579 | 1836 | -257 | 86 | -1068 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1836 | -331 | 82 | -1014 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1489 | 1836 | -347 | 81 | -1005 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1489 | 1836 | -347 | 81 | -1001 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1442 | 1836 | -394 | 79 | -967 | AC no reactive limits
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1379 | 1890 | -511 | 73 | 985 | AC no reactive limits
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1379 | 1890 | -511 | 73 | 985 | AC no reactive limits
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1379 | 1920 | -541 | 72 | -963 | AC no reactive limits
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1379 | 1920 | -541 | 72 | -963 | AC no reactive limits

## 1130
Detailed results
Generated at: | 06/03/2026 22:40:11
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3852
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 6 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 2 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 0 | 10 |  | 10 | 0 | TRUE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 4 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 2 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 3 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 2 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 4 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 2 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 3 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 2 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 3 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 3 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 3 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 1 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 6 | 49 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 5 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 3 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 6 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 6 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 6 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 6 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 6 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 2 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 1 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 9 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 15 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 4 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 4 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 11 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 5 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 42 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 16 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 50 |  | 96 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1833 | 1836 | -3 | 100 | -1259 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1833 | 1836 | -3 | 100 | -1259 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1735 | 1836 | -101 | 95 | -1192 | AC no reactive limits
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1735 | 1836 | -101 | 95 | -1192 | AC no reactive limits
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1733 | 1836 | -103 | 94 | -1186 | AC no reactive limits
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1724 | 1836 | -112 | 94 | -1179 | AC no reactive limits
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1721 | 1836 | -115 | 94 | -1177 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1712 | 1836 | -124 | 93 | -1170 | AC no reactive limits
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1711 | 1836 | -125 | 93 | -1170 | AC no reactive limits
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1694 | 1836 | -142 | 92 | -1156 | AC no reactive limits
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1223 | AC no reactive limits
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1223 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1650 | 1836 | -186 | 90 | -1122 | AC no reactive limits
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1712 | 1920 | -208 | 89 | -1190 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1712 | 1920 | -208 | 89 | -1190 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1629 | 1836 | -207 | 89 | -1110 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1613 | 1836 | -223 | 88 | -1098 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1604 | 1836 | -232 | 87 | -1089 | AC no reactive limits
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 724 | 960 | -236 | 75 | 293 | AC no reactive limits

## 1230
Detailed results
Generated at: | 06/03/2026 22:40:11
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3624.87
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1796 | 1836 | -40 | 98 | -1220 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1796 | 1836 | -40 | 98 | -1220 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1727 | 1836 | -109 | 94 | -1171 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1727 | 1836 | -109 | 94 | -1171 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1715 | 1836 | -121 | 93 | -1162 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1706 | 1836 | -130 | 93 | -1156 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1705 | 1836 | -131 | 93 | -1155 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1697 | 1836 | -139 | 92 | -1150 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1690 | 1836 | -146 | 92 | -1145 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1666 | 1836 | -170 | 91 | -1127 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1616 | 1836 | -220 | 88 | -1092 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1614 | 1836 | -222 | 88 | -1091 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1608 | 1836 | -228 | 88 | -1083 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1597 | 1836 | -239 | 87 | -1078 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1544 | 1890 | -346 | 82 | 1104 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1544 | 1890 | -346 | 82 | 1104 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1544 | 1920 | -376 | 80 | -1077 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1544 | 1920 | -376 | 80 | -1077 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 720 | 999 | -279 | 72 | 273 | AC

## 1330
Detailed results
Generated at: | 06/03/2026 22:40:11
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3664.71
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1706 | 1836 | -130 | 93 | -1167 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1706 | 1836 | -130 | 93 | -1167 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1620 | 1836 | -216 | 88 | -1106 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1620 | 1836 | -216 | 88 | -1106 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1663 | 1890 | -227 | 88 | 1189 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1663 | 1890 | -227 | 88 | 1189 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1609 | 1836 | -227 | 88 | -1099 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1599 | 1836 | -237 | 87 | -1091 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1594 | 1836 | -242 | 87 | -1087 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1663 | 1920 | -257 | 87 | -1157 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1663 | 1920 | -257 | 87 | -1157 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1585 | 1836 | -251 | 86 | -1081 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1579 | 1836 | -257 | 86 | -1077 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1565 | 1836 | -271 | 85 | -1067 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1527 | 1836 | -309 | 83 | -1027 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1504 | 1836 | -332 | 82 | -1024 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1486 | 1836 | -350 | 81 | -1011 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1483 | 1836 | -353 | 81 | -1005 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 709 | 960 | -251 | 74 | 287 | AC

## 1430
Detailed results
Generated at: | 06/03/2026 22:40:11
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3866
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 5 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 2 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 5 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 7 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 5 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 10 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 4 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 8 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 4 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 8 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 7 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 8 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 3 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 6 | 47 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 5 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 3 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 7 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 7 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 7 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 7 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 7 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 2 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 1 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 7 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 12 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 4 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 4 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 12 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 5 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 44 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 16 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1884 | 1890 | -6 | 100 | 1345 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1884 | 1890 | -6 | 100 | 1345 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1884 | 1920 | -36 | 98 | -1305 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1884 | 1920 | -36 | 98 | -1305 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1582 | 1836 | -254 | 86 | -1073 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1582 | 1836 | -254 | 86 | -1073 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 826 | 960 | -134 | 86 | 334 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1463 | 1836 | -373 | 80 | -991 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1463 | 1836 | -373 | 80 | -991 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1458 | 1836 | -378 | 79 | -986 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1446 | 1836 | -390 | 79 | -978 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1437 | 1836 | -399 | 78 | -971 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1435 | 1836 | -401 | 78 | -970 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1421 | 1836 | -415 | 77 | -960 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1420 | 1836 | -416 | 77 | -959 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1836 | -475 | 74 | -903 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1343 | 1836 | -493 | 73 | -904 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1330 | 1836 | -506 | 72 | -894 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1356 | 1890 | -534 | 72 | 969 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1356 | 1890 | -534 | 72 | 969 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1311 | 1836 | -525 | 71 | -877 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1356 | 1920 | -564 | 71 | -948 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1356 | 1920 | -564 | 71 | -948 | AC

## 1530
Detailed results
Generated at: | 06/03/2026 22:40:11
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3678
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 22 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 50 | 53 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 3 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 2 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 4 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 9 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 16 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 10 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 20 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 8 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 16 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 8 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 16 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 15 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 17 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 6 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 12 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 9 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 6 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 13 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 13 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 13 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 13 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 13 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 2 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 1 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 7 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 4 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 4 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 11 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 5 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 43 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 15 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 4 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1887 | 1890 | -3 | 100 | 1346 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1887 | 1890 | -3 | 100 | 1346 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1887 | 1920 | -33 | 98 | -1305 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1887 | 1920 | -33 | 98 | -1305 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 867 | 960 | -93 | 90 | 350 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1489 | 1836 | -347 | 81 | -999 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1489 | 1836 | -347 | 81 | -999 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1836 | -475 | 74 | -910 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1836 | -484 | 74 | -905 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1836 | -484 | 74 | -905 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1345 | 1836 | -491 | 73 | -898 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1339 | 1836 | -497 | 73 | -894 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1335 | 1836 | -501 | 73 | -890 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1330 | 1836 | -506 | 72 | -887 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1321 | 1836 | -515 | 72 | -880 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1342 | 1890 | -548 | 71 | 958 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1342 | 1890 | -548 | 71 | 958 | AC

## 1630
Detailed results
Generated at: | 06/03/2026 22:40:11
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3441
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 308 |  | 580 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 51 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 15 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 24 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 15 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 31 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 12 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 25 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 12 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 25 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 23 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 26 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 9 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 25 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 19 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 13 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 26 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 26 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 26 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 26 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 26 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 6 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 6 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 15 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 20 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 24 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 18 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 19 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 10 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 46 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 60 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 25 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1831 | 1836 | -5 | 100 | -1270 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1831 | 1836 | -5 | 100 | -1270 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1737 | 1836 | -99 | 95 | -1202 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1717 | 1836 | -119 | 94 | -1193 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1717 | 1836 | -119 | 94 | -1193 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1717 | 1836 | -119 | 94 | -1188 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1708 | 1836 | -128 | 93 | -1182 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1705 | 1836 | -131 | 93 | -1179 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1701 | 1836 | -135 | 93 | -1177 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1686 | 1836 | -150 | 92 | -1166 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 870 | 960 | -90 | 91 | 351 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1654 | 1836 | -182 | 90 | -1141 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1606 | 1836 | -230 | 87 | -1102 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1603 | 1836 | -233 | 87 | -1106 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1600 | 1836 | -236 | 87 | -1105 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1552 | 1890 | -338 | 82 | 1108 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1552 | 1890 | -338 | 82 | 1108 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1552 | 1920 | -368 | 81 | -1080 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1552 | 1920 | -368 | 81 | -1080 | AC

## 1730
Detailed results
Generated at: | 06/03/2026 22:40:12
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3613
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1838 | 1836 | 2 | 100 | -1245 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1838 | 1836 | 2 | 100 | -1245 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1727 | 1836 | -109 | 94 | -1166 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1716 | 1836 | -120 | 93 | -1159 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1716 | 1836 | -120 | 93 | -1159 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1703 | 1836 | -133 | 93 | -1149 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1702 | 1836 | -134 | 93 | -1148 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1696 | 1836 | -140 | 92 | -1144 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1691 | 1836 | -145 | 92 | -1141 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1672 | 1836 | -164 | 91 | -1127 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1694 | 1890 | -196 | 90 | 1209 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1694 | 1890 | -196 | 90 | 1209 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1694 | 1920 | -226 | 88 | -1177 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1694 | 1920 | -226 | 88 | -1177 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1593 | 1836 | -243 | 87 | -1070 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1592 | 1836 | -244 | 87 | -1056 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1588 | 1836 | -248 | 86 | -1066 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1586 | 1836 | -250 | 86 | -1061 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1541 | 2000 | -459 | 77 | 1077 | AC

## 1830
Detailed results
Generated at: | 06/03/2026 22:40:12
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3660.45
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1837 | 1836 | 1 | 100 | -1231 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1837 | 1836 | 1 | 100 | -1231 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1723 | 1836 | -113 | 94 | -1150 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1710 | 1836 | -126 | 93 | -1141 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1710 | 1836 | -126 | 93 | -1141 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1699 | 1836 | -137 | 93 | -1133 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1697 | 1836 | -139 | 92 | -1131 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1693 | 1836 | -143 | 92 | -1128 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1687 | 1836 | -149 | 92 | -1124 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1729 | 1890 | -161 | 91 | 1234 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1729 | 1890 | -161 | 91 | 1234 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1670 | 1836 | -166 | 91 | -1111 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1729 | 1920 | -191 | 90 | -1200 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1729 | 1920 | -191 | 90 | -1200 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1594 | 1836 | -242 | 87 | -1041 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1580 | 1836 | -256 | 86 | -1042 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1579 | 1836 | -257 | 86 | -1045 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1576 | 1836 | -260 | 86 | -1044 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1528 | 2000 | -472 | 76 | 1070 | AC

## 1930
Detailed results
Generated at: | 06/03/2026 22:40:12
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3554.42
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1853 | 1836 | 17 | 101 | -1233 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1853 | 1836 | 17 | 101 | -1233 | AC no reactive limits
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1754 | 1836 | -82 | 96 | -1160 | AC no reactive limits
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1733 | 1836 | -103 | 94 | -1143 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1727 | 1836 | -109 | 94 | -1150 | AC no reactive limits
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1727 | 1836 | -109 | 94 | -1150 | AC no reactive limits
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1726 | 1836 | -110 | 94 | -1140 | AC no reactive limits
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1724 | 1836 | -112 | 94 | -1136 | AC no reactive limits
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1723 | 1836 | -113 | 94 | -1135 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1711 | 1836 | -125 | 93 | -1126 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1625 | 1836 | -211 | 89 | -1061 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1611 | 1836 | -225 | 88 | -1052 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1608 | 1836 | -228 | 88 | -1050 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1603 | 1836 | -233 | 87 | -1051 | AC no reactive limits
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1632 | 1890 | -258 | 86 | 1165 | AC no reactive limits
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1632 | 1890 | -258 | 86 | 1165 | AC no reactive limits
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1632 | 1920 | -288 | 85 | -1135 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1632 | 1920 | -288 | 85 | -1135 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1532 | 2000 | -468 | 77 | 1076 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c2 | RRESI22 RTIMI22 2 | 672 | 960 | -288 | 70 | 268 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 672 | 960 | -288 | 70 | 268 | AC no reactive limits

## 2030
Detailed results
Generated at: | 06/03/2026 22:40:12
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3286.26
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1843 | 1836 | 7 | 100 | -1250 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1843 | 1836 | 7 | 100 | -1250 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1759 | 1836 | -77 | 96 | -1190 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1750 | 1836 | -86 | 95 | -1184 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1750 | 1836 | -86 | 95 | -1184 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1738 | 1836 | -98 | 95 | -1174 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1732 | 1836 | -104 | 94 | -1171 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1729 | 1836 | -107 | 94 | -1168 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1724 | 1836 | -112 | 94 | -1165 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1717 | 1836 | -119 | 94 | -1160 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1664 | 1836 | -172 | 91 | -1118 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1634 | 1836 | -202 | 89 | -1085 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1623 | 1836 | -213 | 88 | -1092 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1619 | 1836 | -217 | 88 | -1088 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1428 | 1890 | -462 | 76 | 1019 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1428 | 1890 | -462 | 76 | 1019 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1428 | 1920 | -492 | 74 | -996 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1428 | 1920 | -492 | 74 | -996 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1429 | 2000 | -571 | 71 | 1005 | AC

## 2130
Detailed results
Generated at: | 06/03/2026 22:40:12
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 2936
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00105 | RO | RROVI31 _generator | 0 | 310 |  |  | 34 | 310 |  | 310 | 1 | FALSE | FALSE
RO_RA_00107 | RO | RTURC11 _generator | 0 | 302 |  |  | 34 | 302 |  | 302 | 1 | FALSE | FALSE
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 48 | 110 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 47 | 313 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 44 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 96 | 171 |  | 580 | 0 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 60 | 0 |  | 389 | 0 | FALSE | TRUE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 55 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 3 | 0 |  | 170 | 0 | FALSE | TRUE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 8 | 0 |  | 340 | 0 | FALSE | TRUE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 9 | 0 |  | 118 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 15 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 24 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 15 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 32 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 12 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 25 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 13 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 25 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 23 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 26 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 9 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 28 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 21 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 14 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 29 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 29 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 29 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 29 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 29 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 12 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 20 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 24 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 18 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 19 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 9 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 48 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 12 | 0 |  | 150 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 2 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 7 | 0 |  | 96 | 0 | FALSE | TRUE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 5 | 0 |  | 58 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1836 | 1836 | 0 | 100 | -1145 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1836 | 1836 | 0 | 100 | -1145 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1764 | 1836 | -72 | 96 | -1092 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1741 | 1836 | -95 | 95 | -1074 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1733 | 1836 | -103 | 94 | -1068 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1732 | 1836 | -104 | 94 | -1067 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1729 | 1836 | -107 | 94 | -1108 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1726 | 1836 | -110 | 94 | -1071 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1724 | 1836 | -112 | 94 | -1061 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1662 | 1836 | -174 | 91 | -1007 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1639 | 1836 | -197 | 89 | -981 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1632 | 1836 | -204 | 89 | -992 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1594 | 1836 | -242 | 87 | -959 | AC

## 2230
Detailed results
Generated at: | 06/03/2026 22:40:12
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3132
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 580 |  | 580 | 0 | TRUE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 38 |  | 389 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 52 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 0 | 156 |  | 170 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 15 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 25 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 15 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 32 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 12 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 25 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 13 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 25 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 23 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 27 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 9 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 19 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 13 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 20 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 24 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 18 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 19 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 9 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 49 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 11 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 2 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1831 | 1836 | -5 | 100 | -1125 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1831 | 1836 | -5 | 100 | -1125 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1750 | 1836 | -86 | 95 | -1060 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1732 | 1836 | -104 | 94 | -1045 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1727 | 1836 | -109 | 94 | -1041 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1725 | 1836 | -111 | 94 | -1040 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1723 | 1836 | -113 | 94 | -1041 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1720 | 1836 | -116 | 94 | -1036 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1715 | 1836 | -121 | 93 | -1051 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1715 | 1836 | -121 | 93 | -1051 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1668 | 1836 | -168 | 91 | -990 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1632 | 1836 | -204 | 89 | -967 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1615 | 1836 | -221 | 88 | -958 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1591 | 1836 | -245 | 87 | -944 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1442 | 1890 | -448 | 76 | 1024 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1442 | 1890 | -448 | 76 | 1024 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1442 | 1920 | -478 | 75 | -1001 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1442 | 1920 | -478 | 75 | -1001 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1394 | 1920 | -526 | 73 | 958 | AC

## 2330
Detailed results
Generated at: | 06/03/2026 22:40:12
Business day: | 2026-03-08
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3065
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 397 |  | 580 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 52 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 28 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 25 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 19 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 13 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 11 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 17 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 20 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 24 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 18 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 19 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 9 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 46 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 13 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 2 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 8 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 957 | 960 | -3 | 100 | 385 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1738 | 1836 | -98 | 95 | -1051 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1738 | 1836 | -98 | 95 | -1051 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1647 | 1836 | -189 | 90 | -981 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1630 | 1836 | -206 | 89 | -967 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1629 | 1836 | -207 | 89 | -966 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1628 | 1836 | -208 | 89 | -966 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1626 | 1836 | -210 | 89 | -964 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1624 | 1836 | -212 | 88 | -974 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1624 | 1836 | -212 | 88 | -974 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1621 | 1836 | -215 | 88 | -960 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1562 | 1836 | -274 | 85 | -906 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1551 | 1836 | -285 | 84 | -903 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1533 | 1836 | -303 | 84 | -889 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1510 | 1836 | -326 | 82 | -873 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1450 | 1890 | -440 | 77 | 1031 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1450 | 1890 | -440 | 77 | 1031 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1450 | 1920 | -470 | 76 | -1007 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1450 | 1920 | -470 | 76 | -1007 | AC