## 0030
Detailed results
Generated at: | 08/03/2026 22:45:55
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3552.91
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1999 | 2000 | -1 | 100 | 1416 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1974 | 2000 | -26 | 99 | 1399 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1966 | 2000 | -34 | 98 | 1394 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1941 | 2000 | -59 | 97 | 1377 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1849 | 2000 | -151 | 92 | 1312 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1830 | 2000 | -170 | 92 | 1298 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1803 | 2000 | -197 | 90 | 1269 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1789 | 2000 | -211 | 89 | 1270 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1778 | 2000 | -222 | 89 | 1254 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1769 | 2000 | -231 | 88 | 1254 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1769 | 2000 | -231 | 88 | 1254 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1767 | 2000 | -233 | 88 | 1251 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1766 | 2000 | -234 | 88 | 1252 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1748 | 2000 | -252 | 87 | 1229 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 844 | 999 | -155 | 84 | 316 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1542 | 1836 | -294 | 84 | 1091 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1665 | 2000 | -335 | 83 | 1173 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1658 | 2000 | -342 | 83 | 1169 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1490 | 1836 | -346 | 81 | 1054 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1488 | 1836 | -348 | 81 | 1054 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1480 | 1836 | -356 | 81 | 1046 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1472 | 1836 | -364 | 80 | 1040 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1472 | 1836 | -364 | 80 | 1040 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1456 | 1836 | -380 | 79 | 1030 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1836 | -388 | 79 | 1024 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1437 | 1836 | -399 | 78 | 1016 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1433 | 1836 | -403 | 78 | 1014 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1428 | 1836 | -408 | 78 | 1010 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1427 | 1836 | -409 | 78 | 1009 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1836 | -441 | 76 | 986 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1496 | 2000 | -504 | 75 | 1045 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1496 | 2000 | -504 | 75 | -1025 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 906 | 1248 | -343 | 73 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 906 | 1248 | -343 | 73 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 900 | 1248 | -348 | 72 | 368 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 897 | 1248 | -351 | 72 | 367 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 897 | 1248 | -351 | 72 | 367 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 895 | 1248 | -354 | 72 | 366 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 895 | 1248 | -354 | 72 | 366 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 892 | 1248 | -357 | 71 | 364 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 892 | 1248 | -357 | 71 | 364 | AC

## 0130
Detailed results
Generated at: | 08/03/2026 22:45:55
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3543.51
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1995 | 2000 | -5 | 100 | 1413 | AC no reactive limits
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1975 | 2000 | -25 | 99 | 1399 | AC no reactive limits
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1972 | 2000 | -28 | 99 | 1398 | AC no reactive limits
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1957 | 2000 | -43 | 98 | 1388 | AC no reactive limits
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1855 | 2000 | -145 | 93 | 1315 | AC no reactive limits
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1835 | 2000 | -165 | 92 | 1301 | AC no reactive limits
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1805 | 2000 | -195 | 90 | 1270 | AC no reactive limits
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1790 | 2000 | -210 | 89 | 1270 | AC no reactive limits
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1782 | 2000 | -218 | 89 | 1257 | AC no reactive limits
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1774 | 2000 | -226 | 89 | 1257 | AC no reactive limits
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1770 | 2000 | -230 | 89 | 1254 | AC no reactive limits
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1768 | 2000 | -232 | 88 | 1252 | AC no reactive limits
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1767 | 2000 | -233 | 88 | 1252 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1752 | 2000 | -248 | 88 | 1233 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 849 | 999 | -150 | 85 | 318 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1537 | 1836 | -299 | 84 | 1087 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1671 | 2000 | -329 | 84 | 1177 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1665 | 2000 | -335 | 83 | 1173 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1487 | 1836 | -349 | 81 | 1051 | AC no reactive limits
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1487 | 1836 | -349 | 81 | 1051 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1836 | -351 | 81 | 1051 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1469 | 1836 | -367 | 80 | 1037 | AC no reactive limits
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1469 | 1836 | -367 | 80 | 1037 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1467 | 1836 | -369 | 80 | 1036 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1458 | 1836 | -378 | 79 | 1026 | AC no reactive limits
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1444 | 1836 | -392 | 79 | 1020 | AC no reactive limits
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1435 | 1836 | -401 | 78 | 1010 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1435 | 1836 | -401 | 78 | 1012 | AC no reactive limits
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1427 | 1836 | -409 | 78 | 1006 | AC no reactive limits
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1425 | 1836 | -411 | 78 | 1005 | AC no reactive limits
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1394 | 1836 | -442 | 76 | 982 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1491 | 2000 | -509 | 75 | 1040 | AC no reactive limits
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1491 | 2000 | -509 | 75 | -1023 | AC no reactive limits
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1480 | 2000 | -520 | 74 | -1015 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1480 | 2000 | -520 | 74 | 1034 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 905 | 1248 | -343 | 72 | 370 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 905 | 1248 | -343 | 72 | 370 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 899 | 1248 | -349 | 72 | 368 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 898 | 1248 | -351 | 72 | 367 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 898 | 1248 | -351 | 72 | 367 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 895 | 1248 | -353 | 72 | 366 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 895 | 1248 | -353 | 72 | 366 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 892 | 1248 | -356 | 71 | 365 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 892 | 1248 | -356 | 71 | 365 | AC no reactive limits

## 0230
Detailed results
Generated at: | 08/03/2026 22:45:55
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3541.56
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 2001 | 2000 | 1 | 100 | 1417 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1983 | 2000 | -17 | 99 | 1405 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1980 | 2000 | -20 | 99 | 1404 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1966 | 2000 | -34 | 98 | 1395 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1860 | 2000 | -140 | 93 | 1320 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1840 | 2000 | -160 | 92 | 1305 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1804 | 2000 | -196 | 90 | 1270 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1789 | 2000 | -211 | 89 | 1271 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1782 | 2000 | -218 | 89 | 1257 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1775 | 2000 | -225 | 89 | 1258 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1772 | 2000 | -228 | 89 | 1256 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1770 | 2000 | -230 | 88 | 1254 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1769 | 2000 | -231 | 88 | 1254 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 880 | 999 | -119 | 88 | 330 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1754 | 2000 | -246 | 88 | 1234 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1544 | 1836 | -292 | 84 | 1085 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1678 | 2000 | -322 | 84 | 1183 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1671 | 2000 | -329 | 84 | 1179 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1836 | -342 | 81 | 1049 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1836 | -342 | 81 | 1049 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1491 | 1836 | -345 | 81 | 1049 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1473 | 1836 | -363 | 80 | 1033 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1473 | 1836 | -363 | 80 | 1033 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1473 | 1836 | -363 | 80 | 1033 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1459 | 1836 | -377 | 79 | 1024 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1451 | 1836 | -385 | 79 | 1018 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1444 | 1836 | -392 | 79 | 1013 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1436 | 1836 | -400 | 78 | 1008 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1431 | 1836 | -405 | 78 | 1004 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1429 | 1836 | -407 | 78 | 1002 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1396 | 1836 | -440 | 76 | 979 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1475 | 2000 | -525 | 74 | 1028 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1475 | 2000 | -525 | 74 | -1012 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1464 | 2000 | -536 | 73 | -1004 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1464 | 2000 | -536 | 73 | 1023 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 908 | 1248 | -340 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 908 | 1248 | -340 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 902 | 1248 | -346 | 72 | 368 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 892 | 1248 | -357 | 71 | 364 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 892 | 1248 | -357 | 71 | 364 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 889 | 1248 | -359 | 71 | 363 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 889 | 1248 | -359 | 71 | 363 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 886 | 1248 | -362 | 71 | 362 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 886 | 1248 | -362 | 71 | 362 | AC

## 0330
Detailed results
Generated at: | 08/03/2026 22:45:55
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3523.83
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 2000 | 2000 | 0 | 100 | 1416 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1982 | 2000 | -18 | 99 | 1405 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1980 | 2000 | -20 | 99 | 1405 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1969 | 2000 | -31 | 98 | 1397 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1857 | 2000 | -143 | 93 | 1318 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1837 | 2000 | -163 | 92 | 1303 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1794 | 2000 | -206 | 90 | 1263 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1779 | 2000 | -221 | 89 | 1264 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1773 | 2000 | -227 | 89 | 1251 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1767 | 2000 | -233 | 88 | 1252 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1766 | 2000 | -234 | 88 | 1252 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1764 | 2000 | -236 | 88 | 1250 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1763 | 2000 | -237 | 88 | 1250 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 878 | 999 | -121 | 88 | 329 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1747 | 2000 | -253 | 87 | 1229 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1564 | 1836 | -272 | 85 | 1090 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1678 | 2000 | -322 | 84 | 1183 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1671 | 2000 | -329 | 84 | 1179 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1514 | 1836 | -322 | 82 | 1054 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1514 | 1836 | -322 | 82 | 1054 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1513 | 1836 | -323 | 82 | 1056 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1495 | 1836 | -341 | 81 | 1039 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1493 | 1836 | -343 | 81 | 1038 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1493 | 1836 | -343 | 81 | 1038 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1480 | 1836 | -356 | 81 | 1029 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1472 | 1836 | -364 | 80 | 1023 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1464 | 1836 | -372 | 80 | 1017 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1457 | 1836 | -379 | 79 | 1013 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1452 | 1836 | -384 | 79 | 1009 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1450 | 1836 | -386 | 79 | 1007 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1417 | 1836 | -419 | 77 | 984 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 909 | 1248 | -339 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 909 | 1248 | -339 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 903 | 1248 | -345 | 72 | 368 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1447 | 2000 | -553 | 72 | 1009 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1447 | 2000 | -553 | 72 | -994 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1437 | 2000 | -563 | 72 | -986 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1437 | 2000 | -563 | 72 | 1004 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 891 | 1248 | -358 | 71 | 363 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 891 | 1248 | -358 | 71 | 363 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 888 | 1248 | -360 | 71 | 362 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 888 | 1248 | -360 | 71 | 362 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 885 | 1248 | -363 | 71 | 361 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 885 | 1248 | -363 | 71 | 361 | AC

## 0430
Detailed results
Generated at: | 08/03/2026 22:45:55
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3524.77
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1997 | 2000 | -3 | 100 | 1414 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1980 | 2000 | -20 | 99 | 1403 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1978 | 2000 | -22 | 99 | 1402 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1968 | 2000 | -32 | 98 | 1396 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1858 | 2000 | -142 | 93 | 1318 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1837 | 2000 | -163 | 92 | 1302 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1798 | 2000 | -202 | 90 | 1265 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1783 | 2000 | -217 | 89 | 1266 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1776 | 2000 | -224 | 89 | 1253 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1769 | 2000 | -231 | 88 | 1254 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1768 | 2000 | -232 | 88 | 1253 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1765 | 2000 | -235 | 88 | 1250 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1764 | 2000 | -236 | 88 | 1251 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1748 | 2000 | -252 | 87 | 1230 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 848 | 999 | -151 | 85 | 320 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1553 | 1836 | -283 | 85 | 1080 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1676 | 2000 | -324 | 84 | 1182 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1670 | 2000 | -330 | 84 | 1178 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1503 | 1836 | -333 | 82 | 1045 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1503 | 1836 | -333 | 82 | 1045 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1502 | 1836 | -334 | 82 | 1047 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1836 | -351 | 81 | 1030 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1836 | -351 | 81 | 1030 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1479 | 1836 | -357 | 81 | 1025 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1472 | 1836 | -364 | 80 | 1021 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1460 | 1836 | -376 | 80 | 1012 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1452 | 1836 | -384 | 79 | 1007 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1836 | -388 | 79 | 1004 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1441 | 1836 | -395 | 78 | 999 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1836 | -397 | 78 | 997 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1409 | 1836 | -427 | 77 | 976 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1460 | 2000 | -540 | 73 | -1002 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1460 | 2000 | -540 | 73 | 1018 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 909 | 1248 | -340 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 909 | 1248 | -340 | 73 | 371 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1450 | 2000 | -550 | 72 | -994 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1450 | 2000 | -550 | 72 | 1012 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 903 | 1248 | -346 | 72 | 368 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 899 | 1248 | -349 | 72 | 367 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 899 | 1248 | -349 | 72 | 367 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 897 | 1248 | -352 | 72 | 366 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 897 | 1248 | -352 | 72 | 366 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 894 | 1248 | -355 | 72 | 365 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 894 | 1248 | -355 | 72 | 365 | AC

## 0530
Detailed results
Generated at: | 08/03/2026 22:45:55
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3016
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1969 | 2000 | -31 | 98 | 1388 | AC no reactive limits
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1952 | 2000 | -48 | 98 | 1382 | AC no reactive limits
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1951 | 2000 | -49 | 98 | 1378 | AC no reactive limits
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1951 | 2000 | -49 | 98 | 1379 | AC no reactive limits
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1815 | 2000 | -185 | 91 | 1284 | AC no reactive limits
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1792 | 2000 | -208 | 90 | 1266 | AC no reactive limits
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1725 | 2000 | -275 | 86 | 1210 | AC no reactive limits
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1716 | 2000 | -284 | 86 | 1212 | AC no reactive limits
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1713 | 2000 | -287 | 86 | 1210 | AC no reactive limits
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1712 | 2000 | -288 | 86 | 1209 | AC no reactive limits
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1705 | 2000 | -295 | 85 | 1208 | AC no reactive limits
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1700 | 2000 | -300 | 85 | 1195 | AC no reactive limits
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1693 | 2000 | -307 | 85 | 1196 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1677 | 2000 | -323 | 84 | 1179 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1651 | 2000 | -349 | 83 | 1160 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1646 | 2000 | -354 | 82 | 1157 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 752 | 999 | -247 | 75 | 284 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 927 | 1248 | -322 | 74 | 378 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 927 | 1248 | -322 | 74 | 378 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 924 | 1248 | -324 | 74 | 377 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 924 | 1248 | -324 | 74 | 377 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 921 | 1248 | -327 | 74 | 376 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 921 | 1248 | -327 | 74 | 376 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 900 | 1248 | -348 | 72 | 367 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 900 | 1248 | -348 | 72 | 367 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1320 | 1836 | -516 | 72 | 907 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 895 | 1248 | -354 | 72 | 365 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1426 | 2000 | -574 | 71 | 1004 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1300 | 1836 | -536 | 71 | 896 | AC no reactive limits

## 0630
Detailed results
Generated at: | 08/03/2026 22:45:55
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3496
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00105 | RO | RROVI31 _generator | 0 | 310 |  |  | 310 | 1 |  | 310 | 1 | FALSE | FALSE
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 389 | 54 |  | 389 | 0 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 24 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 57 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 2 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 21 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 28 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 22 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 22 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 29 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 15 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 11 | 59 |  | 59 | 0 | FALSE | FALSE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 7 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 9 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 21 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 25 | 67 |  | 67 | 0 | FALSE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 9 |  | 9 | 0 | FALSE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 17 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 18 | 24 |  | 24 | 0 | FALSE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 13 |  | 13 | 0 | FALSE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 55 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 14 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 20 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 19 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 16 | 34 |  | 34 | 0 | FALSE | FALSE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 25 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 96 |  | 96 | 0 | TRUE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 58 |  | 58 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 2 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 3 | 29 |  | 29 | 0 | FALSE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 2 | 27 |  | 27 | 0 | FALSE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 4 | 52 |  | 52 | 0 | FALSE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1997 | 2000 | -3 | 100 | 1392 | AC no reactive limits
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1963 | 2000 | -37 | 98 | 1370 | AC no reactive limits
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1955 | 2000 | -45 | 98 | 1368 | AC no reactive limits
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1953 | 2000 | -47 | 98 | 1365 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1862 | 2000 | -138 | 93 | 1292 | AC no reactive limits
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1836 | 2000 | -164 | 92 | 1278 | AC no reactive limits
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1836 | 2000 | -164 | 92 | 1283 | AC no reactive limits
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1832 | 2000 | -168 | 92 | 1279 | AC no reactive limits
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1775 | 2000 | -225 | 89 | 1238 | AC no reactive limits
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1773 | 2000 | -227 | 89 | 1237 | AC no reactive limits
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1773 | 2000 | -227 | 89 | 1236 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 858 | 999 | -141 | 86 | 332 | AC no reactive limits
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1676 | 2000 | -324 | 84 | 1173 | AC no reactive limits
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1666 | 2000 | -334 | 83 | 1149 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1659 | 2000 | -341 | 83 | 1145 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1652 | 2000 | -348 | 83 | 1141 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1588 | 2000 | -412 | 79 | 1114 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1366 | 1836 | -470 | 74 | 954 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1472 | 2000 | -528 | 74 | 1021 | AC no reactive limits
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1472 | 2000 | -528 | 74 | -1005 | AC no reactive limits
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1463 | 2000 | -537 | 73 | -997 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1463 | 2000 | -537 | 73 | 1016 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1342 | 1836 | -494 | 73 | 932 | AC no reactive limits
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1342 | 1836 | -494 | 73 | 932 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1324 | 1836 | -512 | 72 | 917 | AC no reactive limits
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1324 | 1836 | -512 | 72 | 917 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1313 | 1836 | -523 | 72 | 910 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1312 | 1836 | -524 | 71 | 908 | AC no reactive limits
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1306 | 1836 | -530 | 71 | 906 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1286 | 1836 | -550 | 70 | 888 | AC no reactive limits

## 0730
Detailed results
Generated at: | 08/03/2026 22:45:55
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3439
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1925 | 2000 | -75 | 96 | 1346 | AC no reactive limits
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1910 | 2000 | -90 | 95 | 1339 | AC no reactive limits
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1892 | 2000 | -108 | 95 | 1325 | AC no reactive limits
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1890 | 2000 | -110 | 94 | 1326 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1840 | 2000 | -160 | 92 | 1285 | AC no reactive limits
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1744 | 2000 | -256 | 87 | 1217 | AC no reactive limits
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1742 | 2000 | -258 | 87 | 1219 | AC no reactive limits
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1741 | 2000 | -259 | 87 | 1219 | AC no reactive limits
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1722 | 2000 | -278 | 86 | 1206 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1544 | 1836 | -292 | 84 | 1080 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1518 | 1836 | -318 | 83 | 1066 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1506 | 1836 | -330 | 82 | 1054 | AC no reactive limits
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1506 | 1836 | -330 | 82 | 1054 | AC no reactive limits
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1492 | 1836 | -344 | 81 | 1041 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1492 | 1836 | -344 | 81 | 1041 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1836 | -351 | 81 | 1036 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1605 | 2000 | -395 | 80 | 1112 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1472 | 1836 | -364 | 80 | 1027 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1600 | 2000 | -400 | 80 | 1109 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1836 | -370 | 80 | 1018 | AC no reactive limits
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1464 | 1836 | -372 | 80 | 1022 | AC no reactive limits
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1446 | 1836 | -390 | 79 | 1007 | AC no reactive limits
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1836 | -393 | 79 | 1004 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1570 | 2000 | -430 | 79 | 1093 | AC no reactive limits
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1438 | 1836 | -398 | 78 | 999 | AC no reactive limits
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1416 | 1836 | -420 | 77 | 984 | AC no reactive limits
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1529 | 2000 | -471 | 76 | 1075 | AC no reactive limits
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1519 | 2000 | -481 | 76 | 1051 | AC no reactive limits
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1514 | 2000 | -486 | 76 | 1056 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 934 | 1248 | -315 | 75 | 381 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 934 | 1248 | -315 | 75 | 381 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 931 | 1248 | -317 | 75 | 380 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 931 | 1248 | -317 | 75 | 380 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 928 | 1248 | -321 | 74 | 379 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 928 | 1248 | -321 | 74 | 379 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 907 | 1248 | -342 | 73 | 370 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 907 | 1248 | -342 | 73 | 370 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 901 | 1248 | -348 | 72 | 368 | AC no reactive limits

## 0830
Detailed results
Generated at: | 08/03/2026 22:45:56
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3967
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 0 | 50 |  | 50 | 0 | TRUE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 0 | 114 |  | 114 | 0 | TRUE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 9 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 14 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 23 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 30 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 12 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 23 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 12 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 23 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 22 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 25 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 26 | 9 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 20 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 13 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 27 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 27 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 27 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 27 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 27 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 11 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 16 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 25 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 17 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 22 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 26 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 18 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 19 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 9 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 13 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 53 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 12 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 17 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 19 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 13 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 7 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 96 |  | 96 | 0 | TRUE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 58 |  | 58 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1396 | AC no reactive limits
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1965 | 2000 | -35 | 98 | 1380 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1955 | 2000 | -45 | 98 | 1372 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1929 | 2000 | -71 | 96 | 1356 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1911 | 2000 | -89 | 96 | 1334 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1701 | 1836 | -135 | 93 | 1197 | AC no reactive limits
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1820 | 2000 | -180 | 91 | 1273 | AC no reactive limits
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1818 | 2000 | -182 | 91 | 1275 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1817 | 2000 | -183 | 91 | 1275 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1665 | 1836 | -171 | 91 | 1172 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1665 | 1836 | -171 | 91 | 1172 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1657 | 1836 | -179 | 90 | 1168 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1802 | 2000 | -198 | 90 | 1264 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1652 | 1836 | -184 | 90 | 1162 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1645 | 1836 | -191 | 90 | 1157 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1645 | 1836 | -191 | 90 | 1157 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1621 | 1836 | -215 | 88 | 1139 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1613 | 1836 | -223 | 88 | 1134 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1588 | 1836 | -248 | 86 | 1116 | AC no reactive limits
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1586 | 1836 | -250 | 86 | 1113 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1574 | 1836 | -262 | 86 | 1105 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1568 | 1836 | -268 | 85 | 1100 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1550 | 1836 | -286 | 84 | 1087 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1674 | 2000 | -326 | 84 | 1177 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1666 | 2000 | -334 | 83 | 1154 | AC no reactive limits
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1661 | 2000 | -339 | 83 | 1152 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1660 | 2000 | -340 | 83 | 1151 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 824 | 999 | -175 | 82 | 306 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1591 | 2000 | -409 | 80 | 1112 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 949 | 1248 | -300 | 76 | 387 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 949 | 1248 | -300 | 76 | 387 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 946 | 1248 | -302 | 76 | 386 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 946 | 1248 | -302 | 76 | 386 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 943 | 1248 | -306 | 76 | 385 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 943 | 1248 | -306 | 76 | 385 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1506 | 2000 | -494 | 75 | 1049 | AC no reactive limits
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1506 | 2000 | -494 | 75 | -1032 | AC no reactive limits
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1497 | 2000 | -503 | 75 | -1025 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1497 | 2000 | -503 | 75 | 1045 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1140 | 1600 | -460 | 71 | 787 | AC

## 0930
Detailed results
Generated at: | 08/03/2026 22:45:56
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3733.63
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1758 | 1836 | -78 | 96 | 1241 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1754 | 1836 | -82 | 96 | 1238 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1900 | 2000 | -100 | 95 | 1334 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1739 | 1836 | -97 | 95 | 1227 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1735 | 1836 | -101 | 94 | 1224 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1735 | 1836 | -101 | 94 | 1224 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1882 | 2000 | -118 | 94 | 1325 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1868 | 2000 | -132 | 93 | 1314 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1707 | 1836 | -129 | 93 | 1206 | AC no reactive limits
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1858 | 2000 | -142 | 93 | 1309 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1686 | 1836 | -150 | 92 | 1189 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1686 | 1836 | -150 | 92 | 1189 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1817 | 2000 | -183 | 91 | 1272 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1660 | 1836 | -176 | 90 | 1170 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1654 | 1836 | -182 | 90 | 1165 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1642 | 1836 | -194 | 89 | 1158 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1642 | 1836 | -194 | 89 | 1156 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1624 | 1836 | -212 | 88 | 1144 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1609 | 1836 | -227 | 88 | 1133 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1724 | 2000 | -276 | 86 | 1210 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1723 | 2000 | -277 | 86 | 1212 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1723 | 2000 | -277 | 86 | 1212 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1704 | 2000 | -296 | 85 | 1200 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1585 | 2000 | -415 | 79 | 1103 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 791 | 999 | -208 | 79 | 297 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1579 | 2000 | -421 | 79 | 1100 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1532 | 2000 | -468 | 77 | 1081 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1521 | 2000 | -479 | 76 | 1059 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1496 | 2000 | -504 | 75 | 1051 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1485 | 2000 | -515 | 74 | 1043 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 915 | 1248 | -334 | 73 | 373 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 915 | 1248 | -334 | 73 | 373 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 910 | 1248 | -339 | 73 | 372 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 910 | 1248 | -339 | 73 | 372 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 909 | 1248 | -340 | 73 | 371 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 907 | 1248 | -341 | 73 | 371 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 907 | 1248 | -341 | 73 | 371 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 904 | 1248 | -344 | 72 | 369 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 904 | 1248 | -344 | 72 | 369 | AC

## 1030
Detailed results
Generated at: | 08/03/2026 22:45:56
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3639.09
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1844 | 1836 | 8 | 100 | 1303 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1809 | 1836 | -27 | 99 | 1279 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1807 | 1836 | -29 | 98 | 1277 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1791 | 1836 | -45 | 98 | 1266 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1791 | 1836 | -45 | 98 | 1266 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1763 | 1836 | -73 | 96 | 1246 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1720 | 1836 | -116 | 94 | 1214 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1720 | 1836 | -116 | 94 | 1214 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1712 | 1836 | -124 | 93 | 1210 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1706 | 1836 | -130 | 93 | 1203 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1857 | 2000 | -143 | 93 | 1303 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1693 | 1836 | -143 | 92 | 1196 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1691 | 1836 | -145 | 92 | 1193 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1833 | 2000 | -167 | 92 | 1291 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1672 | 1836 | -164 | 91 | 1180 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1817 | 2000 | -183 | 91 | 1278 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1654 | 1836 | -182 | 90 | 1167 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1791 | 2000 | -209 | 90 | 1263 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1757 | 2000 | -243 | 88 | 1233 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 871 | 999 | -128 | 87 | 327 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1658 | 2000 | -342 | 83 | 1164 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1658 | 2000 | -342 | 83 | 1167 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1658 | 2000 | -342 | 83 | 1167 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1642 | 2000 | -358 | 82 | 1156 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1592 | 2000 | -408 | 80 | 1111 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1528 | 2000 | -472 | 76 | 1064 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1523 | 2000 | -477 | 76 | 1061 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 915 | 1248 | -333 | 73 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 915 | 1248 | -333 | 73 | 374 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1167 | 1600 | -433 | 73 | 805 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 909 | 1248 | -339 | 73 | 371 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1455 | 2000 | -545 | 73 | 1023 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1434 | 2000 | -566 | 72 | 1014 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1140 | 1600 | -460 | 71 | 790 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 884 | 1248 | -365 | 71 | 361 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 884 | 1248 | -365 | 71 | 361 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1415 | 2000 | -585 | 71 | 986 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 882 | 1248 | -367 | 71 | 360 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 882 | 1248 | -367 | 71 | 360 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 878 | 1248 | -370 | 70 | 359 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 878 | 1248 | -370 | 70 | 359 | AC

## 1130
Detailed results
Generated at: | 08/03/2026 22:45:56
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3810.67
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1793 | 1836 | -43 | 98 | 1266 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1773 | 1836 | -63 | 97 | 1252 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1759 | 1836 | -77 | 96 | 1241 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1757 | 1836 | -79 | 96 | 1240 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1757 | 1836 | -79 | 96 | 1240 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1910 | 2000 | -90 | 95 | 1345 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1874 | 2000 | -126 | 94 | 1322 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1869 | 2000 | -131 | 93 | 1317 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1710 | 1836 | -126 | 93 | 1208 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1698 | 1836 | -138 | 92 | 1198 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1698 | 1836 | -138 | 92 | 1198 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1678 | 1836 | -158 | 91 | 1184 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1826 | 2000 | -174 | 91 | 1288 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1672 | 1836 | -164 | 91 | 1177 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1817 | 2000 | -183 | 91 | 1274 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1660 | 1836 | -176 | 90 | 1169 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1660 | 1836 | -176 | 90 | 1171 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1640 | 1836 | -196 | 89 | 1156 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1626 | 1836 | -210 | 89 | 1146 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1733 | 2000 | -267 | 87 | 1222 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1733 | 2000 | -267 | 87 | 1222 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1732 | 2000 | -268 | 87 | 1219 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1720 | 2000 | -280 | 86 | 1213 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1615 | 2000 | -385 | 81 | 1141 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 801 | 999 | -198 | 80 | 301 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1588 | 2000 | -412 | 79 | 1108 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1582 | 2000 | -418 | 79 | 1103 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1576 | 2000 | -424 | 79 | 1099 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1560 | 2000 | -440 | 78 | 1099 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1467 | 2000 | -533 | 73 | -1011 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1467 | 2000 | -533 | 73 | 1027 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 914 | 1248 | -335 | 73 | 373 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 914 | 1248 | -335 | 73 | 373 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1458 | 2000 | -542 | 73 | -1003 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1458 | 2000 | -542 | 73 | 1022 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 908 | 1248 | -341 | 73 | 371 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 903 | 1248 | -346 | 72 | 369 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 903 | 1248 | -346 | 72 | 369 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 900 | 1248 | -348 | 72 | 368 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 900 | 1248 | -348 | 72 | 368 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 897 | 1248 | -352 | 72 | 366 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 897 | 1248 | -352 | 72 | 366 | AC

## 1230
Detailed results
Generated at: | 08/03/2026 22:45:56
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 4128
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00105 | RO | RROVI31 _generator | 0 | 310 |  |  | 310 | 1 |  | 310 | 1 | FALSE | FALSE
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 389 | 365 |  | 389 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 10 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 17 |  | 90 | 0 | FALSE | FALSE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 0 | 170 |  | 170 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 8 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 13 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 8 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 17 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 8 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 13 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 13 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 12 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 14 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 5 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 13 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 10 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 7 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 14 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 14 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 14 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 14 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 14 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 17 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 27 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 17 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 18 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 49 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 11 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 8 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 96 |  | 96 | 0 | TRUE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 58 |  | 58 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1998 | 2000 | -2 | 100 | 1405 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1950 | 2000 | -50 | 98 | 1373 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1939 | 2000 | -61 | 97 | 1366 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1907 | 2000 | -93 | 95 | 1334 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1888 | 2000 | -112 | 94 | 1329 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1723 | 1836 | -113 | 94 | 1202 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1715 | 1836 | -121 | 93 | 1196 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1715 | 1836 | -121 | 93 | 1196 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1699 | 1836 | -137 | 93 | 1184 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1680 | 1836 | -156 | 92 | 1173 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1830 | 2000 | -170 | 91 | 1288 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1830 | 2000 | -170 | 91 | 1288 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1829 | 2000 | -171 | 91 | 1285 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1674 | 1836 | -162 | 91 | 1168 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1674 | 1836 | -162 | 91 | 1168 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1817 | 2000 | -183 | 91 | 1280 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1662 | 1836 | -174 | 90 | 1159 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1798 | 2000 | -202 | 90 | 1268 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1641 | 1836 | -195 | 89 | 1145 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1620 | 1836 | -216 | 88 | 1130 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1762 | 2000 | -238 | 88 | 1229 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1611 | 1836 | -225 | 88 | 1124 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1601 | 1836 | -235 | 87 | 1117 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1583 | 1836 | -253 | 86 | 1104 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1580 | 1836 | -256 | 86 | 1102 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1683 | 2000 | -317 | 84 | 1184 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1662 | 2000 | -338 | 83 | -1138 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1662 | 2000 | -338 | 83 | 1159 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1661 | 2000 | -339 | 83 | 1154 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1653 | 2000 | -347 | 83 | 1150 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1651 | 2000 | -349 | 83 | 1153 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1651 | 2000 | -349 | 83 | -1129 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1013 | 1248 | -235 | 81 | 413 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1013 | 1248 | -235 | 81 | 413 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1010 | 1248 | -238 | 81 | 412 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1010 | 1248 | -238 | 81 | 412 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1007 | 1248 | -242 | 81 | 411 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1007 | 1248 | -242 | 81 | 411 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 731 | 999 | -269 | 73 | 270 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 898 | 1248 | -351 | 72 | 366 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 898 | 1248 | -351 | 72 | 366 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 892 | 1248 | -356 | 71 | 364 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [DIR]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1364 | 1920 | -556 | 71 | 935 | AC

## 1330
Detailed results
Generated at: | 08/03/2026 22:45:56
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3742
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00105 | RO | RROVI31 _generator | 0 | 310 |  |  | 310 | 1 |  | 310 | 1 | FALSE | FALSE
RO_RA_00107 | RO | RTURC11 _generator | 0 | 302 |  |  | 302 | 211 |  | 302 | 1 | FALSE | FALSE
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 389 | 0 |  | 389 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 9 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 0 | 170 |  | 170 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 8 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 13 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 8 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 17 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 7 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 13 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 13 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 12 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 14 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 5 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 13 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 10 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 7 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 14 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 14 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 14 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 14 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 14 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 16 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 26 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 20 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 24 | 67 |  | 67 | 0 | FALSE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 9 |  | 9 | 0 | FALSE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 17 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 17 | 24 |  | 24 | 0 | FALSE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 13 |  | 13 | 0 | FALSE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 48 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 11 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 18 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 34 |  | 34 | 0 | FALSE | FALSE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 8 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 96 |  | 96 | 0 | TRUE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 58 |  | 58 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1996 | 2000 | -4 | 100 | 1402 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1941 | 2000 | -59 | 97 | 1365 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1916 | 2000 | -84 | 96 | 1337 | AC no reactive limits
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1899 | 2000 | -101 | 95 | 1336 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1864 | 2000 | -136 | 93 | 1312 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1816 | 2000 | -184 | 91 | 1277 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1816 | 2000 | -184 | 91 | 1277 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1814 | 2000 | -186 | 91 | 1273 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1792 | 2000 | -208 | 90 | 1262 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1782 | 2000 | -218 | 89 | 1258 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1741 | 2000 | -259 | 87 | 1215 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1718 | 2000 | -282 | 86 | 1207 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1529 | 1836 | -307 | 83 | 1075 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1654 | 2000 | -346 | 83 | -1134 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1654 | 2000 | -346 | 83 | 1154 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1647 | 2000 | -353 | 82 | 1142 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1643 | 2000 | -357 | 82 | 1148 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1643 | 2000 | -357 | 82 | -1125 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1639 | 2000 | -361 | 82 | 1138 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1496 | 1836 | -340 | 81 | 1051 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1836 | -358 | 80 | 1039 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1836 | -358 | 80 | 1039 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1471 | 1836 | -365 | 80 | 1035 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1450 | 1836 | -386 | 79 | 1020 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1836 | -393 | 79 | 1015 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1836 | -393 | 79 | 1015 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [DIR]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1506 | 1920 | -414 | 78 | 1026 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1437 | 1836 | -399 | 78 | 1006 | AC no reactive limits
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1413 | 1836 | -423 | 77 | 993 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1396 | 1836 | -440 | 76 | 982 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1390 | 1836 | -446 | 76 | 978 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1191 | 1600 | -409 | 74 | 826 | AC no reactive limits
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1363 | 1836 | -473 | 74 | 959 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1363 | 1836 | -473 | 74 | 959 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 735 | 999 | -264 | 74 | 270 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1166 | 1600 | -434 | 73 | 806 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [DIR]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1388 | 1920 | -532 | 72 | 937 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1146 | 1600 | -454 | 72 | 793 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1138 | 1600 | -462 | 71 | 788 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1402 | 2000 | -598 | 70 | 989 | AC

## 1430
Detailed results
Generated at: | 08/03/2026 22:45:56
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3913
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 389 | 120 |  | 389 | 0 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 0 | 50 |  | 50 | 0 | TRUE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 0 | 114 |  | 114 | 0 | TRUE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 8 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 0 | 170 |  | 170 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 8 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 14 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 8 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 18 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 8 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 14 | 20 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 14 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 13 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 15 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 5 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 25 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 19 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 13 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 26 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 26 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 26 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 26 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 26 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 11 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 15 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 23 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 21 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 25 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 17 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 18 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 50 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 11 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 16 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 7 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 96 |  | 96 | 0 | TRUE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 58 |  | 58 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1997 | 2000 | -3 | 100 | 1403 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1929 | 2000 | -71 | 96 | 1357 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1923 | 2000 | -77 | 96 | 1354 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1872 | 2000 | -128 | 94 | 1310 | AC no reactive limits
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1706 | 1836 | -130 | 93 | 1203 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1838 | 2000 | -162 | 92 | 1295 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1654 | 1836 | -182 | 90 | 1165 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1654 | 1836 | -182 | 90 | 1165 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1652 | 1836 | -184 | 90 | 1164 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1637 | 1836 | -199 | 89 | 1156 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1629 | 1836 | -207 | 89 | 1147 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1772 | 2000 | -228 | 89 | 1247 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1772 | 2000 | -228 | 89 | 1247 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1770 | 2000 | -230 | 88 | 1243 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1760 | 2000 | -240 | 88 | 1240 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1613 | 1836 | -223 | 88 | 1135 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1613 | 1836 | -223 | 88 | 1135 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 877 | 999 | -122 | 88 | 326 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1602 | 1836 | -234 | 87 | 1128 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1575 | 1836 | -261 | 86 | 1110 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1565 | 1836 | -271 | 85 | 1102 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1555 | 1836 | -281 | 85 | 1094 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1545 | 1836 | -291 | 84 | 1088 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1526 | 1836 | -310 | 83 | 1074 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1650 | 2000 | -350 | 82 | 1165 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1318 | 1600 | -282 | 82 | 904 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-UA] [DIR]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1567 | 1920 | -353 | 82 | 1064 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1619 | 2000 | -381 | 81 | 1139 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1617 | 2000 | -383 | 81 | 1124 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1610 | 2000 | -390 | 81 | 1120 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1603 | 2000 | -397 | 80 | 1117 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1277 | 1600 | -323 | 80 | 882 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1269 | 1600 | -331 | 79 | 876 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1255 | 1600 | -345 | 78 | 866 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1526 | 2000 | -474 | 76 | 1067 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1526 | 2000 | -474 | 76 | -1050 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-UA] [DIR]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1457 | 1920 | -463 | 76 | 979 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1516 | 2000 | -484 | 76 | -1042 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1516 | 2000 | -484 | 76 | 1062 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1177 | 1600 | -423 | 74 | 816 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1177 | 1600 | -423 | 74 | 816 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1462 | 2000 | -538 | 73 | 1028 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-UA] [DIR]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1390 | 1920 | -530 | 72 | 943 | AC
Base case | Base case | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1147 | 1600 | -453 | 72 | 796 | AC

## 1530
Detailed results
Generated at: | 08/03/2026 22:45:56
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3527
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1998 | 2000 | -2 | 100 | 1404 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1948 | 2000 | -52 | 97 | 1370 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1946 | 2000 | -54 | 97 | 1371 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1883 | 2000 | -117 | 94 | 1327 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1823 | 2000 | -177 | 91 | 1275 | AC no reactive limits
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1801 | 2000 | -199 | 90 | 1268 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1799 | 2000 | -201 | 90 | 1264 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1798 | 2000 | -202 | 90 | 1266 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1732 | 2000 | -268 | 87 | 1219 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1730 | 2000 | -270 | 86 | 1217 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1729 | 2000 | -271 | 86 | 1216 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1673 | 2000 | -327 | 84 | 1181 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1524 | 1836 | -312 | 83 | 1059 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1501 | 1836 | -335 | 82 | 1048 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1493 | 1836 | -343 | 81 | 1039 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1493 | 1836 | -343 | 81 | 1039 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1622 | 2000 | -378 | 81 | 1128 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1620 | 2000 | -380 | 81 | 1128 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1615 | 2000 | -385 | 81 | 1124 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1471 | 1836 | -365 | 80 | 1021 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1471 | 1836 | -365 | 80 | 1021 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1469 | 1836 | -367 | 80 | 1019 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1836 | -388 | 79 | 1005 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1836 | -388 | 79 | 1005 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1437 | 1836 | -399 | 78 | 996 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1421 | 1836 | -415 | 77 | 986 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1414 | 1836 | -422 | 77 | 981 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1398 | 1836 | -438 | 76 | 969 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 948 | 1248 | -300 | 76 | 387 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 948 | 1248 | -300 | 76 | 387 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 946 | 1248 | -303 | 76 | 386 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 946 | 1248 | -303 | 76 | 386 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1390 | 1836 | -446 | 76 | 964 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 942 | 1248 | -306 | 75 | 385 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 942 | 1248 | -306 | 75 | 385 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1503 | 2000 | -497 | 75 | -1033 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1503 | 2000 | -497 | 75 | 1050 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1493 | 2000 | -507 | 75 | 1045 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1493 | 2000 | -507 | 75 | -1025 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1454 | 2000 | -546 | 73 | 1024 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 906 | 1248 | -342 | 73 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 906 | 1248 | -342 | 73 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 901 | 1248 | -348 | 72 | 368 | AC

## 1630
Detailed results
Generated at: | 08/03/2026 22:45:57
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3214
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 55 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 2 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 44 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 28 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 17 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 12 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 24 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 24 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 24 | 22 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 6 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 7 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 15 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 20 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 24 | 67 |  | 67 | 0 | FALSE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 9 |  | 9 | 0 | FALSE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 16 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 17 | 24 |  | 24 | 0 | FALSE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 13 |  | 13 | 0 | FALSE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 11 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 46 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 34 |  | 34 | 0 | FALSE | FALSE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 24 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 66 | 71 |  | 71 | 0 | FALSE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1403 | AC no reactive limits
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1936 | 2000 | -64 | 97 | 1363 | AC no reactive limits
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1901 | 2000 | -99 | 95 | 1340 | AC no reactive limits
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1862 | 2000 | -138 | 93 | 1313 | AC no reactive limits
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1812 | 2000 | -188 | 91 | 1278 | AC no reactive limits
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1779 | 2000 | -221 | 89 | 1253 | AC no reactive limits
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1753 | 2000 | -247 | 88 | 1226 | AC no reactive limits
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1738 | 2000 | -262 | 87 | 1229 | AC no reactive limits
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1730 | 2000 | -270 | 86 | 1218 | AC no reactive limits
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1728 | 2000 | -272 | 86 | 1217 | AC no reactive limits
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1727 | 2000 | -273 | 86 | 1216 | AC no reactive limits
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1714 | 2000 | -286 | 86 | 1202 | AC no reactive limits
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1700 | 2000 | -300 | 85 | 1198 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1656 | 2000 | -344 | 83 | 1159 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1620 | 2000 | -380 | 81 | 1131 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1613 | 2000 | -387 | 81 | 1128 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 959 | 1248 | -289 | 77 | 392 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 959 | 1248 | -289 | 77 | 392 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 957 | 1248 | -292 | 77 | 391 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 957 | 1248 | -292 | 77 | 391 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 953 | 1248 | -295 | 76 | 390 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 953 | 1248 | -295 | 76 | 390 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 761 | 999 | -238 | 76 | 294 | AC no reactive limits
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1483 | 2000 | -517 | 74 | -1017 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1483 | 2000 | -517 | 74 | 1033 | AC no reactive limits
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1474 | 2000 | -526 | 74 | -1009 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1474 | 2000 | -526 | 74 | 1028 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1461 | 2000 | -539 | 73 | 1026 | AC no reactive limits

## 1730
Detailed results
Generated at: | 08/03/2026 22:45:57
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3256
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 55 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 44 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 22 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 28 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 22 | 35 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 22 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 20 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 14 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 15 | 5 |  | 54 | 0 | FALSE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 20 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 24 | 67 |  | 67 | 0 | FALSE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 9 |  | 9 | 0 | FALSE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 16 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 17 | 24 |  | 24 | 0 | FALSE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 13 |  | 13 | 0 | FALSE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 11 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 47 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 34 |  | 34 | 0 | FALSE | FALSE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 23 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 66 | 71 |  | 71 | 0 | FALSE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1995 | 2000 | -5 | 100 | 1398 | AC no reactive limits
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1931 | 2000 | -69 | 97 | 1356 | AC no reactive limits
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1894 | 2000 | -106 | 95 | 1331 | AC no reactive limits
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1852 | 2000 | -148 | 93 | 1303 | AC no reactive limits
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1794 | 2000 | -206 | 90 | 1262 | AC no reactive limits
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1764 | 2000 | -236 | 88 | 1239 | AC no reactive limits
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1724 | 2000 | -276 | 86 | 1210 | AC no reactive limits
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1723 | 2000 | -277 | 86 | 1201 | AC no reactive limits
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1722 | 2000 | -278 | 86 | 1209 | AC no reactive limits
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1722 | 2000 | -278 | 86 | 1209 | AC no reactive limits
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1706 | 2000 | -294 | 85 | 1204 | AC no reactive limits
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1683 | 2000 | -317 | 84 | 1176 | AC no reactive limits
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1668 | 2000 | -332 | 83 | 1173 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1626 | 2000 | -374 | 81 | 1136 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1621 | 2000 | -379 | 81 | 1132 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1611 | 2000 | -389 | 81 | 1122 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1606 | 2000 | -394 | 80 | 1119 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 994 | 1248 | -255 | 80 | 405 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 994 | 1248 | -255 | 80 | 405 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 991 | 1248 | -257 | 79 | 404 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 991 | 1248 | -257 | 79 | 404 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 988 | 1248 | -261 | 79 | 403 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 988 | 1248 | -261 | 79 | 403 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1836 | -475 | 74 | 929 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1349 | 1836 | -487 | 74 | 915 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 727 | 999 | -272 | 73 | 281 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 727 | 999 | -272 | 73 | 264 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1328 | 1836 | -508 | 72 | 897 | AC no reactive limits
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1328 | 1836 | -508 | 72 | 897 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 900 | 1248 | -349 | 72 | 367 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 900 | 1248 | -349 | 72 | 367 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 894 | 1248 | -355 | 72 | 365 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1310 | 1836 | -526 | 71 | 890 | AC no reactive limits
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1310 | 1836 | -526 | 71 | 890 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1303 | 1836 | -533 | 71 | 877 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1303 | 1836 | -533 | 71 | 872 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1412 | 2000 | -588 | 71 | 982 | AC no reactive limits
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1412 | 2000 | -588 | 71 | -967 | AC no reactive limits
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1290 | 1836 | -546 | 70 | 862 | AC no reactive limits
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1289 | 1836 | -547 | 70 | 868 | AC no reactive limits
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1404 | 2000 | -596 | 70 | -960 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1404 | 2000 | -596 | 70 | 977 | AC no reactive limits

## 1830
Detailed results
Generated at: | 08/03/2026 22:45:57
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 2977
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00107 | RO | RTURC11 _generator | 0 | 302 |  |  | 302 | 1 |  | 302 | 1 | FALSE | FALSE
RO_RA_00108 | RO | RTURC51 _generator | 0 | 300 |  |  | 300 | 289 |  | 300 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 274 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 24 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 57 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 46 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 14 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 23 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 14 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 29 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 23 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 12 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 23 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 21 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 24 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 29 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 22 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 15 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 11 | 59 |  | 59 | 0 | FALSE | FALSE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 21 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 25 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 17 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 18 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 49 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 11 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 16 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 24 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 69 | 0 |  | 71 | 0 | FALSE | TRUE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 96 | 0 |  | 96 | 0 | FALSE | TRUE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 58 | 0 |  | 58 | 0 | FALSE | TRUE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 2 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 3 | 29 |  | 29 | 0 | FALSE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 2 | 27 |  | 27 | 0 | FALSE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 4 | 52 |  | 52 | 0 | FALSE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1400 | AC no reactive limits
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1940 | 2000 | -60 | 97 | 1367 | AC no reactive limits
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1926 | 2000 | -74 | 96 | 1355 | AC no reactive limits
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1851 | 2000 | -149 | 93 | 1305 | AC no reactive limits
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1744 | 2000 | -256 | 87 | 1227 | AC no reactive limits
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1728 | 2000 | -272 | 86 | 1216 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1677 | 2000 | -323 | 84 | 1171 | AC no reactive limits
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1660 | 2000 | -340 | 83 | 1168 | AC no reactive limits
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1658 | 2000 | -342 | 83 | 1166 | AC no reactive limits
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1657 | 2000 | -343 | 83 | 1166 | AC no reactive limits
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1638 | 2000 | -362 | 82 | 1144 | AC no reactive limits
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1619 | 2000 | -381 | 81 | 1144 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1599 | 2000 | -401 | 80 | 1118 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1594 | 2000 | -406 | 80 | 1116 | AC no reactive limits
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1594 | 2000 | -406 | 80 | 1115 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1583 | 2000 | -417 | 79 | 1111 | AC no reactive limits
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1583 | 2000 | -417 | 79 | 1114 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1430 | 1836 | -406 | 78 | 965 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1421 | 1836 | -415 | 77 | 966 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 767 | 999 | -232 | 77 | 279 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 756 | 999 | -243 | 76 | 292 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1378 | 1836 | -458 | 75 | 913 | AC no reactive limits
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1377 | 1836 | -459 | 75 | 921 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1377 | 1836 | -459 | 75 | 921 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1374 | 1836 | -462 | 75 | 927 | AC no reactive limits
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1374 | 1836 | -462 | 75 | 927 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 933 | 1248 | -315 | 75 | 380 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 933 | 1248 | -315 | 75 | 380 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 931 | 1248 | -317 | 75 | 379 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 931 | 1248 | -317 | 75 | 379 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1836 | -471 | 74 | 912 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 928 | 1248 | -321 | 74 | 378 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 928 | 1248 | -321 | 74 | 378 | AC no reactive limits
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1356 | 1836 | -480 | 74 | 898 | AC no reactive limits
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1356 | 1836 | -480 | 74 | 907 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1350 | 1836 | -486 | 74 | 899 | AC no reactive limits
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1346 | 1836 | -490 | 73 | 896 | AC no reactive limits
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1331 | 1836 | -505 | 73 | 885 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 901 | 1248 | -348 | 72 | 367 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 901 | 1248 | -348 | 72 | 367 | AC no reactive limits
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1318 | 1836 | -518 | 72 | 874 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 895 | 1248 | -354 | 72 | 364 | AC no reactive limits

## 1930
Detailed results
Generated at: | 08/03/2026 22:45:57
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3109
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00107 | RO | RTURC11 _generator | 0 | 302 |  |  | 302 | 141 |  | 302 | 1 | FALSE | FALSE
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 293 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 49 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 59 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 22 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 14 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 23 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 14 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 30 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 12 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 24 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 12 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 24 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 22 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 25 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 30 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 22 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 15 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 31 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 31 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 31 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 31 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 31 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 11 | 59 |  | 59 | 0 | FALSE | FALSE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 17 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 21 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 25 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 18 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 18 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 51 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 11 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 16 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 15 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 13 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 25 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 2 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 3 | 29 |  | 29 | 0 | FALSE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 3 | 27 |  | 27 | 0 | FALSE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 4 | 52 |  | 52 | 0 | FALSE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1400 | AC no reactive limits
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1929 | 2000 | -71 | 96 | 1358 | AC no reactive limits
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1921 | 2000 | -79 | 96 | 1351 | AC no reactive limits
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1835 | 2000 | -165 | 92 | 1293 | AC no reactive limits
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1743 | 2000 | -257 | 87 | 1226 | AC no reactive limits
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1726 | 2000 | -274 | 86 | 1214 | AC no reactive limits
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1665 | 2000 | -335 | 83 | 1170 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1662 | 2000 | -338 | 83 | 1157 | AC no reactive limits
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1662 | 2000 | -338 | 83 | 1169 | AC no reactive limits
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1662 | 2000 | -338 | 83 | 1168 | AC no reactive limits
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1644 | 2000 | -356 | 82 | 1147 | AC no reactive limits
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1624 | 2000 | -376 | 81 | 1148 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 808 | 999 | -191 | 81 | 294 | AC no reactive limits
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1599 | 2000 | -401 | 80 | 1118 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1593 | 2000 | -407 | 80 | 1113 | AC no reactive limits
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1589 | 2000 | -411 | 79 | 1111 | AC no reactive limits
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1586 | 2000 | -414 | 79 | 1116 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1583 | 2000 | -417 | 79 | 1111 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1438 | 1836 | -398 | 78 | 968 | AC no reactive limits
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1435 | 1836 | -401 | 78 | 973 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 962 | 1248 | -287 | 77 | 392 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 962 | 1248 | -287 | 77 | 392 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 959 | 1248 | -289 | 77 | 391 | AC no reactive limits
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 959 | 1248 | -289 | 77 | 391 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 956 | 1248 | -293 | 77 | 389 | AC no reactive limits
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 956 | 1248 | -293 | 77 | 389 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1396 | 1836 | -440 | 76 | 934 | AC no reactive limits
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1396 | 1836 | -440 | 76 | 934 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1836 | -441 | 76 | 940 | AC no reactive limits
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1836 | -441 | 76 | 940 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1390 | 1836 | -446 | 76 | 923 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1836 | -454 | 75 | 923 | AC no reactive limits
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1371 | 1836 | -465 | 75 | 908 | AC no reactive limits
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1370 | 1836 | -466 | 75 | 915 | AC no reactive limits
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1363 | 1836 | -473 | 74 | 907 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1836 | -475 | 74 | 905 | AC no reactive limits
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1349 | 1836 | -487 | 73 | 896 | AC no reactive limits
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1332 | 1836 | -504 | 73 | 882 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 904 | 1248 | -344 | 72 | 368 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 904 | 1248 | -344 | 72 | 368 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 899 | 1248 | -350 | 72 | 366 | AC no reactive limits

## 2030
Detailed results
Generated at: | 08/03/2026 22:45:57
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3315
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 46 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 56 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 22 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 14 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 29 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 23 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 2 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 23 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 21 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 24 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 28 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 21 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 15 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 20 | 2 |  | 32 | 0 | FALSE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 24 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 17 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 17 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 49 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 11 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 24 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 67 | 71 |  | 71 | 0 | FALSE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 2 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 3 | 29 |  | 29 | 0 | FALSE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 2 | 27 |  | 27 | 0 | FALSE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 4 | 52 |  | 52 | 0 | FALSE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1995 | 2000 | -5 | 100 | 1401 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1933 | 2000 | -67 | 97 | 1360 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1916 | 2000 | -84 | 96 | 1351 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1859 | 2000 | -141 | 93 | 1312 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1782 | 2000 | -218 | 89 | 1256 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1759 | 2000 | -241 | 88 | 1240 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1705 | 2000 | -295 | 85 | 1201 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1703 | 2000 | -297 | 85 | 1200 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1703 | 2000 | -297 | 85 | 1199 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1701 | 2000 | -299 | 85 | 1190 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1685 | 2000 | -315 | 84 | 1192 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1660 | 2000 | -340 | 83 | 1163 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1648 | 2000 | -352 | 82 | 1161 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1627 | 2000 | -373 | 81 | 1141 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1613 | 2000 | -387 | 81 | 1128 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1608 | 2000 | -392 | 80 | 1125 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1591 | 2000 | -409 | 80 | 1112 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 978 | 1248 | -270 | 78 | 399 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 978 | 1248 | -270 | 78 | 399 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 976 | 1248 | -273 | 78 | 398 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 976 | 1248 | -273 | 78 | 398 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 972 | 1248 | -276 | 78 | 397 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 972 | 1248 | -276 | 78 | 397 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 776 | 999 | -223 | 78 | 300 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1836 | -432 | 76 | 963 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 763 | 999 | -236 | 76 | 280 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1398 | 1836 | -438 | 76 | 958 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1372 | 1836 | -464 | 75 | 938 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1372 | 1836 | -464 | 75 | 938 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1359 | 1836 | -477 | 74 | 930 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1359 | 1836 | -477 | 74 | 930 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1338 | 1836 | -498 | 73 | 914 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1335 | 1836 | -501 | 73 | 911 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1327 | 1836 | -509 | 72 | 907 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 902 | 1248 | -347 | 72 | 368 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 902 | 1248 | -347 | 72 | 368 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1321 | 1836 | -515 | 72 | 902 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1318 | 1836 | -518 | 72 | 899 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 896 | 1248 | -353 | 72 | 366 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1303 | 1836 | -533 | 71 | 889 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1294 | 1836 | -542 | 70 | 881 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1287 | 1836 | -549 | 70 | 877 | AC

## 2130
Detailed results
Generated at: | 08/03/2026 22:45:58
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2904
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 24 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 59 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 14 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 23 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 30 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 12 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 24 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 12 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 24 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 22 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 25 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 29 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 15 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 31 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 31 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 31 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 31 | 4 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 31 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 11 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 21 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 25 | 67 |  | 67 | 0 | FALSE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 9 |  | 9 | 0 | FALSE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 17 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 18 | 24 |  | 24 | 0 | FALSE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 13 |  | 13 | 0 | FALSE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 51 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 11 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 16 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 15 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 34 |  | 34 | 0 | FALSE | FALSE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 25 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1995 | 2000 | -5 | 100 | 1402 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1925 | 2000 | -75 | 96 | 1356 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1878 | 2000 | -122 | 94 | 1324 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1827 | 2000 | -173 | 91 | 1289 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1794 | 2000 | -206 | 90 | 1266 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1768 | 2000 | -232 | 88 | 1246 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1744 | 2000 | -256 | 87 | 1220 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1742 | 2000 | -258 | 87 | 1227 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1741 | 2000 | -259 | 87 | 1227 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1740 | 2000 | -260 | 87 | 1226 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1732 | 2000 | -268 | 87 | 1224 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1703 | 2000 | -297 | 85 | 1194 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1689 | 2000 | -311 | 84 | 1190 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1647 | 2000 | -353 | 82 | 1151 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1603 | 2000 | -397 | 80 | 1120 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1598 | 2000 | -402 | 80 | 1117 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 XVK_IS11 1 | 1514 | 2000 | -486 | 76 | 1067 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1502 | 2000 | -498 | 75 | 1044 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1502 | 2000 | -498 | 75 | -1027 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 749 | 999 | -250 | 75 | 276 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1492 | 2000 | -508 | 75 | 1039 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1492 | 2000 | -508 | 75 | -1019 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1331 | 1836 | -505 | 73 | 764 | AC no reactive limits

## 2230
Detailed results
Generated at: | 08/03/2026 22:45:58
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3403
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 24 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 53 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 28 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 14 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 22 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 29 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 23 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 23 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 21 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 24 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 29 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 15 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 21 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 25 | 67 |  | 67 | 0 | FALSE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 9 |  | 9 | 0 | FALSE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 17 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 18 | 24 |  | 24 | 0 | FALSE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 13 |  | 13 | 0 | FALSE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 11 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 50 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 11 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 16 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 34 |  | 34 | 0 | FALSE | FALSE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 24 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1993 | 2000 | -7 | 100 | 1402 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1932 | 2000 | -68 | 97 | 1361 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1881 | 2000 | -119 | 94 | 1325 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1838 | 2000 | -162 | 92 | 1296 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1821 | 2000 | -179 | 91 | 1285 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1805 | 2000 | -195 | 90 | 1261 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1796 | 2000 | -204 | 90 | 1265 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1795 | 2000 | -205 | 90 | 1267 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1775 | 2000 | -225 | 89 | 1250 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1774 | 2000 | -226 | 89 | 1250 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1773 | 2000 | -227 | 89 | 1249 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1766 | 2000 | -234 | 88 | 1237 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1750 | 2000 | -250 | 88 | 1233 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1703 | 2000 | -297 | 85 | 1186 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1650 | 2000 | -350 | 82 | 1142 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1650 | 2000 | -350 | 82 | -1122 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1615 | 2000 | -385 | 81 | 1127 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1608 | 2000 | -392 | 80 | 1123 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1465 | 1836 | -371 | 80 | 882 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1440 | 1836 | -396 | 78 | 881 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1432 | 1836 | -404 | 78 | 872 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1432 | 1836 | -404 | 78 | 872 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1411 | 1836 | -425 | 77 | 861 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1411 | 1836 | -425 | 77 | 861 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1393 | 1836 | -443 | 76 | 841 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1836 | -444 | 76 | 842 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1836 | -448 | 76 | 841 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1836 | -448 | 76 | 837 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1384 | 1836 | -452 | 75 | 836 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1375 | 1836 | -461 | 75 | 829 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1374 | 1836 | -462 | 75 | 827 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1357 | 1836 | -479 | 74 | 814 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 723 | 999 | -276 | 72 | 279 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 721 | 999 | -279 | 72 | 267 | AC

## 2330
Detailed results
Generated at: | 08/03/2026 22:45:58
Business day: | 2026-03-10
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3461
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 0 | 50 |  | 50 | 0 | TRUE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 54 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 2 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 0 | 1 |  | 10 | 0 | TRUE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 5 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 22 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 28 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 29 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 15 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 31 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 11 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 21 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 25 | 67 |  | 67 | 0 | FALSE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 9 |  | 9 | 0 | FALSE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 19 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 19 | 24 |  | 24 | 0 | FALSE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 9 | 13 |  | 13 | 0 | FALSE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 13 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 51 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 11 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 16 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 12 | 34 |  | 34 | 0 | FALSE | FALSE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 26 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 96 |  | 96 | 0 | TRUE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 58 |  | 58 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1404 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1929 | 2000 | -71 | 96 | 1360 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1877 | 2000 | -123 | 94 | 1323 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1821 | 2000 | -179 | 91 | 1284 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1817 | 2000 | -183 | 91 | 1283 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1807 | 2000 | -193 | 90 | 1264 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1797 | 2000 | -203 | 90 | 1271 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1793 | 2000 | -207 | 90 | 1264 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1778 | 2000 | -222 | 89 | 1254 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1778 | 2000 | -222 | 89 | 1253 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1777 | 2000 | -223 | 89 | 1253 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1769 | 2000 | -231 | 88 | 1240 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1752 | 2000 | -248 | 88 | 1235 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1704 | 2000 | -296 | 85 | 1189 | AC no reactive limits
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1676 | 2000 | -324 | 84 | -1140 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1676 | 2000 | -324 | 84 | 1162 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1664 | 2000 | -336 | 83 | 1155 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1664 | 2000 | -336 | 83 | -1131 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1490 | 1836 | -346 | 81 | 906 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1610 | 2000 | -390 | 80 | 1124 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1475 | 1836 | -361 | 80 | 911 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1602 | 2000 | -398 | 80 | 1120 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1460 | 1836 | -376 | 80 | 898 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1460 | 1836 | -376 | 80 | 898 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1444 | 1836 | -392 | 79 | 889 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1444 | 1836 | -392 | 79 | 889 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1424 | 1836 | -412 | 78 | 869 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1423 | 1836 | -413 | 78 | 871 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1420 | 1836 | -416 | 77 | 869 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1836 | -418 | 77 | 865 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1414 | 1836 | -422 | 77 | 863 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1411 | 1836 | -425 | 77 | 859 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1406 | 1836 | -430 | 77 | 857 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1385 | 1836 | -451 | 75 | 840 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 746 | 999 | -253 | 75 | 277 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 900 | 1248 | -348 | 72 | 361 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 900 | 1248 | -348 | 72 | 361 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 898 | 1248 | -351 | 72 | 360 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 898 | 1248 | -351 | 72 | 360 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 894 | 1248 | -354 | 72 | 359 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 894 | 1248 | -354 | 72 | 359 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 705 | 999 | -294 | 71 | 272 | AC