## 0030
Detailed results
Generated at: | 14/03/2026 21:58:04
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3307
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 12 |  | 313 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 52 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 14 |  | 14 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 0 | 118 |  | 118 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 0 | 45 |  | 45 | 0 | TRUE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 0 | 37 |  | 37 | 0 | TRUE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 0 | 46 |  | 46 | 0 | TRUE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 0 | 48 |  | 48 | 0 | TRUE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 0 | 39 |  | 39 | 0 | TRUE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 0 | 74 |  | 74 | 0 | TRUE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 0 | 45 |  | 45 | 0 | TRUE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 0 | 25 |  | 25 | 0 | TRUE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 4 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 3 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 2 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 4 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 4 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 4 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 4 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 4 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 19 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 15 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 16 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 7 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 47 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 13 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 217 | 57 |  | 217 | 0 | FALSE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 222 | 0 |  | 222 | 0 | FALSE | TRUE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 9 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 8 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 13 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1412 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1963 | 2000 | -37 | 98 | 1391 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1955 | 2000 | -45 | 98 | 1387 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1922 | 2000 | -78 | 96 | 1364 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1827 | 2000 | -173 | 91 | 1296 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1821 | 2000 | -179 | 91 | 1292 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1796 | 2000 | -204 | 90 | 1265 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1784 | 2000 | -216 | 89 | 1267 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1772 | 2000 | -228 | 89 | 1250 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1769 | 2000 | -231 | 88 | 1254 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1763 | 2000 | -237 | 88 | 1250 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1763 | 2000 | -237 | 88 | 1250 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1761 | 2000 | -239 | 88 | 1249 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1719 | 2000 | -281 | 86 | 1209 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1654 | 2000 | -346 | 83 | 1166 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1647 | 2000 | -353 | 82 | 1162 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1836 | -432 | 76 | 984 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 954 | 1248 | -295 | 76 | 390 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 954 | 1248 | -295 | 76 | 390 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 951 | 1248 | -297 | 76 | 389 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 951 | 1248 | -297 | 76 | 389 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 948 | 1248 | -301 | 76 | 387 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 948 | 1248 | -301 | 76 | 387 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1489 | 2000 | -511 | 74 | -1022 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1489 | 2000 | -511 | 74 | 1039 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1836 | -474 | 74 | 953 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1836 | -474 | 74 | 953 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1478 | 2000 | -522 | 74 | -1014 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1478 | 2000 | -522 | 74 | 1033 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1357 | 1836 | -479 | 74 | 950 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1357 | 1836 | -479 | 74 | 950 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1350 | 1836 | -486 | 74 | 946 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1344 | 1836 | -492 | 73 | 941 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1339 | 1836 | -497 | 73 | 937 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1316 | 1836 | -520 | 72 | 921 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 894 | 1248 | -355 | 72 | 365 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 894 | 1248 | -355 | 72 | 365 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1312 | 1836 | -524 | 71 | 918 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1311 | 1836 | -525 | 71 | 917 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1306 | 1836 | -530 | 71 | 914 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 888 | 1248 | -360 | 71 | 363 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1303 | 1836 | -533 | 71 | 911 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1287 | 1836 | -549 | 70 | 900 | AC

## 0130
Detailed results
Generated at: | 14/03/2026 21:58:04
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3454
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 105 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 51 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 14 |  | 14 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 0 | 118 |  | 118 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 0 | 45 |  | 45 | 0 | TRUE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 0 | 37 |  | 37 | 0 | TRUE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 0 | 46 |  | 46 | 0 | TRUE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 0 | 48 |  | 48 | 0 | TRUE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 0 | 39 |  | 39 | 0 | TRUE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 0 | 74 |  | 74 | 0 | TRUE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 0 | 45 |  | 45 | 0 | TRUE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 0 | 25 |  | 25 | 0 | TRUE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 4 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 3 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 2 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 4 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 4 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 4 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 4 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 4 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 19 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 15 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 15 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 7 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 46 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 13 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 36 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 222 | 0 |  | 222 | 0 | FALSE | TRUE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 9 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 8 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 13 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1413 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1961 | 2000 | -39 | 98 | 1390 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1942 | 2000 | -58 | 97 | 1378 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1916 | 2000 | -84 | 96 | 1360 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1835 | 2000 | -165 | 92 | 1302 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1829 | 2000 | -171 | 91 | 1297 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1822 | 2000 | -178 | 91 | 1283 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1811 | 2000 | -189 | 91 | 1286 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1798 | 2000 | -202 | 90 | 1269 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1788 | 2000 | -212 | 89 | 1267 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1785 | 2000 | -215 | 89 | 1265 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1780 | 2000 | -220 | 89 | 1262 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1778 | 2000 | -222 | 89 | 1261 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1741 | 2000 | -259 | 87 | 1224 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1652 | 2000 | -348 | 83 | 1164 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1645 | 2000 | -355 | 82 | 1160 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1574 | 2000 | -426 | 79 | 1098 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1574 | 2000 | -426 | 79 | -1079 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1563 | 2000 | -437 | 78 | -1070 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1563 | 2000 | -437 | 78 | 1092 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 971 | 1248 | -277 | 78 | 397 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 971 | 1248 | -277 | 78 | 397 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 969 | 1248 | -280 | 78 | 396 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 969 | 1248 | -280 | 78 | 396 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 965 | 1248 | -283 | 77 | 395 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 965 | 1248 | -283 | 77 | 395 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1416 | 1836 | -420 | 77 | 992 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1386 | 1836 | -450 | 75 | 969 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1386 | 1836 | -450 | 75 | 969 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1376 | 1836 | -460 | 75 | 963 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1376 | 1836 | -460 | 75 | 963 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1836 | -475 | 74 | 953 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1350 | 1836 | -486 | 74 | 944 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1350 | 1836 | -486 | 74 | 944 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1333 | 1836 | -503 | 73 | 932 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1330 | 1836 | -506 | 72 | 930 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1329 | 1836 | -507 | 72 | 929 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1325 | 1836 | -511 | 72 | 926 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1322 | 1836 | -514 | 72 | 924 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 896 | 1248 | -353 | 72 | 366 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 896 | 1248 | -353 | 72 | 366 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 890 | 1248 | -359 | 71 | 364 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1305 | 1836 | -531 | 71 | 912 | AC

## 0230
Detailed results
Generated at: | 14/03/2026 21:58:04
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3637
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 26 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 58 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 7 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 0 | 118 |  | 118 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 0 | 45 |  | 45 | 0 | TRUE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 0 | 48 |  | 48 | 0 | TRUE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 0 | 39 |  | 39 | 0 | TRUE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 0 | 29 |  | 38 | 0 | TRUE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 5 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 4 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 2 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 5 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 5 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 5 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 5 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 5 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 22 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 17 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 17 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 13 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 52 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 3 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 15 |  | 71 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 7 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 10 | 29 |  | 29 | 0 | FALSE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 9 | 27 |  | 27 | 0 | FALSE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 15 | 52 |  | 52 | 0 | FALSE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 2000 | 2000 | 0 | 100 | 1416 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1957 | 2000 | -43 | 98 | 1386 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1912 | 2000 | -88 | 96 | 1356 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1902 | 2000 | -98 | 95 | 1349 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1830 | 2000 | -170 | 91 | 1297 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1826 | 2000 | -174 | 91 | 1285 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1823 | 2000 | -177 | 91 | 1292 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1816 | 2000 | -184 | 91 | 1288 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1800 | 2000 | -200 | 90 | 1269 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1789 | 2000 | -211 | 89 | 1267 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1788 | 2000 | -212 | 89 | 1266 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1784 | 2000 | -216 | 89 | 1265 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1783 | 2000 | -217 | 89 | 1264 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1738 | 2000 | -262 | 87 | 1221 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1519 | 1836 | -317 | 83 | 1053 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 820 | 999 | -179 | 82 | 319 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1642 | 2000 | -358 | 82 | 1155 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1634 | 2000 | -366 | 82 | 1151 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1495 | 1836 | -341 | 81 | 1034 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1495 | 1836 | -341 | 81 | 1034 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1622 | 2000 | -378 | 81 | -1110 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1622 | 2000 | -378 | 81 | 1130 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1486 | 1836 | -350 | 81 | 1030 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1486 | 1836 | -350 | 81 | 1030 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1610 | 2000 | -390 | 80 | -1100 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1610 | 2000 | -390 | 80 | 1123 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1836 | -370 | 80 | 1015 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 993 | 1248 | -255 | 80 | 406 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 993 | 1248 | -255 | 80 | 406 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 991 | 1248 | -258 | 79 | 405 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 991 | 1248 | -258 | 79 | 405 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 987 | 1248 | -261 | 79 | 403 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 987 | 1248 | -261 | 79 | 403 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1449 | 1836 | -387 | 79 | 1002 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1444 | 1836 | -392 | 79 | 999 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1441 | 1836 | -395 | 79 | 997 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1441 | 1836 | -395 | 78 | 996 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1440 | 1836 | -396 | 78 | 996 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1435 | 1836 | -401 | 78 | 992 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1434 | 1836 | -402 | 78 | 992 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1410 | 1836 | -426 | 77 | 974 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 908 | 1248 | -341 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 908 | 1248 | -341 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 902 | 1248 | -347 | 72 | 368 | AC

## 0330
Detailed results
Generated at: | 14/03/2026 21:58:05
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3533
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 24 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 58 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 47 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 0 | 118 |  | 118 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 0 | 45 |  | 45 | 0 | TRUE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 0 | 37 |  | 37 | 0 | TRUE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 0 | 46 |  | 46 | 0 | TRUE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 0 | 48 |  | 48 | 0 | TRUE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 0 | 39 |  | 39 | 0 | TRUE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 0 | 74 |  | 74 | 0 | TRUE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 0 | 45 |  | 45 | 0 | TRUE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 0 | 25 |  | 25 | 0 | TRUE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 4 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 3 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 2 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 5 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 5 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 5 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 5 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 5 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 0 | 32 |  | 32 | 0 | TRUE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 0 | 49 |  | 49 | 0 | TRUE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 0 | 54 |  | 54 | 0 | TRUE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 20 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 15 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 16 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 7 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 48 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 13 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 3 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 222 | 0 |  | 222 | 0 | FALSE | TRUE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 10 | 25 |  | 29 | 0 | FALSE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 8 | 27 |  | 27 | 0 | FALSE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 14 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1997 | 2000 | -3 | 100 | 1413 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1962 | 2000 | -38 | 98 | 1388 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1934 | 2000 | -66 | 97 | 1370 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1893 | 2000 | -107 | 95 | 1341 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1844 | 2000 | -156 | 92 | 1307 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1833 | 2000 | -167 | 92 | 1289 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1832 | 2000 | -168 | 92 | 1298 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1822 | 2000 | -178 | 91 | 1292 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1809 | 2000 | -191 | 90 | 1275 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1800 | 2000 | -200 | 90 | 1273 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1799 | 2000 | -201 | 90 | 1273 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1796 | 2000 | -204 | 90 | 1271 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1795 | 2000 | -205 | 90 | 1271 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1737 | 2000 | -263 | 87 | 1220 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1652 | 2000 | -348 | 83 | 1161 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1645 | 2000 | -355 | 82 | 1157 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1012 | 1248 | -236 | 81 | 413 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1012 | 1248 | -236 | 81 | 413 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1010 | 1248 | -239 | 81 | 412 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1010 | 1248 | -239 | 81 | 412 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1613 | 2000 | -387 | 81 | 1123 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1613 | 2000 | -387 | 81 | -1103 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1006 | 1248 | -242 | 81 | 411 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1006 | 1248 | -242 | 81 | 411 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1601 | 2000 | -399 | 80 | -1094 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1601 | 2000 | -399 | 80 | 1117 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1458 | 1836 | -378 | 79 | 993 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1441 | 1836 | -395 | 78 | 980 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1441 | 1836 | -395 | 78 | 980 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1431 | 1836 | -405 | 78 | 974 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1431 | 1836 | -405 | 78 | 974 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1836 | -418 | 77 | 966 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1399 | 1836 | -437 | 76 | 950 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1390 | 1836 | -446 | 76 | 943 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1836 | -448 | 76 | 943 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1387 | 1836 | -449 | 76 | 942 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1387 | 1836 | -449 | 76 | 941 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1836 | -454 | 75 | 938 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1381 | 1836 | -455 | 75 | 937 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1359 | 1836 | -477 | 74 | 921 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 903 | 1248 | -345 | 72 | 369 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 903 | 1248 | -345 | 72 | 369 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 898 | 1248 | -351 | 72 | 367 | AC

## 0430
Detailed results
Generated at: | 14/03/2026 21:58:05
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3487
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 38 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 24 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 58 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 14 |  | 14 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 0 | 118 |  | 118 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 0 | 45 |  | 45 | 0 | TRUE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 0 | 37 |  | 37 | 0 | TRUE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 0 | 46 |  | 46 | 0 | TRUE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 0 | 48 |  | 48 | 0 | TRUE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 0 | 39 |  | 39 | 0 | TRUE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 0 | 38 |  | 38 | 0 | TRUE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 0 | 74 |  | 74 | 0 | TRUE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 0 | 45 |  | 45 | 0 | TRUE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 0 | 25 |  | 25 | 0 | TRUE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 4 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 3 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 2 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 5 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 5 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 5 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 5 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 5 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 20 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 15 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 16 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 7 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 48 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 13 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 125 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 222 | 0 |  | 222 | 0 | FALSE | TRUE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 10 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 8 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 14 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1411 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1966 | 2000 | -34 | 98 | 1392 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1956 | 2000 | -44 | 98 | 1386 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1923 | 2000 | -77 | 96 | 1362 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1845 | 2000 | -155 | 92 | 1308 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1838 | 2000 | -162 | 92 | 1302 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1834 | 2000 | -166 | 92 | 1289 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1821 | 2000 | -179 | 91 | 1292 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1812 | 2000 | -188 | 91 | 1277 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1802 | 2000 | -198 | 90 | 1275 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1793 | 2000 | -207 | 90 | 1269 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1788 | 2000 | -212 | 89 | 1266 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1786 | 2000 | -214 | 89 | 1265 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1754 | 2000 | -246 | 88 | 1232 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1660 | 2000 | -340 | 83 | 1168 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1653 | 2000 | -347 | 83 | 1164 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1587 | 2000 | -413 | 79 | 1104 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1587 | 2000 | -413 | 79 | -1085 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 987 | 1248 | -261 | 79 | 403 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 987 | 1248 | -261 | 79 | 403 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1836 | -388 | 79 | 987 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 985 | 1248 | -264 | 79 | 402 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 985 | 1248 | -264 | 79 | 402 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1575 | 2000 | -425 | 79 | 1098 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1575 | 2000 | -425 | 79 | -1076 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 981 | 1248 | -267 | 79 | 401 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 981 | 1248 | -267 | 79 | 401 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1836 | -410 | 78 | 969 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1836 | -410 | 78 | 969 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1410 | 1836 | -426 | 77 | 960 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1410 | 1836 | -426 | 77 | 960 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1836 | -441 | 76 | 949 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1373 | 1836 | -463 | 75 | 932 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1370 | 1836 | -466 | 75 | 929 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1836 | -471 | 74 | 926 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1836 | -471 | 74 | 926 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1360 | 1836 | -476 | 74 | 923 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1358 | 1836 | -478 | 74 | 921 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1343 | 1836 | -493 | 73 | 910 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 899 | 1248 | -350 | 72 | 367 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 899 | 1248 | -350 | 72 | 367 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 893 | 1248 | -355 | 72 | 365 | AC

## 0530
Detailed results
Generated at: | 14/03/2026 21:58:05
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3238
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1943 | 2000 | -57 | 97 | 1374 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1933 | 2000 | -67 | 97 | 1370 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1925 | 2000 | -75 | 96 | 1361 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1876 | 2000 | -124 | 94 | 1328 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1814 | 2000 | -186 | 91 | 1285 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1804 | 2000 | -196 | 90 | 1277 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1801 | 2000 | -199 | 90 | 1265 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1788 | 2000 | -212 | 89 | 1267 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1780 | 2000 | -220 | 89 | 1253 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1769 | 2000 | -231 | 88 | 1251 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1762 | 2000 | -238 | 88 | 1247 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1756 | 2000 | -244 | 88 | 1243 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1753 | 2000 | -247 | 88 | 1241 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1719 | 2000 | -281 | 86 | 1206 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1042 | 1248 | -207 | 83 | 426 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1042 | 1248 | -207 | 83 | 426 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1039 | 1248 | -209 | 83 | 424 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1039 | 1248 | -209 | 83 | 424 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1035 | 1248 | -213 | 83 | 423 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1035 | 1248 | -213 | 83 | 423 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1630 | 2000 | -370 | 82 | 1146 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1624 | 2000 | -376 | 81 | 1142 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1546 | 2000 | -454 | 77 | 1075 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1546 | 2000 | -454 | 77 | -1057 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1535 | 2000 | -465 | 77 | 1069 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1535 | 2000 | -465 | 77 | -1048 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1336 | 1836 | -500 | 73 | 908 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 900 | 1248 | -349 | 72 | 368 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 900 | 1248 | -349 | 72 | 368 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1320 | 1836 | -516 | 72 | 898 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1320 | 1836 | -516 | 72 | 898 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1318 | 1836 | -518 | 72 | 894 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1318 | 1836 | -518 | 72 | 894 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 894 | 1248 | -355 | 72 | 365 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1302 | 1836 | -534 | 71 | 885 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1288 | 1836 | -548 | 70 | 873 | AC

## 0630
Detailed results
Generated at: | 14/03/2026 21:58:05
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 2879
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1973 | 2000 | -27 | 99 | 1387 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1935 | 2000 | -65 | 97 | 1355 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1922 | 2000 | -78 | 96 | 1347 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1886 | 2000 | -114 | 94 | 1324 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1781 | 2000 | -219 | 89 | 1246 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1776 | 2000 | -224 | 89 | 1246 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1776 | 2000 | -224 | 89 | 1246 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1752 | 2000 | -248 | 88 | 1218 | AC no reactive limits
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1707 | 2000 | -293 | 85 | 1196 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1704 | 2000 | -296 | 85 | 1194 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1703 | 2000 | -297 | 85 | 1194 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1617 | 2000 | -383 | 81 | 1123 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1611 | 2000 | -389 | 81 | 1120 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1579 | 2000 | -421 | 79 | 1107 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1576 | 2000 | -424 | 79 | 1088 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 958 | 1248 | -291 | 77 | 391 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 958 | 1248 | -291 | 77 | 391 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 955 | 1248 | -293 | 77 | 390 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 955 | 1248 | -293 | 77 | 390 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 952 | 1248 | -297 | 76 | 389 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 952 | 1248 | -297 | 76 | 389 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 923 | 1248 | -325 | 74 | 377 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 923 | 1248 | -325 | 74 | 377 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 917 | 1248 | -331 | 73 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1298 | 1836 | -538 | 71 | 894 | AC

## 0730
Detailed results
Generated at: | 14/03/2026 21:58:05
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Fallback
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type

## 0830
Detailed results
Generated at: | 14/03/2026 21:58:05
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 449.32
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 220 kV Portile de Fier-Resita 1&2/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1242 | 1248 | -7 | 99 | 507 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1242 | 1248 | -7 | 99 | 507 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1240 | 1248 | -9 | 99 | 506 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1240 | 1248 | -9 | 99 | 506 | AC

## 0930
Detailed results
Generated at: | 14/03/2026 21:58:05
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 695.48
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1233 | 1248 | -16 | 99 | 503 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1233 | 1248 | -16 | 99 | 503 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1223 | 1248 | -26 | 98 | 499 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1223 | 1248 | -26 | 98 | 499 | AC

## 1030
Detailed results
Generated at: | 14/03/2026 21:58:05
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 871.81
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 220 kV Portile de Fier-Resita 1&2/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1241 | 1248 | -8 | 99 | 506 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1241 | 1248 | -8 | 99 | 506 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1234 | 1248 | -14 | 99 | 504 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1234 | 1248 | -14 | 99 | 504 | AC

## 1130
Detailed results
Generated at: | 14/03/2026 21:58:05
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 649.28
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 220 kV Portile de Fier-Resita 1&2/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1234 | 1248 | -15 | 99 | 503 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1234 | 1248 | -15 | 99 | 503 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1218 | 1248 | -30 | 98 | 497 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1218 | 1248 | -30 | 98 | 497 | AC

## 1230
Detailed results
Generated at: | 14/03/2026 21:58:05
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 346.26
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1254 | 1248 | 6 | 100 | 511 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1254 | 1248 | 6 | 100 | 511 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1227 | 1248 | -21 | 98 | 500 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1227 | 1248 | -21 | 98 | 500 | AC

## 1330
Detailed results
Generated at: | 14/03/2026 21:58:05
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 15.38
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 220 kV Portile de Fier-Resita 1&2/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1233 | 1248 | -15 | 99 | 503 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1233 | 1248 | -15 | 99 | 503 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1194 | 1248 | -55 | 96 | 487 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1194 | 1248 | -55 | 96 | 487 | AC

## 1430
Detailed results
Generated at: | 14/03/2026 21:58:06
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Fallback
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type

## 1530
Detailed results
Generated at: | 14/03/2026 21:58:06
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 2957
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 120 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 26 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 59 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 4 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 0 | 14 |  | 14 | 0 | TRUE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 0 | 15 |  | 15 | 0 | TRUE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 0 | 10 |  | 10 | 0 | TRUE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 0 | 10 |  | 10 | 0 | TRUE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 0 | 15 |  | 15 | 0 | TRUE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 0 | 12 |  | 12 | 0 | TRUE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 0 | 170 |  | 170 | 0 | TRUE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 1 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 1 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 1 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 1 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 1 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 1 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 1 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 1 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 11 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 15 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 22 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 17 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 17 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 13 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 51 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 16 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 43 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 96 |  | 96 | 0 | TRUE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 58 |  | 58 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1396 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1908 | 2000 | -92 | 95 | 1328 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1904 | 2000 | -96 | 95 | 1328 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1879 | 2000 | -121 | 94 | 1312 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1759 | 2000 | -241 | 88 | 1227 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1754 | 2000 | -246 | 88 | 1220 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1750 | 2000 | -250 | 88 | 1220 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1684 | 2000 | -316 | 84 | 1174 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1681 | 2000 | -319 | 84 | 1172 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1681 | 2000 | -319 | 84 | 1172 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1043 | 1248 | -206 | 84 | 426 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1043 | 1248 | -206 | 84 | 426 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1040 | 1248 | -208 | 83 | 425 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1040 | 1248 | -208 | 83 | 425 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1662 | 2000 | -338 | 83 | 1150 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1036 | 1248 | -212 | 83 | 423 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1036 | 1248 | -212 | 83 | 423 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1511 | 1836 | -325 | 82 | 1052 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1632 | 2000 | -368 | 82 | 1129 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1625 | 2000 | -375 | 81 | 1126 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 939 | 1248 | -309 | 75 | 384 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 939 | 1248 | -309 | 75 | 384 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 933 | 1248 | -315 | 75 | 381 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1475 | 2000 | -525 | 74 | 1007 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1454 | 2000 | -546 | 73 | 1011 | AC

## 1630
Detailed results
Generated at: | 14/03/2026 21:58:06
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2536
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 63 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 2 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 4 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 9 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 14 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 9 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 19 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 7 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 14 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 16 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 5 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 17 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 12 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 7 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 8 | 15 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 15 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 0 | 32 |  | 32 | 0 | TRUE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 22 | 67 |  | 67 | 0 | FALSE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 9 |  | 9 | 0 | FALSE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 17 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 17 | 24 |  | 24 | 0 | FALSE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 13 |  | 13 | 0 | FALSE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 13 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 50 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 0 | 30 |  | 30 | 0 | TRUE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 4 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 48 | 71 |  | 71 | 0 | FALSE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 0 | 96 |  | 96 | 0 | TRUE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 58 |  | 58 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1411 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1936 | 2000 | -64 | 97 | 1363 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1927 | 2000 | -73 | 96 | 1359 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1857 | 2000 | -143 | 93 | 1312 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1802 | 2000 | -198 | 90 | 1274 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1777 | 2000 | -223 | 89 | 1255 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1727 | 2000 | -273 | 86 | 1219 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1724 | 2000 | -276 | 86 | 1217 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1724 | 2000 | -276 | 86 | 1217 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1700 | 2000 | -300 | 85 | 1192 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1688 | 2000 | -312 | 84 | 1187 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1686 | 2000 | -314 | 84 | 1191 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1678 | 2000 | -322 | 84 | 1189 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1646 | 2000 | -354 | 82 | 1157 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1639 | 2000 | -361 | 82 | 1153 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1602 | 2000 | -398 | 80 | 1126 | AC

## 1730
Detailed results
Generated at: | 14/03/2026 21:58:06
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 2799
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 25 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 60 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 8 | 46 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 2 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 27 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 10 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 21 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 21 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 22 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 7 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 22 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 17 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 11 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 23 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 23 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 23 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 23 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 23 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 15 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 21 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 19 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 20 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 9 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 13 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 49 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 14 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 3 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 94 |  | 222 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1999 | 2000 | -1 | 100 | 1414 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1950 | 2000 | -50 | 98 | 1374 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1938 | 2000 | -62 | 97 | 1368 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1910 | 2000 | -90 | 96 | 1350 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1782 | 2000 | -218 | 89 | 1259 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1767 | 2000 | -233 | 88 | 1249 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1698 | 2000 | -302 | 85 | 1199 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1691 | 2000 | -309 | 85 | 1194 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1688 | 2000 | -312 | 84 | 1192 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1674 | 2000 | -326 | 84 | 1173 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1656 | 2000 | -344 | 83 | 1163 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1654 | 2000 | -346 | 83 | 1167 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1652 | 2000 | -348 | 83 | 1170 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1645 | 2000 | -355 | 82 | 1158 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1639 | 2000 | -361 | 82 | 1155 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1017 | 1248 | -232 | 81 | 415 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1017 | 1248 | -232 | 81 | 415 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1014 | 1248 | -234 | 81 | 414 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1014 | 1248 | -234 | 81 | 414 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1010 | 1248 | -238 | 81 | 412 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1010 | 1248 | -238 | 81 | 412 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1599 | 2000 | -401 | 80 | 1123 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 918 | 1248 | -330 | 74 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 918 | 1248 | -330 | 74 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 913 | 1248 | -336 | 73 | 372 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1324 | 1836 | -512 | 72 | 907 | AC

## 1830
Detailed results
Generated at: | 14/03/2026 21:58:06
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2387.74
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1987 | 2000 | -13 | 99 | 1405 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1958 | 2000 | -42 | 98 | 1377 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1938 | 2000 | -62 | 97 | 1366 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1893 | 2000 | -107 | 95 | 1337 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1779 | 2000 | -221 | 89 | 1257 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1759 | 2000 | -241 | 88 | 1242 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1694 | 2000 | -306 | 85 | 1195 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1685 | 2000 | -315 | 84 | 1189 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1681 | 2000 | -319 | 84 | 1186 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1666 | 2000 | -334 | 83 | 1167 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1645 | 2000 | -355 | 82 | 1165 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1642 | 2000 | -358 | 82 | 1153 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1642 | 2000 | -358 | 82 | 1152 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1637 | 2000 | -363 | 82 | 1155 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1636 | 2000 | -364 | 82 | 1150 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1005 | 1248 | -243 | 81 | 409 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1005 | 1248 | -243 | 81 | 409 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1003 | 1248 | -246 | 80 | 408 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1003 | 1248 | -246 | 80 | 408 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 999 | 1248 | -249 | 80 | 407 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 999 | 1248 | -249 | 80 | 407 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1573 | 2000 | -427 | 79 | 1106 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1417 | 1836 | -419 | 77 | 946 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1386 | 1836 | -450 | 75 | 936 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 914 | 1248 | -335 | 73 | 372 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 914 | 1248 | -335 | 73 | 372 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 908 | 1248 | -340 | 73 | 370 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1295 | 1836 | -541 | 71 | 861 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1288 | 1836 | -548 | 70 | 853 | AC

## 1930
Detailed results
Generated at: | 14/03/2026 21:58:06
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2613.76
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1992 | 2000 | -8 | 100 | 1410 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1969 | 2000 | -31 | 98 | 1388 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1950 | 2000 | -50 | 98 | 1377 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1909 | 2000 | -91 | 95 | 1350 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1810 | 2000 | -190 | 91 | 1280 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1792 | 2000 | -208 | 90 | 1267 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1731 | 2000 | -269 | 87 | 1223 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1731 | 2000 | -269 | 87 | 1213 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1723 | 2000 | -277 | 86 | 1217 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1719 | 2000 | -281 | 86 | 1214 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1712 | 2000 | -288 | 86 | 1213 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1707 | 2000 | -293 | 85 | 1200 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1701 | 2000 | -299 | 85 | 1202 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1657 | 2000 | -343 | 83 | 1165 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1650 | 2000 | -350 | 83 | 1161 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1645 | 2000 | -355 | 82 | 1154 | AC no reactive limits
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1022 | 1248 | -227 | 82 | 416 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1022 | 1248 | -227 | 82 | 416 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1019 | 1248 | -230 | 82 | 415 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1019 | 1248 | -230 | 82 | 415 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1015 | 1248 | -233 | 81 | 414 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1015 | 1248 | -233 | 81 | 414 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1484 | 1836 | -352 | 81 | 997 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1425 | 1836 | -411 | 78 | 965 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 915 | 1248 | -333 | 73 | 373 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 915 | 1248 | -333 | 73 | 373 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 909 | 1248 | -339 | 73 | 370 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1328 | 1836 | -508 | 72 | 878 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1319 | 1836 | -517 | 72 | 878 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1297 | 1836 | -539 | 71 | 860 | AC

## 2030
Detailed results
Generated at: | 14/03/2026 21:58:06
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 2654
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-1) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-1) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1978 | 2000 | -22 | 99 | 1401 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1912 | 2000 | -88 | 96 | 1350 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1910 | 2000 | -90 | 96 | 1351 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1872 | 2000 | -128 | 94 | 1326 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1785 | 2000 | -215 | 89 | 1264 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1772 | 2000 | -228 | 89 | 1254 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1718 | 2000 | -282 | 86 | 1206 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1709 | 2000 | -291 | 85 | 1209 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1700 | 2000 | -300 | 85 | 1203 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1700 | 2000 | -300 | 85 | 1196 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1700 | 2000 | -300 | 85 | 1205 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1696 | 2000 | -304 | 85 | 1200 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1695 | 2000 | -305 | 85 | 1199 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1650 | 2000 | -350 | 82 | 1158 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1630 | 2000 | -370 | 81 | 1148 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1623 | 2000 | -377 | 81 | 1144 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 957 | 1248 | -291 | 77 | 391 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 957 | 1248 | -291 | 77 | 391 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 955 | 1248 | -294 | 76 | 390 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 955 | 1248 | -294 | 76 | 390 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 951 | 1248 | -297 | 76 | 388 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 951 | 1248 | -297 | 76 | 388 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 894 | 1248 | -355 | 72 | 365 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 894 | 1248 | -355 | 72 | 365 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 888 | 1248 | -360 | 71 | 363 | AC

## 2130
Detailed results
Generated at: | 14/03/2026 21:58:06
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 2956
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 273 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 55 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 14 |  | 14 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 7 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 12 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 19 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 12 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 25 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 10 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 20 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 10 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 20 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 18 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 21 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 7 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 20 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 15 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 10 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 21 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 21 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 21 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 21 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 21 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 9 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 4 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 4 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 4 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 14 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 19 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 7 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 18 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 18 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 46 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 13 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 150 | 0 |  | 150 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 25 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 96 | 73 |  | 96 | 0 | FALSE | FALSE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 58 | 0 |  | 58 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1413 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1913 | 2000 | -87 | 96 | 1354 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1898 | 2000 | -102 | 95 | 1342 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1896 | 2000 | -104 | 95 | 1343 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1787 | 2000 | -213 | 89 | 1266 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1779 | 2000 | -221 | 89 | 1260 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1727 | 2000 | -273 | 86 | 1213 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1715 | 2000 | -285 | 86 | 1207 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1711 | 2000 | -289 | 86 | 1210 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1708 | 2000 | -292 | 85 | 1211 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1698 | 2000 | -302 | 85 | 1202 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1694 | 2000 | -306 | 85 | 1199 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1694 | 2000 | -306 | 85 | 1199 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1679 | 2000 | -321 | 84 | 1179 | AC no reactive limits
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1635 | 2000 | -365 | 82 | 1153 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1628 | 2000 | -372 | 81 | 1149 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1836 | -370 | 80 | 882 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1459 | 1836 | -377 | 79 | 846 | AC no reactive limits
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1436 | 1836 | -400 | 78 | 854 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1436 | 1836 | -400 | 78 | 854 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1422 | 1836 | -414 | 77 | 842 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 966 | 1248 | -283 | 77 | 388 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 966 | 1248 | -283 | 77 | 388 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 963 | 1248 | -285 | 77 | 387 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 963 | 1248 | -285 | 77 | 387 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 960 | 1248 | -289 | 77 | 386 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 960 | 1248 | -289 | 77 | 386 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1408 | 1836 | -428 | 77 | 837 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1408 | 1836 | -428 | 77 | 837 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1836 | -444 | 76 | 819 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1379 | 1836 | -457 | 75 | 810 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1378 | 1836 | -458 | 75 | 809 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1374 | 1836 | -462 | 75 | 805 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1373 | 1836 | -463 | 75 | 803 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1371 | 1836 | -465 | 75 | 803 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1836 | -468 | 74 | 800 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 899 | 1248 | -349 | 72 | 362 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 899 | 1248 | -349 | 72 | 362 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 894 | 1248 | -355 | 72 | 360 | AC

## 2230
Detailed results
Generated at: | 14/03/2026 21:58:06
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3216
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological_ra | BG | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00103 | TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 218 |  | 280 | 1 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 25 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 57 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 14 |  | 14 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 8 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 2 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 27 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 22 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 22 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 22 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 17 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 12 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 23 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 23 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 23 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 23 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 24 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 15 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 21 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 8 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 20 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 20 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 9 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 13 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 51 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 14 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 150 | 103 |  | 150 | 0 | FALSE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 27 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1996 | 2000 | -4 | 100 | 1412 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1930 | 2000 | -70 | 97 | 1363 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1919 | 2000 | -81 | 96 | 1354 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1903 | 2000 | -97 | 95 | 1346 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1809 | 2000 | -191 | 90 | 1279 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1800 | 2000 | -200 | 90 | 1272 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1760 | 2000 | -240 | 88 | 1233 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1748 | 2000 | -252 | 87 | 1228 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1742 | 2000 | -258 | 87 | 1230 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1741 | 2000 | -259 | 87 | 1232 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1734 | 2000 | -266 | 87 | 1225 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1727 | 2000 | -273 | 86 | 1220 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1724 | 2000 | -276 | 86 | 1218 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1706 | 2000 | -294 | 85 | 1196 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1555 | 1836 | -281 | 85 | 958 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1533 | 1836 | -303 | 84 | 937 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1533 | 1836 | -303 | 84 | 937 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1648 | 2000 | -352 | 82 | 1159 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1510 | 1836 | -326 | 82 | 924 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1641 | 2000 | -359 | 82 | 1154 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1836 | -331 | 82 | 921 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1836 | -331 | 82 | 921 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1502 | 1836 | -334 | 82 | 913 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1483 | 1836 | -353 | 81 | 899 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1482 | 1836 | -354 | 81 | 898 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1474 | 1836 | -362 | 80 | 893 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1473 | 1836 | -363 | 80 | 893 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1470 | 1836 | -366 | 80 | 890 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1468 | 1836 | -368 | 80 | 888 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 996 | 1248 | -253 | 80 | 400 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 996 | 1248 | -253 | 80 | 400 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 993 | 1248 | -255 | 80 | 399 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 993 | 1248 | -255 | 80 | 399 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1456 | 1836 | -380 | 79 | 878 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 990 | 1248 | -259 | 79 | 398 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 990 | 1248 | -259 | 79 | 398 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 914 | 1248 | -334 | 73 | 368 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 914 | 1248 | -334 | 73 | 368 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 908 | 1248 | -340 | 73 | 366 | AC

## 2330
Detailed results
Generated at: | 14/03/2026 21:58:07
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3318
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Constanta Nord- Cernavoda/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00105 | RO | RROVI31 _generator | 0 | 310 |  |  | 310 | 1 |  | 310 | 1 | FALSE | FALSE
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 295 | 174 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 313 | 1 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 280 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 389 | 34 |  | 389 | 0 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 25 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 55 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 14 |  | 14 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 7 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 12 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 19 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 12 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 25 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 10 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 20 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 10 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 20 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 18 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 21 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 7 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 22 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 16 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 11 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 4 | 59 |  | 59 | 0 | FALSE | FALSE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 2 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 2 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 2 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 6 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 0 | 32 |  | 32 | 0 | TRUE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 20 | 67 |  | 67 | 0 | FALSE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 9 |  | 9 | 0 | FALSE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 16 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 16 | 24 |  | 24 | 0 | FALSE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 13 |  | 13 | 0 | FALSE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 49 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 14 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 13 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 34 |  | 34 | 0 | FALSE | FALSE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 24 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 10 | 29 |  | 29 | 0 | FALSE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 8 | 27 |  | 27 | 0 | FALSE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 14 | 52 |  | 52 | 0 | FALSE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1409 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1935 | 2000 | -65 | 97 | 1365 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1924 | 2000 | -76 | 96 | 1356 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1864 | 2000 | -136 | 93 | 1320 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1856 | 2000 | -144 | 93 | 1300 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1853 | 2000 | -147 | 93 | 1308 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1847 | 2000 | -153 | 92 | 1298 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1843 | 2000 | -157 | 92 | 1302 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1842 | 2000 | -158 | 92 | 1303 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1839 | 2000 | -161 | 92 | 1299 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1809 | 2000 | -191 | 90 | 1276 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1805 | 2000 | -195 | 90 | 1274 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1803 | 2000 | -197 | 90 | 1273 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1765 | 2000 | -235 | 88 | 1236 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1663 | 2000 | -337 | 83 | 1165 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1654 | 2000 | -346 | 83 | 1160 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1624 | 2000 | -376 | 81 | -1104 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1624 | 2000 | -376 | 81 | 1124 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1609 | 2000 | -391 | 80 | 1116 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1609 | 2000 | -391 | 80 | -1093 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1437 | 1836 | -399 | 78 | 849 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1437 | 1836 | -399 | 78 | 849 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1419 | 1836 | -417 | 77 | 837 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1412 | 1836 | -424 | 77 | 828 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1409 | 1836 | -427 | 77 | 831 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1836 | -432 | 76 | 828 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1836 | -432 | 76 | 828 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1836 | -444 | 76 | 815 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1384 | 1836 | -452 | 75 | 806 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1384 | 1836 | -452 | 75 | 807 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1383 | 1836 | -453 | 75 | 807 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1836 | -454 | 75 | 805 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1376 | 1836 | -460 | 75 | 799 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1836 | -474 | 74 | 789 | AC