## 0030
Detailed results
Generated at: | 14/03/2026 22:04:42
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3421.7
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1835 | 1836 | -1 | 100 | -1269 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1835 | 1836 | -1 | 100 | -1269 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1742 | 1836 | -94 | 95 | -1203 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1742 | 1836 | -94 | 95 | -1203 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1741 | 1836 | -95 | 95 | -1202 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1719 | 1836 | -117 | 94 | -1187 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1719 | 1836 | -117 | 94 | -1187 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1717 | 1836 | -119 | 94 | -1186 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1714 | 1836 | -122 | 93 | -1184 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1703 | 1836 | -133 | 93 | -1175 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1639 | 1836 | -197 | 89 | -1130 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1617 | 1836 | -219 | 88 | -1114 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1616 | 1836 | -220 | 88 | -1114 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1590 | 1836 | -246 | 87 | -1092 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1561 | 1890 | -329 | 83 | 1111 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1561 | 1890 | -329 | 83 | 1111 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 785 | 960 | -175 | 82 | 317 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1561 | 1920 | -359 | 81 | -1083 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1561 | 1920 | -359 | 81 | -1083 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 739 | 999 | -261 | 74 | 282 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 687 | 960 | -273 | 72 | 277 | AC

## 0130
Detailed results
Generated at: | 14/03/2026 22:04:42
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3613.92
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1842 | 1836 | 6 | 100 | -1274 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1842 | 1836 | 6 | 100 | -1274 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1751 | 1836 | -85 | 95 | -1211 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1751 | 1836 | -85 | 95 | -1211 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1743 | 1836 | -93 | 95 | -1205 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1725 | 1836 | -111 | 94 | -1192 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1721 | 1836 | -115 | 94 | -1189 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1717 | 1836 | -119 | 94 | -1187 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1717 | 1836 | -119 | 94 | -1187 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1701 | 1836 | -135 | 93 | -1175 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1643 | 1836 | -193 | 90 | -1134 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1618 | 1836 | -218 | 88 | -1116 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1614 | 1836 | -222 | 88 | -1113 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1648 | 1890 | -242 | 87 | 1173 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1648 | 1890 | -242 | 87 | 1173 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1599 | 1836 | -237 | 87 | -1100 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1648 | 1920 | -272 | 86 | -1142 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1648 | 1920 | -272 | 86 | -1142 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 794 | 960 | -166 | 83 | 321 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 811 | 999 | -188 | 81 | 311 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 747 | 999 | -252 | 75 | 290 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 699 | 960 | -261 | 73 | 282 | AC

## 0230
Detailed results
Generated at: | 14/03/2026 22:04:42
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3826.74
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1801 | 1836 | -35 | 98 | -1230 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1801 | 1836 | -35 | 98 | -1230 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1789 | 1890 | -101 | 95 | 1273 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1789 | 1890 | -101 | 95 | 1273 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1789 | 1920 | -131 | 93 | -1236 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1789 | 1920 | -131 | 93 | -1236 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1706 | 1836 | -130 | 93 | -1165 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1706 | 1836 | -130 | 93 | -1165 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1692 | 1836 | -144 | 92 | -1154 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1670 | 1836 | -166 | 91 | -1138 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1668 | 1836 | -168 | 91 | -1137 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1664 | 1836 | -172 | 91 | -1134 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1663 | 1836 | -173 | 91 | -1134 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1647 | 1836 | -189 | 90 | -1122 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 840 | 960 | -120 | 87 | 339 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1588 | 1836 | -248 | 87 | -1080 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1563 | 1836 | -273 | 85 | -1062 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1556 | 1836 | -280 | 85 | -1056 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 846 | 999 | -153 | 85 | 323 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1546 | 1836 | -290 | 84 | -1047 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 774 | 999 | -225 | 77 | 300 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 732 | 960 | -228 | 76 | 295 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 707 | 999 | -292 | 71 | 262 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1332 | 1890 | -558 | 70 | 948 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1332 | 1890 | -558 | 70 | 948 | AC

## 0330
Detailed results
Generated at: | 14/03/2026 22:04:42
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3875.72
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1754 | 1836 | -82 | 96 | -1182 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1754 | 1836 | -82 | 96 | -1182 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1797 | 1890 | -93 | 95 | 1278 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1797 | 1890 | -93 | 95 | 1278 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1797 | 1920 | -123 | 94 | -1241 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1797 | 1920 | -123 | 94 | -1241 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 897 | 960 | -63 | 93 | 360 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1670 | 1836 | -166 | 91 | -1125 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1670 | 1836 | -166 | 91 | -1125 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1644 | 1836 | -192 | 90 | -1104 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1627 | 1836 | -209 | 89 | -1092 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1624 | 1836 | -212 | 88 | -1090 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1622 | 1836 | -214 | 88 | -1088 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1601 | 1836 | -235 | 87 | -1074 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1601 | 1836 | -235 | 87 | -1073 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 862 | 999 | -137 | 86 | 331 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1539 | 1836 | -297 | 84 | -1029 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1506 | 1836 | -330 | 82 | -1003 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 769 | 960 | -191 | 80 | 308 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 799 | 999 | -200 | 80 | 311 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 717 | 999 | -282 | 72 | 267 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1327 | 1890 | -563 | 70 | 944 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1327 | 1890 | -563 | 70 | 944 | AC

## 0430
Detailed results
Generated at: | 14/03/2026 22:04:42
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3861.8
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1779 | 1836 | -57 | 97 | -1201 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1779 | 1836 | -57 | 97 | -1201 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1767 | 1890 | -123 | 94 | 1258 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1767 | 1890 | -123 | 94 | 1258 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 896 | 960 | -64 | 93 | 360 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1700 | 1836 | -136 | 93 | -1148 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1700 | 1836 | -136 | 93 | -1148 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1767 | 1920 | -153 | 92 | -1222 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1767 | 1920 | -153 | 92 | -1222 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1674 | 1836 | -162 | 91 | -1127 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1655 | 1836 | -181 | 90 | -1114 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1655 | 1836 | -181 | 90 | -1113 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1652 | 1836 | -184 | 90 | -1111 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 897 | 999 | -102 | 90 | 342 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1629 | 1836 | -207 | 89 | -1095 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1628 | 1836 | -208 | 89 | -1094 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1574 | 1836 | -262 | 86 | -1056 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1545 | 1836 | -291 | 84 | -1033 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1545 | 1836 | -291 | 84 | -1035 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 833 | 999 | -167 | 83 | 322 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1529 | 1836 | -307 | 83 | -1023 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 774 | 960 | -186 | 81 | 310 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 742 | 999 | -257 | 74 | 277 | AC

## 0530
Detailed results
Generated at: | 14/03/2026 22:04:42
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3869.44
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1837 | 1836 | 1 | 100 | -1241 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1837 | 1836 | 1 | 100 | -1241 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1750 | 1836 | -86 | 95 | -1181 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1750 | 1836 | -86 | 95 | -1181 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1733 | 1836 | -103 | 94 | -1169 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1772 | 1890 | -118 | 94 | 1261 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1772 | 1890 | -118 | 94 | 1261 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1710 | 1836 | -126 | 93 | -1152 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1708 | 1836 | -128 | 93 | -1151 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1705 | 1836 | -131 | 93 | -1148 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1704 | 1836 | -132 | 93 | -1148 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1772 | 1920 | -148 | 92 | -1226 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1772 | 1920 | -148 | 92 | -1226 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1685 | 1836 | -151 | 92 | -1134 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1633 | 1836 | -203 | 89 | -1097 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1606 | 1836 | -230 | 87 | -1076 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1605 | 1836 | -231 | 87 | -1077 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 839 | 960 | -121 | 87 | 339 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1594 | 1836 | -242 | 87 | -1069 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 818 | 999 | -181 | 82 | 319 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 736 | 960 | -224 | 77 | 297 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 760 | 999 | -239 | 76 | 298 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1323 | 1890 | -567 | 70 | 942 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1323 | 1890 | -567 | 70 | 942 | AC

## 0630
Detailed results
Generated at: | 14/03/2026 22:04:42
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3675.88
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1839 | 1836 | 3 | 100 | -1258 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1839 | 1836 | 3 | 100 | -1258 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1745 | 1836 | -91 | 95 | -1192 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1745 | 1836 | -91 | 95 | -1192 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1742 | 1836 | -94 | 95 | -1190 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1716 | 1836 | -120 | 93 | -1172 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1713 | 1836 | -123 | 93 | -1170 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1711 | 1836 | -125 | 93 | -1168 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 894 | 960 | -66 | 93 | 361 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1704 | 1836 | -132 | 93 | -1163 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1697 | 1836 | -139 | 92 | -1158 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1636 | 1836 | -200 | 89 | -1101 | AC no reactive limits
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1672 | 1890 | -218 | 88 | 1190 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1672 | 1890 | -218 | 88 | 1190 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1620 | 1836 | -216 | 88 | -1102 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1608 | 1836 | -228 | 88 | -1095 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1600 | 1836 | -236 | 87 | -1089 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1672 | 1920 | -248 | 87 | -1158 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1672 | 1920 | -248 | 87 | -1158 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 783 | 960 | -177 | 82 | 315 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 768 | 960 | -192 | 80 | 309 | AC
RO_CO_00032 | N-1 OHL 220 kV Urechesti-Targu Jiu Nord | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 760 | 960 | -200 | 79 | 306 | AC
RO_CO_00033 | N-1 OHL 220 kV Paroseni-Targu Jiu Nord | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 759 | 960 | -201 | 79 | 306 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 750 | 960 | -210 | 78 | 302 | AC
RO_CO_00026 | N-1 TRA 400/220 kV AT Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 725 | 960 | -235 | 76 | 292 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 686 | 960 | -274 | 71 | 275 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 710 | 999 | -289 | 71 | 276 | AC

## 0730
Detailed results
Generated at: | 14/03/2026 22:04:42
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3243.14
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1839 | 1836 | 3 | 100 | -1266 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1839 | 1836 | 3 | 100 | -1266 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1832 | 1836 | -4 | 100 | -1268 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1793 | 1836 | -43 | 98 | -1234 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1768 | 1836 | -68 | 96 | -1217 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1767 | 1836 | -69 | 96 | -1216 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1766 | 1836 | -70 | 96 | -1215 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1764 | 1836 | -72 | 96 | -1214 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1756 | 1836 | -80 | 96 | -1209 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1703 | 1836 | -133 | 93 | -1171 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1686 | 1836 | -150 | 92 | -1159 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1685 | 1836 | -151 | 92 | -1158 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1681 | 1836 | -155 | 92 | -1155 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 866 | 960 | -94 | 90 | 347 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1695 | 1890 | -195 | 90 | 1203 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1695 | 1890 | -195 | 90 | 1203 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1695 | 1920 | -225 | 88 | -1170 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1695 | 1920 | -225 | 88 | -1170 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 767 | 960 | -193 | 80 | 306 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 745 | 960 | -215 | 78 | 297 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 730 | 960 | -230 | 76 | 291 | AC
RO_CO_00026 | N-1 TRA 400/220 kV AT Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 696 | 960 | -264 | 73 | 278 | AC

## 0830
Detailed results
Generated at: | 14/03/2026 22:04:43
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3404.76
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1837 | 1836 | 1 | 100 | -1266 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1837 | 1836 | 1 | 100 | -1266 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1798 | 1836 | -38 | 98 | -1245 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1770 | 1836 | -66 | 96 | -1220 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1815 | 1890 | -75 | 96 | 1287 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1815 | 1890 | -75 | 96 | 1287 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1757 | 1836 | -79 | 96 | -1210 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1755 | 1836 | -81 | 96 | -1209 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1749 | 1836 | -87 | 95 | -1205 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1749 | 1836 | -87 | 95 | -1205 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1747 | 1836 | -89 | 95 | -1203 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 912 | 960 | -48 | 95 | 364 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1815 | 1920 | -105 | 95 | -1249 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1815 | 1920 | -105 | 95 | -1249 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1682 | 1836 | -154 | 92 | -1157 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1677 | 1836 | -159 | 91 | -1154 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1671 | 1836 | -165 | 91 | -1149 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1670 | 1836 | -166 | 91 | -1149 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 793 | 960 | -167 | 83 | 316 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 781 | 960 | -179 | 81 | 311 | AC
RO_CO_00032 | N-1 OHL 220 kV Urechesti-Targu Jiu Nord | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 771 | 960 | -189 | 80 | 307 | AC
RO_CO_00033 | N-1 OHL 220 kV Paroseni-Targu Jiu Nord | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 771 | 960 | -189 | 80 | 307 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 757 | 960 | -203 | 79 | 301 | AC
RO_CO_00026 | N-1 TRA 400/220 kV AT Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 736 | 960 | -224 | 77 | 293 | AC

## 0930
Detailed results
Generated at: | 14/03/2026 22:04:43
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3155
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 9 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 6 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 10 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 6 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 13 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 6 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 10 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 5 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 10 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 10 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 11 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 4 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 1 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 1 | 18 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 1 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 8 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 4 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 16 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 26 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 12 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 16 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 5 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 12 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 6 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 41 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 10 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 8 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 9 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1337 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1337 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1885 | 1920 | -35 | 98 | -1296 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1885 | 1920 | -35 | 98 | -1296 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 898 | 960 | -62 | 94 | 359 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 762 | 960 | -198 | 79 | 303 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 742 | 960 | -218 | 77 | 295 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1836 | -432 | 76 | -953 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1836 | -432 | 76 | -953 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 712 | 960 | -248 | 74 | 283 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1344 | 1836 | -492 | 73 | -919 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1329 | 1836 | -507 | 72 | -900 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1318 | 1836 | -518 | 72 | -892 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1314 | 1836 | -522 | 72 | -889 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1313 | 1836 | -523 | 72 | -888 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1306 | 1836 | -530 | 71 | -884 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1302 | 1836 | -534 | 71 | -881 | AC

## 1030
Detailed results
Generated at: | 14/03/2026 22:04:43
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3044
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 9 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 1 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 1 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 1 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 1 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 1 | 23 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 5 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 2 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 15 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 26 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 8 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 16 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 5 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 13 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 6 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 42 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 10 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 8 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 9 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1337 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1337 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1885 | 1920 | -35 | 98 | -1296 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1885 | 1920 | -35 | 98 | -1296 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 874 | 960 | -86 | 91 | 350 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 710 | 960 | -250 | 74 | 283 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1316 | 1836 | -520 | 72 | -886 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1316 | 1836 | -520 | 72 | -886 | AC

## 1130
Detailed results
Generated at: | 14/03/2026 22:04:43
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2844
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 9 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 1 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 1 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 1 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 1 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 1 | 20 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 5 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 2 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 15 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 25 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 8 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 16 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 5 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 12 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 6 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 41 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 10 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 8 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 9 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1339 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1339 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1885 | 1920 | -35 | 98 | -1298 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1885 | 1920 | -35 | 98 | -1298 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 832 | 960 | -128 | 87 | 333 | AC

## 1230
Detailed results
Generated at: | 14/03/2026 22:04:43
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2656
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 8 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 1 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 1 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 1 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 1 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 1 | 3 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 5 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 2 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 13 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 22 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 7 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 15 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 4 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 12 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 5 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 39 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 10 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 8 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 8 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1341 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1341 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1885 | 1920 | -35 | 98 | -1301 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1885 | 1920 | -35 | 98 | -1301 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 790 | 960 | -170 | 82 | 316 | AC

## 1330
Detailed results
Generated at: | 14/03/2026 22:04:43
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2598
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 51 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 7 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 1 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 1 | 18 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 1 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 1 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 5 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 2 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 12 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 20 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 7 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 15 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 4 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 11 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 12 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 5 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 39 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 10 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 8 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 8 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1343 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1343 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1885 | 1920 | -35 | 98 | -1303 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1885 | 1920 | -35 | 98 | -1303 | AC

## 1430
Detailed results
Generated at: | 14/03/2026 22:04:43
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2612
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 24 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 54 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 6 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 1 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 1 | 47 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 1 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 1 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 1 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 5 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 2 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 11 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 18 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 8 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 20 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 15 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 16 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 7 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 43 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 10 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 8 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 7 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1345 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1885 | 1890 | -5 | 100 | 1345 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1885 | 1920 | -35 | 98 | -1304 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1885 | 1920 | -35 | 98 | -1304 | AC

## 1530
Detailed results
Generated at: | 14/03/2026 22:04:43
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3199.02
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1812 | 1890 | -78 | 96 | 1290 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1812 | 1890 | -78 | 96 | 1290 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1812 | 1920 | -108 | 94 | -1253 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1812 | 1920 | -108 | 94 | -1253 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 844 | 960 | -116 | 88 | 339 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1836 | -306 | 83 | -1035 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1836 | -306 | 83 | -1035 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1472 | 1836 | -364 | 80 | -1008 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1471 | 1836 | -365 | 80 | -994 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1449 | 1836 | -387 | 79 | -978 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1447 | 1836 | -389 | 79 | -977 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1836 | -393 | 79 | -974 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1438 | 1836 | -398 | 78 | -970 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1434 | 1836 | -402 | 78 | -967 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1373 | 1836 | -463 | 75 | -923 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1836 | -468 | 75 | -920 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 715 | 960 | -245 | 74 | 286 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1366 | 1836 | -470 | 74 | -918 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 710 | 960 | -250 | 74 | 284 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1329 | 1836 | -507 | 72 | -891 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 688 | 960 | -272 | 72 | 275 | AC

## 1630
Detailed results
Generated at: | 14/03/2026 22:04:43
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3679.66
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 946 | 960 | -14 | 99 | 379 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1822 | 1890 | -68 | 96 | 1295 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1822 | 1890 | -68 | 96 | 1295 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1822 | 1920 | -98 | 95 | -1257 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1822 | 1920 | -98 | 95 | -1257 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1590 | 1836 | -246 | 87 | -1109 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1556 | 1836 | -280 | 85 | -1074 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1556 | 1836 | -280 | 85 | -1074 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 808 | 960 | -152 | 84 | 322 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1509 | 1836 | -327 | 82 | -1041 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1836 | -351 | 81 | -1024 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1483 | 1836 | -353 | 81 | -1023 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1469 | 1836 | -367 | 80 | -1013 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1467 | 1836 | -369 | 80 | -1012 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1836 | -370 | 80 | -1011 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1836 | -418 | 77 | -978 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1400 | 1836 | -436 | 76 | -964 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1836 | -454 | 75 | -952 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1355 | 1836 | -481 | 74 | -933 | AC

## 1730
Detailed results
Generated at: | 14/03/2026 22:04:44
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3805.44
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1822 | 1890 | -68 | 96 | 1293 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1822 | 1890 | -68 | 96 | 1293 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1762 | 1836 | -74 | 96 | -1211 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1822 | 1920 | -98 | 95 | -1255 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1822 | 1920 | -98 | 95 | -1255 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1706 | 1836 | -130 | 93 | -1158 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1706 | 1836 | -130 | 93 | -1158 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1661 | 1836 | -175 | 90 | -1127 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1632 | 1836 | -204 | 89 | -1107 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1630 | 1836 | -206 | 89 | -1106 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1619 | 1836 | -217 | 88 | -1097 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1615 | 1836 | -221 | 88 | -1095 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1612 | 1836 | -224 | 88 | -1093 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1592 | 1836 | -244 | 87 | -1078 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1544 | 1836 | -292 | 84 | -1045 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1520 | 1836 | -316 | 83 | -1029 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1519 | 1836 | -317 | 83 | -1016 | AC no reactive limits

## 1830
Detailed results
Generated at: | 14/03/2026 22:04:44
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3571
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00105 | RO | RROVI31 _generator | 0 | 310 |  |  | 45 | 310 |  | 310 | 1 | FALSE | FALSE
RO_RA_00107 | RO | RTURC11 _generator | 0 | 302 |  |  | 42 | 302 |  | 302 | 1 | FALSE | FALSE
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 47 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 50 | 127 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 45 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 64 | 488 |  | 580 | 0 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 56 | 0 |  | 389 | 0 | FALSE | TRUE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 50 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 62 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 8 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 5 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 2 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 4 | 0 |  | 170 | 0 | FALSE | TRUE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 4 | 0 |  | 340 | 0 | FALSE | TRUE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 11 | 0 |  | 118 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 28 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 17 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 12 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 15 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 13 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 21 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 8 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 20 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 21 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 9 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 14 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 52 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 14 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 14 | 0 |  | 217 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 71 | 0 |  | 71 | 0 | FALSE | TRUE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 9 | 0 |  | 96 | 0 | FALSE | TRUE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 5 | 0 |  | 58 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1830 | 1836 | -6 | 100 | -1235 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1830 | 1836 | -6 | 100 | -1235 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1755 | 1836 | -81 | 96 | -1181 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1730 | 1836 | -106 | 94 | -1169 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1730 | 1836 | -106 | 94 | -1169 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1729 | 1836 | -107 | 94 | -1160 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1725 | 1836 | -111 | 94 | -1157 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1717 | 1836 | -119 | 94 | -1153 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1712 | 1836 | -124 | 93 | -1145 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1710 | 1836 | -126 | 93 | -1145 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 917 | 999 | -82 | 92 | 368 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1670 | 1836 | -166 | 91 | -1113 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1621 | 1836 | -215 | 88 | -1078 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 832 | 960 | -128 | 87 | 331 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1581 | 1836 | -255 | 86 | -1059 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1571 | 1836 | -265 | 86 | -1051 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1512 | 1890 | -378 | 80 | 1080 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1512 | 1890 | -378 | 80 | 1080 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1512 | 1920 | -408 | 79 | -1054 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1512 | 1920 | -408 | 79 | -1054 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1365 | 1920 | -555 | 71 | 955 | AC

## 1930
Detailed results
Generated at: | 14/03/2026 22:04:44
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3613
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 580 |  | 580 | 0 | TRUE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 68 |  | 389 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 50 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 63 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 8 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 5 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 2 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 0 | 60 |  | 340 | 0 | TRUE | FALSE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 0 | 118 |  | 118 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 22 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 28 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 17 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 12 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 24 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 15 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 22 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 8 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 20 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 21 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 10 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 14 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 52 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 15 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 71 | 0 |  | 71 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1830 | 1836 | -6 | 100 | -1242 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1830 | 1836 | -6 | 100 | -1242 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1756 | 1836 | -80 | 96 | -1180 | AC no reactive limits
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1737 | 1836 | -99 | 95 | -1165 | AC no reactive limits
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1733 | 1836 | -103 | 94 | -1163 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1731 | 1836 | -105 | 94 | -1173 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1731 | 1836 | -105 | 94 | -1173 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1729 | 1836 | -107 | 94 | -1159 | AC no reactive limits
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1713 | 1836 | -123 | 93 | -1155 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1704 | 1836 | -132 | 93 | -1144 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1676 | 1836 | -160 | 91 | -1123 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1643 | 1836 | -193 | 89 | -1088 | AC no reactive limits
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1575 | 1836 | -261 | 86 | -1062 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1617 | 1890 | -273 | 86 | 1155 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1617 | 1890 | -273 | 86 | 1155 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1566 | 1836 | -270 | 85 | -1053 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1630 | 1920 | -290 | 85 | 1144 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1617 | 1920 | -303 | 84 | -1125 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1617 | 1920 | -303 | 84 | -1125 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 806 | 960 | -154 | 84 | 321 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1385 | 1920 | -535 | 72 | 974 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1351 | 1920 | -569 | 70 | 944 | AC

## 2030
Detailed results
Generated at: | 14/03/2026 22:04:44
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3307
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00105 | RO | RROVI31 _generator | 0 | 310 |  |  | 3 | 310 |  | 310 | 1 | FALSE | FALSE
RO_RA_00107 | RO | RTURC11 _generator | 0 | 302 |  |  | 3 | 302 |  | 302 | 1 | FALSE | FALSE
RO_RA_00111 | RO | RBRAZ41 _generator | 0 | 295 |  |  | 4 | 1 |  | 295 | 1 | FALSE | FALSE
RO_RA_00112 | RO | RBRZ241 _generator | 0 | 313 |  |  | 4 | 82 |  | 313 | 1 | FALSE | FALSE
RO_RA_00113 | RO | RBRAZ22 _generator | 0 | 280 |  |  | 3 | 1 |  | 280 | 1 | FALSE | FALSE
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 5 | 105 |  | 580 | 0 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 5 | 0 |  | 389 | 0 | FALSE | TRUE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 50 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 61 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 8 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 2 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 6 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 0 | 0 |  | 170 | 0 | FALSE | TRUE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 1 | 0 |  | 340 | 0 | FALSE | TRUE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 1 | 0 |  | 118 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 27 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 10 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 7 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 22 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 17 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 12 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 15 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 1 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 21 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 8 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 19 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 20 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 9 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 13 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 7 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 51 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 14 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 1 | 0 |  | 150 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 27 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 1 | 0 |  | 96 | 0 | FALSE | TRUE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 0 | 0 |  | 58 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1831 | 1836 | -5 | 100 | -1239 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1831 | 1836 | -5 | 100 | -1239 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1766 | 1836 | -70 | 96 | -1193 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1756 | 1836 | -80 | 96 | -1192 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1756 | 1836 | -80 | 96 | -1192 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1747 | 1836 | -89 | 95 | -1178 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1743 | 1836 | -93 | 95 | -1176 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1742 | 1836 | -94 | 95 | -1175 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1735 | 1836 | -101 | 94 | -1171 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1720 | 1836 | -116 | 94 | -1159 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1677 | 1836 | -159 | 91 | -1125 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1655 | 1836 | -181 | 90 | -1104 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1627 | 1836 | -209 | 89 | -1093 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1623 | 1836 | -213 | 88 | -1089 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1338 | 1890 | -552 | 71 | 956 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1338 | 1890 | -552 | 71 | 956 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 674 | 960 | -286 | 70 | 270 | AC

## 2130
Detailed results
Generated at: | 14/03/2026 22:04:44
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3342.69
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1847 | 1836 | 11 | 101 | -1132 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1847 | 1836 | 11 | 101 | -1132 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1783 | 1836 | -53 | 97 | -1086 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1783 | 1836 | -53 | 97 | -1086 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1773 | 1836 | -63 | 97 | -1077 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1756 | 1836 | -80 | 96 | -1064 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1754 | 1836 | -82 | 96 | -1063 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1752 | 1836 | -84 | 95 | -1061 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1748 | 1836 | -88 | 95 | -1059 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1729 | 1836 | -107 | 94 | -1044 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1716 | 1836 | -120 | 93 | -999 | AC no reactive limits
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1680 | 1836 | -156 | 92 | -1000 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1663 | 1836 | -173 | 91 | -995 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1653 | 1836 | -183 | 90 | -985 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 855 | 999 | -144 | 86 | 326 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 793 | 999 | -206 | 79 | 306 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1497 | 1890 | -393 | 79 | 1071 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1497 | 1890 | -393 | 79 | 1071 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 751 | 960 | -209 | 78 | 302 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1497 | 1920 | -423 | 78 | -1045 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1497 | 1920 | -423 | 78 | -1045 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 707 | 999 | -292 | 71 | 263 | AC

## 2230
Detailed results
Generated at: | 14/03/2026 22:04:44
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3244.47
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1844 | 1836 | 8 | 100 | -1129 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1844 | 1836 | 8 | 100 | -1129 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1777 | 1836 | -59 | 97 | -1079 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1777 | 1836 | -59 | 97 | -1079 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1769 | 1836 | -67 | 96 | -1072 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1755 | 1836 | -81 | 96 | -1061 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1753 | 1836 | -83 | 95 | -1060 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1748 | 1836 | -88 | 95 | -1057 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1748 | 1836 | -88 | 95 | -1055 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1732 | 1836 | -104 | 94 | -1043 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1671 | 1836 | -165 | 91 | -997 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1659 | 1836 | -177 | 90 | -988 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1657 | 1836 | -179 | 90 | -984 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1652 | 1836 | -184 | 90 | -976 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 802 | 999 | -197 | 80 | 304 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 753 | 960 | -207 | 78 | 304 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1445 | 1890 | -445 | 76 | 1029 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1445 | 1890 | -445 | 76 | 1029 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1445 | 1920 | -475 | 75 | -1005 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1445 | 1920 | -475 | 75 | -1005 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 738 | 999 | -262 | 74 | 283 | AC

## 2330
Detailed results
Generated at: | 14/03/2026 22:04:44
Business day: | 2026-03-16
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3215
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 251 |  | 580 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 25 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 55 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 7 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 0 | 170 |  | 170 | 0 | TRUE | FALSE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 0 | 292 |  | 340 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 12 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 19 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 25 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 10 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 20 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 10 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 20 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 18 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 21 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 7 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 22 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 16 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 11 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 23 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 4 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 2 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 2 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 2 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 6 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 20 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 6 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 16 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 16 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 8 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 12 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 6 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 49 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 10 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 14 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 11 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 24 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 10 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 8 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 14 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1831 | 1836 | -5 | 100 | -1111 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1831 | 1836 | -5 | 100 | -1111 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1770 | 1836 | -66 | 96 | -1052 | AC no reactive limits
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1763 | 1836 | -73 | 96 | -1045 | AC no reactive limits
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1747 | 1836 | -89 | 95 | -1055 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1747 | 1836 | -89 | 95 | -1055 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1740 | 1836 | -96 | 95 | -1041 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1736 | 1836 | -100 | 95 | -1039 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1733 | 1836 | -103 | 94 | -1035 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1721 | 1836 | -115 | 94 | -1026 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1668 | 1836 | -168 | 91 | -985 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1645 | 1836 | -191 | 90 | -966 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1635 | 1836 | -201 | 89 | -951 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1635 | 1836 | -201 | 89 | -960 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 819 | 999 | -181 | 82 | 310 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 759 | 960 | -201 | 79 | 306 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1445 | 1890 | -445 | 76 | 1028 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1445 | 1890 | -445 | 76 | 1028 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1445 | 1920 | -475 | 75 | -1004 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1445 | 1920 | -475 | 75 | -1004 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 746 | 999 | -253 | 75 | 286 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 683 | 960 | -277 | 71 | 275 | AC no reactive limits