## 1230Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3355
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 | 2000 | 2000 | -3 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1885 | 2000 | 2000 | -115 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1814 | 2000 | 2000 | -186 | 91 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1805 | 2000 | 2000 | -195 | 90 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1778 | 2000 | 2000 | -222 | 89 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1774 | -2000 | -2000 | -226 | 89 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1759 | 2000 | 2000 | -241 | 88 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1756 | -2000 | -2000 | -244 | 88 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1746 | 2000 | 2000 | -254 | 87 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1737 | 2000 | 2000 | -263 | 87 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1734 | 2000 | 2000 | -266 | 87 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1734 | 2000 | 2000 | -266 | 87 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1733 | 2000 | 2000 | -267 | 87 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1733 | 2000 | 2000 | -267 | 87 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1732 | 2000 | 2000 | -268 | 87 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1686 | 2000 | 2000 | -314 | 84 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1685 | 2000 | 2000 | -315 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1671 | 2000 | 2000 | -329 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1575 | 2000 | 2000 | -425 | 79 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -983 | -1248 | -1248 | -266 | 79 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -981 | -1248 | -1248 | -267 | 79 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -975 | -1248 | -1248 | -274 | 78 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -973 | -1248 | -1248 | -275 | 78 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1557 | 2000 | 2000 | -443 | 78 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -967 | -1248 | -1248 | -281 | 77 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -964 | -1248 | -1248 | -285 | 77 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -879 | -1248 | -1248 | -370 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -878 | -1248 | -1248 | -370 | 70 | []

## 1230Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3355
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 |  | 2000 | -3 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1885 |  | 2000 | -115 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1814 |  | 2000 | -186 | 91 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1805 |  | 2000 | -195 | 90 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1778 |  | 2000 | -222 | 89 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1774 |  | -2000 | -226 | 89 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1759 |  | 2000 | -241 | 88 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1756 |  | -2000 | -244 | 88 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1746 |  | 2000 | -254 | 87 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1737 |  | 2000 | -263 | 87 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1734 |  | 2000 | -266 | 87 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1734 |  | 2000 | -266 | 87 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1733 |  | 2000 | -267 | 87 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1733 |  | 2000 | -267 | 87 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1732 |  | 2000 | -268 | 87 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1686 |  | 2000 | -314 | 84 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1685 |  | 2000 | -315 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1671 |  | 2000 | -329 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1575 |  | 2000 | -425 | 79 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -983 |  | -1248 | -266 | 79 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -981 |  | -1248 | -267 | 79 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -975 |  | -1248 | -274 | 78 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -973 |  | -1248 | -275 | 78 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1557 |  | 2000 | -443 | 78 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -967 |  | -1248 | -281 | 77 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -964 |  | -1248 | -285 | 77 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -879 |  | -1248 | -370 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -878 |  | -1248 | -370 | 70 | []

## 1330Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3429
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1996 | 2000 | 2000 | -4 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1876 | 2000 | 2000 | -124 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1794 | 2000 | 2000 | -206 | 90 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1723 | 2000 | 2000 | -277 | 86 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1715 | 2000 | 2000 | -285 | 86 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1708 | 2000 | 2000 | -292 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1706 | 2000 | 2000 | -294 | 85 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1705 | 2000 | 2000 | -295 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1704 | 2000 | 2000 | -296 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1703 | 2000 | 2000 | -297 | 85 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1702 | 2000 | 2000 | -298 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1702 | 2000 | 2000 | -298 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1701 | -2000 | -2000 | -299 | 85 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1686 | 2000 | 2000 | -314 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1684 | -2000 | -2000 | -316 | 84 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1659 | 2000 | 2000 | -341 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1627 | 2000 | 2000 | -373 | 81 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1598 | 2000 | 2000 | -402 | 80 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -985 | -1248 | -1248 | -264 | 79 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -984 | -1248 | -1248 | -264 | 79 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -978 | -1248 | -1248 | -271 | 78 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -974 | -1248 | -1248 | -274 | 78 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -969 | -1248 | -1248 | -279 | 78 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1550 | 2000 | 2000 | -450 | 78 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -965 | -1248 | -1248 | -284 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1533 | 2000 | 2000 | -467 | 77 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1376 | -1836 | -1836 | -460 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -880 | -1248 | -1248 | -369 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -880 | -1248 | -1248 | -369 | 70 | []

## 1330Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3429
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1996 |  | 2000 | -4 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1876 |  | 2000 | -124 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1794 |  | 2000 | -206 | 90 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1723 |  | 2000 | -277 | 86 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1715 |  | 2000 | -285 | 86 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1708 |  | 2000 | -292 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1706 |  | 2000 | -294 | 85 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1705 |  | 2000 | -295 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1704 |  | 2000 | -296 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1703 |  | 2000 | -297 | 85 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1702 |  | 2000 | -298 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1702 |  | 2000 | -298 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1701 |  | -2000 | -299 | 85 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1686 |  | 2000 | -314 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1684 |  | -2000 | -316 | 84 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1659 |  | 2000 | -341 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1627 |  | 2000 | -373 | 81 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1598 |  | 2000 | -402 | 80 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -985 |  | -1248 | -264 | 79 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -984 |  | -1248 | -264 | 79 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -978 |  | -1248 | -271 | 78 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -974 |  | -1248 | -274 | 78 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -969 |  | -1248 | -279 | 78 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1550 |  | 2000 | -450 | 78 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -965 |  | -1248 | -284 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1533 |  | 2000 | -467 | 77 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1376 |  | -1836 | -460 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -880 |  | -1248 | -369 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -880 |  | -1248 | -369 | 70 | []

## 1430Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3441
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1999 | 2000 | 2000 | -1 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1878 | 2000 | 2000 | -122 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1791 | 2000 | 2000 | -209 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1565 | -1836 | -1836 | -271 | 85 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1703 | 2000 | 2000 | -297 | 85 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1694 | 2000 | 2000 | -306 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1692 | 2000 | 2000 | -308 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 | 2000 | 2000 | -309 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 | 2000 | 2000 | -309 | 85 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1689 | 2000 | 2000 | -311 | 84 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1689 | 2000 | 2000 | -311 | 84 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1664 | 2000 | 2000 | -336 | 83 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1657 | 2000 | 2000 | -343 | 83 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1631 | 2000 | 2000 | -369 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1628 | -2000 | -2000 | -372 | 81 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1614 | 2000 | 2000 | -386 | 81 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1611 | -2000 | -2000 | -389 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1603 | 2000 | 2000 | -397 | 80 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -964 | -1248 | -1248 | -285 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1543 | 2000 | 2000 | -457 | 77 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -963 | -1248 | -1248 | -286 | 77 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1537 | 2000 | 2000 | -463 | 77 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -957 | -1248 | -1248 | -291 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1527 | 2000 | 2000 | -473 | 76 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -951 | -1248 | -1248 | -298 | 76 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -948 | -1248 | -1248 | -301 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -942 | -1248 | -1248 | -307 | 75 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1342 | -1836 | -1836 | -494 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1307 | -1836 | -1836 | -529 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -884 | -1248 | -1248 | -365 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -884 | -1248 | -1248 | -365 | 71 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1298 | -1836 | -1836 | -538 | 71 | []

## 1430Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3441
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1999 |  | 2000 | -1 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1878 |  | 2000 | -122 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1791 |  | 2000 | -209 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1565 |  | -1836 | -271 | 85 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1703 |  | 2000 | -297 | 85 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1694 |  | 2000 | -306 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1692 |  | 2000 | -308 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 |  | 2000 | -309 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 |  | 2000 | -309 | 85 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1689 |  | 2000 | -311 | 84 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1689 |  | 2000 | -311 | 84 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1664 |  | 2000 | -336 | 83 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1657 |  | 2000 | -343 | 83 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1631 |  | 2000 | -369 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1628 |  | -2000 | -372 | 81 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1614 |  | 2000 | -386 | 81 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1611 |  | -2000 | -389 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1603 |  | 2000 | -397 | 80 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -964 |  | -1248 | -285 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1543 |  | 2000 | -457 | 77 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -963 |  | -1248 | -286 | 77 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1537 |  | 2000 | -463 | 77 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -957 |  | -1248 | -291 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1527 |  | 2000 | -473 | 76 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -951 |  | -1248 | -298 | 76 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -948 |  | -1248 | -301 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -942 |  | -1248 | -307 | 75 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1342 |  | -1836 | -494 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1307 |  | -1836 | -529 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -884 |  | -1248 | -365 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -884 |  | -1248 | -365 | 71 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1298 |  | -1836 | -538 | 71 | []

## 1530Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3108
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 2000 | 2000 | 2000 | 0 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1873 | 2000 | 2000 | -127 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1783 | 2000 | 2000 | -217 | 89 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1683 | 2000 | 2000 | -317 | 84 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1676 | 2000 | 2000 | -324 | 84 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1674 | 2000 | 2000 | -326 | 84 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1673 | 2000 | 2000 | -327 | 84 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1673 | 2000 | 2000 | -327 | 84 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1671 | 2000 | 2000 | -329 | 84 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1671 | 2000 | 2000 | -329 | 84 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1653 | 2000 | 2000 | -347 | 83 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1609 | 2000 | 2000 | -391 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1596 | 2000 | 2000 | -404 | 80 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1571 | 2000 | 2000 | -429 | 79 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1569 | -2000 | -2000 | -431 | 78 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1554 | 2000 | 2000 | -446 | 78 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1552 | -2000 | -2000 | -448 | 78 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1402 | -1836 | -1836 | -434 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1520 | 2000 | 2000 | -480 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1504 | 2000 | 2000 | -496 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -929 | -1248 | -1248 | -319 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -929 | -1248 | -1248 | -320 | 74 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1484 | 2000 | 2000 | -516 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -923 | -1248 | -1248 | -326 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -917 | -1248 | -1248 | -331 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -914 | -1248 | -1248 | -335 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -908 | -1248 | -1248 | -340 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -881 | -1248 | -1248 | -367 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -881 | -1248 | -1248 | -368 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3108
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 2000 |  | 2000 | 0 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1873 |  | 2000 | -127 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1783 |  | 2000 | -217 | 89 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1683 |  | 2000 | -317 | 84 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1676 |  | 2000 | -324 | 84 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1674 |  | 2000 | -326 | 84 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1673 |  | 2000 | -327 | 84 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1673 |  | 2000 | -327 | 84 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1671 |  | 2000 | -329 | 84 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1671 |  | 2000 | -329 | 84 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1653 |  | 2000 | -347 | 83 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1609 |  | 2000 | -391 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1596 |  | 2000 | -404 | 80 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1571 |  | 2000 | -429 | 79 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1569 |  | -2000 | -431 | 78 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1554 |  | 2000 | -446 | 78 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1552 |  | -2000 | -448 | 78 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1402 |  | -1836 | -434 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1520 |  | 2000 | -480 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1504 |  | 2000 | -496 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -929 |  | -1248 | -319 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -929 |  | -1248 | -320 | 74 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1484 |  | 2000 | -516 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -923 |  | -1248 | -326 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -917 |  | -1248 | -331 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -914 |  | -1248 | -335 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -908 |  | -1248 | -340 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -881 |  | -1248 | -367 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -881 |  | -1248 | -368 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2556
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 | 2000 | 2000 | -5 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1848 | 2000 | 2000 | -152 | 92 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1740 | 2000 | 2000 | -260 | 87 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1606 | 2000 | 2000 | -394 | 80 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1588 | 2000 | 2000 | -412 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1583 | 2000 | 2000 | -417 | 79 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1583 | 2000 | 2000 | -417 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1578 | 2000 | 2000 | -422 | 79 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1575 | 2000 | 2000 | -425 | 79 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1519 | 2000 | 2000 | -481 | 76 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1504 | 2000 | 2000 | -496 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1460 | 2000 | 2000 | -540 | 73 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1445 | 2000 | 2000 | -555 | 72 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1443 | 2000 | 2000 | -557 | 72 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1422 | 2000 | 2000 | -578 | 71 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1296 | -1836 | -1836 | -540 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -876 | -1248 | -1248 | -372 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -876 | -1248 | -1248 | -373 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2556
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 |  | 2000 | -5 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1848 |  | 2000 | -152 | 92 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1740 |  | 2000 | -260 | 87 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1606 |  | 2000 | -394 | 80 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1588 |  | 2000 | -412 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1583 |  | 2000 | -417 | 79 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1583 |  | 2000 | -417 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1578 |  | 2000 | -422 | 79 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1575 |  | 2000 | -425 | 79 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1519 |  | 2000 | -481 | 76 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1504 |  | 2000 | -496 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1460 |  | 2000 | -540 | 73 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1445 |  | 2000 | -555 | 72 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1443 |  | 2000 | -557 | 72 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1422 |  | 2000 | -578 | 71 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1296 |  | -1836 | -540 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -876 |  | -1248 | -372 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -876 |  | -1248 | -373 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2518
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 | 2000 | 2000 | -5 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1856 | 2000 | 2000 | -144 | 93 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1746 | 2000 | 2000 | -254 | 87 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1637 | 2000 | 2000 | -363 | 82 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1592 | 2000 | 2000 | -408 | 80 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1586 | 2000 | 2000 | -414 | 79 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1581 | 2000 | 2000 | -419 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1576 | 2000 | 2000 | -424 | 79 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1573 | 2000 | 2000 | -427 | 79 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1504 | 2000 | 2000 | -496 | 75 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1487 | 2000 | 2000 | -513 | 74 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1471 | 2000 | 2000 | -529 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1454 | 2000 | 2000 | -546 | 73 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1433 | 2000 | 2000 | -567 | 72 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1412 | 2000 | 2000 | -588 | 71 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1293 | -1836 | -1836 | -543 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -877 | -1248 | -1248 | -371 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -877 | -1248 | -1248 | -371 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2518
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 |  | 2000 | -5 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1856 |  | 2000 | -144 | 93 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1746 |  | 2000 | -254 | 87 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1637 |  | 2000 | -363 | 82 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1592 |  | 2000 | -408 | 80 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1586 |  | 2000 | -414 | 79 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1581 |  | 2000 | -419 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1576 |  | 2000 | -424 | 79 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1573 |  | 2000 | -427 | 79 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1504 |  | 2000 | -496 | 75 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1487 |  | 2000 | -513 | 74 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1471 |  | 2000 | -529 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1454 |  | 2000 | -546 | 73 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1433 |  | 2000 | -567 | 72 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1412 |  | 2000 | -588 | 71 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1293 |  | -1836 | -543 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -877 |  | -1248 | -371 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -877 |  | -1248 | -371 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2471
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1998 | 2000 | 2000 | -2 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1858 | 2000 | 2000 | -142 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1662 | -1836 | -1836 | -174 | 91 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1738 | 2000 | 2000 | -262 | 87 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1513 | -1836 | -1836 | -323 | 82 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1508 | -1836 | -1836 | -328 | 82 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1633 | 2000 | 2000 | -367 | 82 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1484 | -1836 | -1836 | -352 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1477 | -1836 | -1836 | -359 | 80 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1585 | 2000 | 2000 | -415 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1578 | 2000 | 2000 | -422 | 79 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1449 | -1836 | -1836 | -387 | 79 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1574 | 2000 | 2000 | -426 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 | 2000 | 2000 | -432 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1565 | 2000 | 2000 | -435 | 78 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1432 | -1836 | -1836 | -404 | 78 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1427 | -1836 | -1836 | -409 | 78 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1402 | -1836 | -1836 | -434 | 76 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1391 | -1836 | -1836 | -445 | 76 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1383 | -1836 | -1836 | -453 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1365 | -1836 | -1836 | -471 | 74 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1484 | 2000 | 2000 | -516 | 74 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1473 | 2000 | 2000 | -527 | 74 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1464 | 2000 | 2000 | -536 | 73 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1457 | 2000 | 2000 | -543 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -881 | -1248 | -1248 | -367 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -881 | -1248 | -1248 | -367 | 71 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1411 | 2000 | 2000 | -589 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2471
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1998 |  | 2000 | -2 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1858 |  | 2000 | -142 | 93 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1662 |  | -1836 | -174 | 91 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1738 |  | 2000 | -262 | 87 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1513 |  | -1836 | -323 | 82 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1508 |  | -1836 | -328 | 82 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1633 |  | 2000 | -367 | 82 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1484 |  | -1836 | -352 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1477 |  | -1836 | -359 | 80 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1585 |  | 2000 | -415 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1578 |  | 2000 | -422 | 79 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1449 |  | -1836 | -387 | 79 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1574 |  | 2000 | -426 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 |  | 2000 | -432 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1565 |  | 2000 | -435 | 78 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1432 |  | -1836 | -404 | 78 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1427 |  | -1836 | -409 | 78 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1402 |  | -1836 | -434 | 76 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1391 |  | -1836 | -445 | 76 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1383 |  | -1836 | -453 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1365 |  | -1836 | -471 | 74 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1484 |  | 2000 | -516 | 74 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1473 |  | 2000 | -527 | 74 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1464 |  | 2000 | -536 | 73 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1457 |  | 2000 | -543 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -881 |  | -1248 | -367 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -881 |  | -1248 | -367 | 71 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1411 |  | 2000 | -589 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2463
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1994 | 2000 | 2000 | -6 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1847 | 2000 | 2000 | -153 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1618 | -1836 | -1836 | -218 | 88 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1727 | 2000 | 2000 | -273 | 86 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1610 | 2000 | 2000 | -390 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1472 | -1836 | -1836 | -364 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1468 | -1836 | -1836 | -368 | 80 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1450 | -1836 | -1836 | -386 | 79 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1578 | 2000 | 2000 | -422 | 79 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1446 | -1836 | -1836 | -390 | 79 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1573 | 2000 | 2000 | -427 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1572 | 2000 | 2000 | -428 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 | 2000 | 2000 | -432 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1565 | 2000 | 2000 | -435 | 78 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1409 | -1836 | -1836 | -427 | 77 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1391 | -1836 | -1836 | -445 | 76 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1389 | -1836 | -1836 | -447 | 76 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1490 | 2000 | 2000 | -510 | 75 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1367 | -1836 | -1836 | -469 | 74 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1356 | -1836 | -1836 | -480 | 74 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1473 | 2000 | 2000 | -527 | 74 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1347 | -1836 | -1836 | -489 | 73 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1462 | 2000 | 2000 | -538 | 73 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1331 | -1836 | -1836 | -505 | 73 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1446 | 2000 | 2000 | -554 | 72 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 | 2000 | 2000 | -584 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -881 | -1248 | -1248 | -367 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -881 | -1248 | -1248 | -368 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2463
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1994 |  | 2000 | -6 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1847 |  | 2000 | -153 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1618 |  | -1836 | -218 | 88 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1727 |  | 2000 | -273 | 86 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1610 |  | 2000 | -390 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1472 |  | -1836 | -364 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1468 |  | -1836 | -368 | 80 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1450 |  | -1836 | -386 | 79 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1578 |  | 2000 | -422 | 79 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1446 |  | -1836 | -390 | 79 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1573 |  | 2000 | -427 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1572 |  | 2000 | -428 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 |  | 2000 | -432 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1565 |  | 2000 | -435 | 78 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1409 |  | -1836 | -427 | 77 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1391 |  | -1836 | -445 | 76 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1389 |  | -1836 | -447 | 76 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1490 |  | 2000 | -510 | 75 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1367 |  | -1836 | -469 | 74 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1356 |  | -1836 | -480 | 74 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1473 |  | 2000 | -527 | 74 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1347 |  | -1836 | -489 | 73 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1462 |  | 2000 | -538 | 73 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1331 |  | -1836 | -505 | 73 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1446 |  | 2000 | -554 | 72 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 |  | 2000 | -584 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -881 |  | -1248 | -367 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -881 |  | -1248 | -368 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2445
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1998 | 2000 | 2000 | -2 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1837 | 2000 | 2000 | -163 | 92 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1709 | 2000 | 2000 | -291 | 85 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1564 | -1836 | -1836 | -272 | 85 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1566 | 2000 | 2000 | -434 | 78 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1437 | -1836 | -1836 | -399 | 78 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1563 | 2000 | 2000 | -437 | 78 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1559 | 2000 | 2000 | -441 | 78 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1558 | 2000 | 2000 | -442 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1428 | -1836 | -1836 | -408 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1556 | 2000 | 2000 | -444 | 78 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1555 | 2000 | 2000 | -445 | 78 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1414 | -1836 | -1836 | -422 | 77 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1408 | -1836 | -1836 | -428 | 77 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1370 | -1836 | -1836 | -466 | 75 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1480 | 2000 | 2000 | -520 | 74 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1350 | -1836 | -1836 | -486 | 74 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1350 | -1836 | -1836 | -486 | 74 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1464 | 2000 | 2000 | -536 | 73 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1327 | -1836 | -1836 | -509 | 72 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1442 | 2000 | 2000 | -558 | 72 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1316 | -1836 | -1836 | -520 | 72 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1425 | 2000 | 2000 | -575 | 71 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1307 | -1836 | -1836 | -529 | 71 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1292 | -1836 | -1836 | -544 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -878 | -1248 | -1248 | -370 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -878 | -1248 | -1248 | -370 | 70 | []

## 2030Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2445
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1998 |  | 2000 | -2 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1837 |  | 2000 | -163 | 92 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1709 |  | 2000 | -291 | 85 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1564 |  | -1836 | -272 | 85 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1566 |  | 2000 | -434 | 78 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1437 |  | -1836 | -399 | 78 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1563 |  | 2000 | -437 | 78 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1559 |  | 2000 | -441 | 78 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1558 |  | 2000 | -442 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1428 |  | -1836 | -408 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1556 |  | 2000 | -444 | 78 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1555 |  | 2000 | -445 | 78 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1414 |  | -1836 | -422 | 77 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1408 |  | -1836 | -428 | 77 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1370 |  | -1836 | -466 | 75 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1480 |  | 2000 | -520 | 74 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1350 |  | -1836 | -486 | 74 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1350 |  | -1836 | -486 | 74 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1464 |  | 2000 | -536 | 73 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1327 |  | -1836 | -509 | 72 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1442 |  | 2000 | -558 | 72 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1316 |  | -1836 | -520 | 72 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1425 |  | 2000 | -575 | 71 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1307 |  | -1836 | -529 | 71 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1292 |  | -1836 | -544 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -878 |  | -1248 | -370 | 70 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -878 |  | -1248 | -370 | 70 | []

## 2130Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2669
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 | 2000 | 2000 | -5 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1718 | -1836 | -1836 | -118 | 94 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1821 | 2000 | 2000 | -179 | 91 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1604 | -1836 | -1836 | -232 | 87 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1572 | -1836 | -1836 | -264 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1571 | -1836 | -1836 | -265 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1567 | -1836 | -1836 | -269 | 85 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 | 2000 | 2000 | -309 | 85 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1528 | -1836 | -1836 | -308 | 83 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1514 | -1836 | -1836 | -322 | 82 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1511 | -1836 | -1836 | -325 | 82 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1494 | -1836 | -1836 | -342 | 81 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1486 | -1836 | -1836 | -350 | 81 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1480 | -1836 | -1836 | -356 | 81 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1465 | -1836 | -1836 | -371 | 80 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1572 | 2000 | 2000 | -428 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1569 | 2000 | 2000 | -431 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1565 | 2000 | 2000 | -435 | 78 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1550 | 2000 | 2000 | -450 | 77 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1550 | 2000 | 2000 | -450 | 77 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1513 | 2000 | 2000 | -487 | 76 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1510 | 2000 | 2000 | -490 | 76 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1499 | 2000 | 2000 | -501 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -892 | -1248 | -1248 | -356 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -892 | -1248 | -1248 | -356 | 71 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1425 | 2000 | 2000 | -575 | 71 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1421 | 2000 | 2000 | -579 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -878 | -1248 | -1248 | -371 | 70 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -876 | -1248 | -1248 | -373 | 70 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1402 | 2000 | 2000 | -598 | 70 | []

## 2130Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2669
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 |  | 2000 | -5 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1718 |  | -1836 | -118 | 94 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1821 |  | 2000 | -179 | 91 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1604 |  | -1836 | -232 | 87 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1572 |  | -1836 | -264 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1571 |  | -1836 | -265 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1567 |  | -1836 | -269 | 85 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 |  | 2000 | -309 | 85 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1528 |  | -1836 | -308 | 83 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1514 |  | -1836 | -322 | 82 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1511 |  | -1836 | -325 | 82 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1494 |  | -1836 | -342 | 81 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1486 |  | -1836 | -350 | 81 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1480 |  | -1836 | -356 | 81 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1465 |  | -1836 | -371 | 80 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1572 |  | 2000 | -428 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1569 |  | 2000 | -431 | 78 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1565 |  | 2000 | -435 | 78 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1550 |  | 2000 | -450 | 77 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1550 |  | 2000 | -450 | 77 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1513 |  | 2000 | -487 | 76 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1510 |  | 2000 | -490 | 76 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1499 |  | 2000 | -501 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -892 |  | -1248 | -356 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -892 |  | -1248 | -356 | 71 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1425 |  | 2000 | -575 | 71 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1421 |  | 2000 | -579 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -878 |  | -1248 | -371 | 70 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -876 |  | -1248 | -373 | 70 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1402 |  | 2000 | -598 | 70 | []

## 2230Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2989
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 | 2000 | 2000 | -3 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1808 | 2000 | 2000 | -192 | 90 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1642 | -1836 | -1836 | -194 | 89 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1624 | -1836 | -1836 | -212 | 88 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1604 | -1836 | -1836 | -232 | 87 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1595 | -1836 | -1836 | -241 | 87 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1581 | -1836 | -1836 | -255 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1581 | -1836 | -1836 | -255 | 86 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1560 | -1836 | -1836 | -276 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1558 | -1836 | -1836 | -278 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1551 | -1836 | -1836 | -285 | 84 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1551 | -1836 | -1836 | -285 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1546 | -1836 | -1836 | -290 | 84 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1537 | -1836 | -1836 | -299 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1535 | -1836 | -1836 | -301 | 84 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1667 | 2000 | 2000 | -333 | 83 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1517 | -1836 | -1836 | -319 | 83 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 _XVK_IS11_1:line | -1615 | -2000 | -2000 | -385 | 81 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1576 | 2000 | 2000 | -424 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1576 | 2000 | 2000 | -424 | 79 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1574 | 2000 | 2000 | -426 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1536 | 2000 | 2000 | -464 | 77 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1536 | 2000 | 2000 | -464 | 77 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1518 | 2000 | 2000 | -482 | 76 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1508 | 2000 | 2000 | -492 | 75 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1458 | 2000 | 2000 | -542 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -895 | -1248 | -1248 | -354 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -895 | -1248 | -1248 | -354 | 72 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1428 | 2000 | 2000 | -572 | 71 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1425 | 2000 | 2000 | -575 | 71 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1421 | -2000 | -2000 | -579 | 71 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1407 | 2000 | 2000 | -593 | 70 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1404 | -2000 | -2000 | -596 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2989
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 |  | 2000 | -3 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1808 |  | 2000 | -192 | 90 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1642 |  | -1836 | -194 | 89 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1624 |  | -1836 | -212 | 88 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1604 |  | -1836 | -232 | 87 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1595 |  | -1836 | -241 | 87 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1581 |  | -1836 | -255 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1581 |  | -1836 | -255 | 86 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1560 |  | -1836 | -276 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1558 |  | -1836 | -278 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1551 |  | -1836 | -285 | 84 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1551 |  | -1836 | -285 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1546 |  | -1836 | -290 | 84 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1537 |  | -1836 | -299 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1535 |  | -1836 | -301 | 84 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1667 |  | 2000 | -333 | 83 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1517 |  | -1836 | -319 | 83 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 _XVK_IS11_1:line | -1615 |  | -2000 | -385 | 81 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1576 |  | 2000 | -424 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1576 |  | 2000 | -424 | 79 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1574 |  | 2000 | -426 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1536 |  | 2000 | -464 | 77 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1536 |  | 2000 | -464 | 77 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1518 |  | 2000 | -482 | 76 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1508 |  | 2000 | -492 | 75 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1458 |  | 2000 | -542 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -895 |  | -1248 | -354 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -895 |  | -1248 | -354 | 72 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1428 |  | 2000 | -572 | 71 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1425 |  | 2000 | -575 | 71 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1421 |  | -2000 | -579 | 71 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1407 |  | 2000 | -593 | 70 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1404 |  | -2000 | -596 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3022
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1996 | 2000 | 2000 | -4 | 100 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1658 | -1836 | -1836 | -178 | 90 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1807 | 2000 | 2000 | -193 | 90 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1649 | -1836 | -1836 | -187 | 90 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1615 | -1836 | -1836 | -221 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1608 | -1836 | -1836 | -228 | 88 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1598 | -1836 | -1836 | -238 | 87 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1597 | -1836 | -1836 | -239 | 87 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1577 | -1836 | -1836 | -259 | 86 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1572 | -1836 | -1836 | -264 | 86 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1567 | -1836 | -1836 | -269 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1567 | -1836 | -1836 | -269 | 85 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1563 | -1836 | -1836 | -273 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1556 | -1836 | -1836 | -280 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1552 | -1836 | -1836 | -284 | 85 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1673 | 2000 | 2000 | -327 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1534 | -1836 | -1836 | -302 | 84 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1585 | 2000 | 2000 | -415 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1585 | 2000 | 2000 | -415 | 79 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1583 | 2000 | 2000 | -417 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1544 | 2000 | 2000 | -456 | 77 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1542 | 2000 | 2000 | -458 | 77 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1536 | 2000 | 2000 | -464 | 77 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1527 | 2000 | 2000 | -473 | 76 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 _XVK_IS11_1:line | -1510 | -2000 | -2000 | -490 | 75 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1464 | 2000 | 2000 | -536 | 73 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1462 | 2000 | 2000 | -538 | 73 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1461 | -2000 | -2000 | -539 | 73 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1446 | 2000 | 2000 | -554 | 72 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1446 | 2000 | 2000 | -554 | 72 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1443 | -2000 | -2000 | -557 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -896 | -1248 | -1248 | -352 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -896 | -1248 | -1248 | -352 | 72 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 | 2000 | 2000 | -584 | 71 | []

## 2330Curative
Detailed results
Generated at: | 2026-03-19 08:21
Business day: | 19.03.2026
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3022
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1996 |  | 2000 | -4 | 100 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1658 |  | -1836 | -178 | 90 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1807 |  | 2000 | -193 | 90 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1649 |  | -1836 | -187 | 90 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1615 |  | -1836 | -221 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1608 |  | -1836 | -228 | 88 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1598 |  | -1836 | -238 | 87 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1597 |  | -1836 | -239 | 87 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1577 |  | -1836 | -259 | 86 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1572 |  | -1836 | -264 | 86 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1567 |  | -1836 | -269 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1567 |  | -1836 | -269 | 85 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1563 |  | -1836 | -273 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1556 |  | -1836 | -280 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1552 |  | -1836 | -284 | 85 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1673 |  | 2000 | -327 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1534 |  | -1836 | -302 | 84 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1585 |  | 2000 | -415 | 79 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1585 |  | 2000 | -415 | 79 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1583 |  | 2000 | -417 | 79 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1544 |  | 2000 | -456 | 77 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1542 |  | 2000 | -458 | 77 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1536 |  | 2000 | -464 | 77 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1527 |  | 2000 | -473 | 76 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RISAC41 _XVK_IS11_1:line | -1510 |  | -2000 | -490 | 75 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1464 |  | 2000 | -536 | 73 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1462 |  | 2000 | -538 | 73 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1461 |  | -2000 | -539 | 73 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1446 |  | 2000 | -554 | 72 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1446 |  | 2000 | -554 | 72 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1443 |  | -2000 | -557 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -896 |  | -1248 | -352 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -896 |  | -1248 | -352 | 72 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1416 |  | 2000 | -584 | 71 | []