## SRO borders-exports
SUBMISSION DATE: | 19.03.2026
BUSINESS DATE: | 19.03.2026
2nd ID CC Results
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC RO-BG
12:00 | 13:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3355 | 3155 | 2208
13:00 | 14:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3429 | 3229 | 2260
14:00 | 15:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3441 | 3241 | 2268
15:00 | 16:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3108 | 2908 | 2035
16:00 | 17:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2556 | 2356 | 1649
17:00 | 18:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2518 | 2318 | 1622
18:00 | 19:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2471 | 2271 | 1589
19:00 | 20:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2463 | 2263 | 1584
20:00 | 21:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2445 | 2245 | 1571
21:00 | 22:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2669 | 2469 | 1727
22:00 | 23:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2989 | 2789 | 1952
23:00 | 00:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3022 | 2822 | 1975

## SRO borders-imports
SUBMISSION DATE: | 19.03.2026
BUSINESS DATE: | 19.03.2026
2nd ID CC Results
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC BG-RO
12:00 | 13:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 2979 | 2779 | 1945
13:00 | 14:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3362 | 3162 | 2213
14:00 | 15:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3151 | 2951 | 2066
15:00 | 16:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3174 | 2974 | 2081
16:00 | 17:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3246 | 3046 | 2132
17:00 | 18:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3310 | 3110 | 2176
18:00 | 19:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3310 | 3110 | 2177
19:00 | 20:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3230 | 3030 | 2121
20:00 | 21:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3184 | 2984 | 2089
21:00 | 22:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3166 | 2966 | 2076
22:00 | 23:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3012 | 2812 | 1968
23:00 | 00:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3007 | 2807 | 1965

## SRO borders-exports RAs
SUBMISSION DATE: | 19.03.2026
BUSINESS DATE: | 19.03.2026
2nd ID CC Remedial Actions
Name of the RA | RA ID | Type | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst | [10 empty] | notApplied | notApplied
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | [10 empty] | notApplied | notApplied
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | [10 empty] | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | [10 empty] | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00015 | topological | [10 empty] | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | [10 empty] | notApplied | notApplied

## SRO borders-imports RAs
SUBMISSION DATE: | 19.03.2026
BUSINESS DATE: | 19.03.2026
2nd ID CC Remedial Actions
Name of the RA | RA ID | Type | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst | helpful | helpful |  |  |  |  | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful |  |  |  |  | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | notApplied | notApplied |  |  |  |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | notApplied | notApplied |  |  |  |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00015 | topological | helpful | helpful |  |  |  |  | helpful | helpful | helpful | helpful | helpful | notApplied
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | notApplied | notApplied |  |  |  |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV TINTARENI-KOZLODUI 1 | BG_RA_00001 | topological | [6 empty] | helpful | helpful | helpful | helpful | helpful | helpful