## 0030Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 00:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3503
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1562 | 1600 | 1600 | -38 | 98 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1506 | 1600 | 1600 | -94 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1506 | 1600 | 1600 | -94 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1454 | 1600 | 1600 | -146 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1452 | 1600 | 1600 | -148 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1452 | 1600 | 1600 | -148 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1434 | 1600 | 1600 | -166 | 90 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1375 | 1600 | 1600 | -225 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1351 | 1600 | 1600 | -249 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1350 | 1600 | 1600 | -250 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1339 | 1600 | 1600 | -261 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1310 | 1600 | 1600 | -290 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1297 | 1600 | 1600 | -303 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1273 | 1600 | 1600 | -327 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1270 | 1600 | 1600 | -330 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1268 | 1600 | 1600 | -332 | 79 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1256 | 1600 | 1600 | -344 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 | 1600 | 1600 | -383 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 | 1600 | 1600 | -409 | 74 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1111 | 1517 | 1517 | -406 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1134 | 1600 | 1600 | -466 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1126 | 1600 | 1600 | -474 | 70 | []

## 0030Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 00:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3503
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 |  | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1562 |  | 1600 | -38 | 98 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1506 |  | 1600 | -94 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1506 |  | 1600 | -94 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1454 |  | 1600 | -146 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1452 |  | 1600 | -148 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1452 |  | 1600 | -148 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1434 |  | 1600 | -166 | 90 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1375 |  | 1600 | -225 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1351 |  | 1600 | -249 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1350 |  | 1600 | -250 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1339 |  | 1600 | -261 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1310 |  | 1600 | -290 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1297 |  | 1600 | -303 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 |  | 1600 | -310 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1273 |  | 1600 | -327 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1270 |  | 1600 | -330 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1268 |  | 1600 | -332 | 79 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1256 |  | 1600 | -344 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1253 |  | 1600 | -347 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 |  | 1600 | -383 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 |  | 1600 | -395 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 |  | 1600 | -409 | 74 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1175 |  | 1600 | -425 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1111 |  | 1517 | -406 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 |  | 1600 | -441 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1134 |  | 1600 | -466 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1126 |  | 1600 | -474 | 70 | []

## 0130Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 01:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3529
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1559 | 1600 | 1600 | -41 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1492 | 1600 | 1600 | -108 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1489 | 1600 | 1600 | -111 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 | 1600 | 1600 | -151 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 | 1600 | 1600 | -151 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1438 | 1600 | 1600 | -162 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1428 | 1600 | 1600 | -172 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1369 | 1600 | 1600 | -231 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1349 | 1600 | 1600 | -251 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1348 | 1600 | 1600 | -252 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1325 | 1600 | 1600 | -275 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1305 | 1600 | 1600 | -295 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1292 | 1600 | 1600 | -308 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1282 | 1600 | 1600 | -318 | 80 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 | 1600 | 1600 | -398 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1197 | 1600 | 1600 | -403 | 75 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1132 | 1517 | 1517 | -385 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1129 | 1600 | 1600 | -471 | 71 | []

## 0130Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 01:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3529
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1593 |  | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1559 |  | 1600 | -41 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1492 |  | 1600 | -108 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1489 |  | 1600 | -111 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 |  | 1600 | -151 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 |  | 1600 | -151 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1438 |  | 1600 | -162 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1428 |  | 1600 | -172 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1369 |  | 1600 | -231 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1349 |  | 1600 | -251 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1348 |  | 1600 | -252 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1325 |  | 1600 | -275 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1305 |  | 1600 | -295 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1292 |  | 1600 | -308 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1282 |  | 1600 | -318 | 80 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1271 |  | 1600 | -329 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1260 |  | 1600 | -340 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 |  | 1600 | -395 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 |  | 1600 | -398 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1197 |  | 1600 | -403 | 75 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1132 |  | 1517 | -385 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 |  | 1600 | -415 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1150 |  | 1600 | -450 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1129 |  | 1600 | -471 | 71 | []

## 0230Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 02:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3571
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1565 | 1600 | 1600 | -35 | 98 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1505 | 1600 | 1600 | -95 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1497 | 1600 | 1600 | -103 | 94 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1465 | 1600 | 1600 | -135 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1451 | 1600 | 1600 | -149 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 | 1600 | 1600 | -151 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1438 | 1600 | 1600 | -162 | 90 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1380 | 1600 | 1600 | -220 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1343 | 1600 | 1600 | -257 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1343 | 1600 | 1600 | -257 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1326 | 1600 | 1600 | -274 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1317 | 1600 | 1600 | -283 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1303 | 1600 | 1600 | -297 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1288 | 1600 | 1600 | -312 | 81 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1278 | 1600 | 1600 | -322 | 80 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 | 1600 | 1600 | -326 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1266 | 1600 | 1600 | -334 | 79 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1259 | 1600 | 1600 | -341 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 | 1600 | 1600 | -350 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1175 | 1517 | 1517 | -342 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 | 1600 | 1600 | -409 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1134 | 1600 | 1600 | -466 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 | 1600 | 1600 | -470 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1127 | 1600 | 1600 | -473 | 70 | []

## 0230Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 02:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3571
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 |  | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1565 |  | 1600 | -35 | 98 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1505 |  | 1600 | -95 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1497 |  | 1600 | -103 | 94 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1465 |  | 1600 | -135 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1451 |  | 1600 | -149 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 |  | 1600 | -151 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1438 |  | 1600 | -162 | 90 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1380 |  | 1600 | -220 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1343 |  | 1600 | -257 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1343 |  | 1600 | -257 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1326 |  | 1600 | -274 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1317 |  | 1600 | -283 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1303 |  | 1600 | -297 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 |  | 1600 | -310 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1288 |  | 1600 | -312 | 81 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1278 |  | 1600 | -322 | 80 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 |  | 1600 | -326 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1266 |  | 1600 | -334 | 79 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1259 |  | 1600 | -341 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1251 |  | 1600 | -349 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 |  | 1600 | -350 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1240 |  | 1600 | -360 | 77 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1175 |  | 1517 | -342 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 |  | 1600 | -395 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 |  | 1600 | -409 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 |  | 1600 | -442 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1134 |  | 1600 | -466 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 |  | 1600 | -470 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1127 |  | 1600 | -473 | 70 | []

## 0330Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 03:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3552
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1552 | 1600 | 1600 | -48 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1505 | 1600 | 1600 | -95 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1499 | 1600 | 1600 | -101 | 94 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1468 | 1600 | 1600 | -132 | 92 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1448 | 1600 | 1600 | -152 | 91 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1442 | 1600 | 1600 | -158 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1434 | 1600 | 1600 | -166 | 90 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1378 | 1600 | 1600 | -222 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1337 | 1600 | 1600 | -263 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1336 | 1600 | 1600 | -264 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1317 | 1600 | 1600 | -283 | 82 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1312 | 1600 | 1600 | -288 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1303 | 1600 | 1600 | -297 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1291 | 1600 | 1600 | -309 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1283 | 1600 | 1600 | -317 | 80 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1266 | 1600 | 1600 | -334 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1263 | 1600 | 1600 | -337 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1190 | 1517 | 1517 | -327 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 | 1600 | 1600 | -350 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 | 1600 | 1600 | -350 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1203 | 1600 | 1600 | -397 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 | 1600 | 1600 | -410 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1136 | 1600 | 1600 | -464 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1134 | 1600 | 1600 | -466 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 | 1600 | 1600 | -469 | 71 | []

## 0330Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 03:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3552
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 |  | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1552 |  | 1600 | -48 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1505 |  | 1600 | -95 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1499 |  | 1600 | -101 | 94 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1468 |  | 1600 | -132 | 92 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1448 |  | 1600 | -152 | 91 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1442 |  | 1600 | -158 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1434 |  | 1600 | -166 | 90 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1378 |  | 1600 | -222 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1337 |  | 1600 | -263 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1336 |  | 1600 | -264 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1317 |  | 1600 | -283 | 82 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1312 |  | 1600 | -288 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1303 |  | 1600 | -297 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1291 |  | 1600 | -309 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 |  | 1600 | -310 | 81 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1283 |  | 1600 | -317 | 80 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 |  | 1600 | -331 | 79 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1266 |  | 1600 | -334 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1263 |  | 1600 | -337 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1257 |  | 1600 | -343 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1190 |  | 1517 | -327 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 |  | 1600 | -350 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 |  | 1600 | -350 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1203 |  | 1600 | -397 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 |  | 1600 | -410 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 |  | 1600 | -442 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1136 |  | 1600 | -464 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1134 |  | 1600 | -466 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 |  | 1600 | -469 | 71 | []

## 0430Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 04:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3472
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1555 | 1600 | 1600 | -45 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1489 | 1600 | 1600 | -111 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1484 | 1600 | 1600 | -116 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1450 | 1600 | 1600 | -150 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1444 | 1600 | 1600 | -156 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1432 | 1600 | 1600 | -168 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1427 | 1600 | 1600 | -173 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1368 | 1600 | 1600 | -232 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1343 | 1600 | 1600 | -257 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1342 | 1600 | 1600 | -258 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1307 | 1600 | 1600 | -293 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1295 | 1600 | 1600 | -305 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 | 1600 | 1600 | -316 | 80 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1282 | 1600 | 1600 | -318 | 80 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1279 | 1600 | 1600 | -321 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1266 | 1600 | 1600 | -334 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 | 1600 | 1600 | -350 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1217 | 1600 | 1600 | -383 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 | 1600 | 1600 | -396 | 75 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 | 1600 | 1600 | -409 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1099 | 1517 | 1517 | -418 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 | 1600 | 1600 | -443 | 72 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1156 | 1600 | 1600 | -444 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1137 | 1600 | 1600 | -463 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1132 | 1600 | 1600 | -468 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 | 1600 | 1600 | -470 | 71 | []

## 0430Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 04:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3472
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 |  | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1555 |  | 1600 | -45 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1489 |  | 1600 | -111 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1484 |  | 1600 | -116 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1450 |  | 1600 | -150 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1444 |  | 1600 | -156 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1432 |  | 1600 | -168 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1427 |  | 1600 | -173 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1368 |  | 1600 | -232 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1343 |  | 1600 | -257 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1342 |  | 1600 | -258 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1307 |  | 1600 | -293 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1295 |  | 1600 | -305 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 |  | 1600 | -316 | 80 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1282 |  | 1600 | -318 | 80 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1279 |  | 1600 | -321 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1266 |  | 1600 | -334 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1251 |  | 1600 | -349 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 |  | 1600 | -350 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1217 |  | 1600 | -383 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 |  | 1600 | -396 | 75 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 |  | 1600 | -409 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1099 |  | 1517 | -418 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 |  | 1600 | -443 | 72 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1156 |  | 1600 | -444 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1137 |  | 1600 | -463 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1132 |  | 1600 | -468 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 |  | 1600 | -470 | 71 | []

## 0530Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 05:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3431
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1489 | 1600 | 1600 | -111 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1472 | 1600 | 1600 | -128 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1469 | 1600 | 1600 | -131 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1427 | 1600 | 1600 | -173 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1409 | 1600 | 1600 | -191 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1405 | 1600 | 1600 | -195 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1354 | 1600 | 1600 | -246 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1346 | 1600 | 1600 | -254 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1346 | 1600 | 1600 | -254 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1299 | 1600 | 1600 | -301 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1278 | 1600 | 1600 | -322 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1275 | 1600 | 1600 | -325 | 80 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1263 | 1600 | 1600 | -337 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1177 | 1600 | 1600 | -423 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1153 | 1600 | 1600 | -447 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1143 | 1600 | 1600 | -457 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []

## 0530Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 05:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3431
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 |  | 1600 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1594 |  | 1600 | -6 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1489 |  | 1600 | -111 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1472 |  | 1600 | -128 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1469 |  | 1600 | -131 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1427 |  | 1600 | -173 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1409 |  | 1600 | -191 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1405 |  | 1600 | -195 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1354 |  | 1600 | -246 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1346 |  | 1600 | -254 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1346 |  | 1600 | -254 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1299 |  | 1600 | -301 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1278 |  | 1600 | -322 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1275 |  | 1600 | -325 | 80 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1263 |  | 1600 | -337 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 |  | 1600 | -401 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 |  | 1600 | -413 | 74 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1177 |  | 1600 | -423 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 |  | 1600 | -425 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1153 |  | 1600 | -447 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1143 |  | 1600 | -457 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 |  | 1600 | -460 | 71 | []

## 0630Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 06:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3438
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1589 | 1600 | 1600 | -11 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1497 | 1600 | 1600 | -103 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1483 | 1600 | 1600 | -117 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1469 | 1600 | 1600 | -131 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1426 | 1600 | 1600 | -174 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1415 | 1600 | 1600 | -185 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1412 | 1600 | 1600 | -188 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1352 | 1600 | 1600 | -248 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1335 | 1600 | 1600 | -265 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1335 | 1600 | 1600 | -265 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1299 | 1600 | 1600 | -301 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1291 | 1600 | 1600 | -309 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1282 | 1600 | 1600 | -318 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1281 | 1600 | 1600 | -319 | 80 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1216 | 1600 | 1600 | -384 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 | 1600 | 1600 | -410 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1152 | 1600 | 1600 | -448 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 | 1600 | 1600 | -454 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1133 | 1600 | 1600 | -467 | 71 | []

## 0630Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 06:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3438
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1589 |  | 1600 | -11 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1497 |  | 1600 | -103 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1483 |  | 1600 | -117 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1469 |  | 1600 | -131 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1426 |  | 1600 | -174 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1415 |  | 1600 | -185 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1412 |  | 1600 | -188 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1352 |  | 1600 | -248 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1335 |  | 1600 | -265 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1335 |  | 1600 | -265 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1299 |  | 1600 | -301 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1291 |  | 1600 | -309 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1282 |  | 1600 | -318 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1281 |  | 1600 | -319 | 80 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1228 |  | 1600 | -372 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1216 |  | 1600 | -384 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 |  | 1600 | -407 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 |  | 1600 | -410 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 |  | 1600 | -417 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 |  | 1600 | -441 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1152 |  | 1600 | -448 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1150 |  | 1600 | -450 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 |  | 1600 | -454 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1133 |  | 1600 | -467 | 71 | []

## 0730Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 07:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3453
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1492 | 1600 | 1600 | -108 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1481 | 1600 | 1600 | -119 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1478 | 1600 | 1600 | -122 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1439 | 1600 | 1600 | -161 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1419 | 1600 | 1600 | -181 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1417 | 1600 | 1600 | -183 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1354 | 1600 | 1600 | -246 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1339 | 1600 | 1600 | -261 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1339 | 1600 | 1600 | -261 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1309 | 1600 | 1600 | -291 | 82 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1297 | 1600 | 1600 | -303 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1287 | 1600 | 1600 | -313 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1282 | 1600 | 1600 | -318 | 80 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1252 | 1600 | 1600 | -348 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 | 1600 | 1600 | -350 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 | 1600 | 1600 | -400 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 | 1600 | 1600 | -424 | 73 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1172 | 1600 | 1600 | -428 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1169 | 1600 | 1600 | -431 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 | 1600 | 1600 | -433 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1148 | 1600 | 1600 | -452 | 72 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1080 | 1517 | 1517 | -437 | 71 | []

## 0730Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 07:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3453
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 |  | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 |  | 1600 | -5 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1492 |  | 1600 | -108 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1481 |  | 1600 | -119 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1478 |  | 1600 | -122 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1439 |  | 1600 | -161 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1419 |  | 1600 | -181 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1417 |  | 1600 | -183 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1354 |  | 1600 | -246 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1339 |  | 1600 | -261 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1339 |  | 1600 | -261 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1309 |  | 1600 | -291 | 82 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1297 |  | 1600 | -303 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1287 |  | 1600 | -313 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1282 |  | 1600 | -318 | 80 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 |  | 1600 | -340 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1252 |  | 1600 | -348 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1251 |  | 1600 | -349 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 |  | 1600 | -350 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 |  | 1600 | -390 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 |  | 1600 | -400 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 |  | 1600 | -424 | 73 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1172 |  | 1600 | -428 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1169 |  | 1600 | -431 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 |  | 1600 | -433 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 |  | 1600 | -442 | 72 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1148 |  | 1600 | -452 | 72 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1080 |  | 1517 | -437 | 71 | []

## 0830Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 08:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3481
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1589 | 1600 | 1600 | -11 | 99 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1495 | 1600 | 1600 | -105 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1485 | 1600 | 1600 | -115 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1483 | 1600 | 1600 | -117 | 93 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1453 | 1600 | 1600 | -147 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1430 | 1600 | 1600 | -170 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1418 | 1600 | 1600 | -182 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1368 | 1600 | 1600 | -232 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1331 | 1600 | 1600 | -269 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1331 | 1600 | 1600 | -269 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1316 | 1600 | 1600 | -284 | 82 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1291 | 1600 | 1600 | -309 | 81 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1287 | 1600 | 1600 | -313 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1280 | 1600 | 1600 | -320 | 80 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1252 | 1600 | 1600 | -348 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1136 | 1517 | 1517 | -381 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1180 | 1600 | 1600 | -420 | 74 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 | 1600 | 1600 | -426 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 | 1600 | 1600 | -426 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1170 | 1600 | 1600 | -430 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 | 1600 | 1600 | -433 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1121 | 1600 | 1600 | -479 | 70 | []

## 0830Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 08:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3481
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1594 |  | 1600 | -6 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1589 |  | 1600 | -11 | 99 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1495 |  | 1600 | -105 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1485 |  | 1600 | -115 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1483 |  | 1600 | -117 | 93 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1453 |  | 1600 | -147 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1430 |  | 1600 | -170 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1418 |  | 1600 | -182 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1368 |  | 1600 | -232 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1331 |  | 1600 | -269 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1331 |  | 1600 | -269 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1316 |  | 1600 | -284 | 82 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1302 |  | 1600 | -298 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1291 |  | 1600 | -309 | 81 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1287 |  | 1600 | -313 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1280 |  | 1600 | -320 | 80 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1271 |  | 1600 | -329 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 |  | 1600 | -331 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1253 |  | 1600 | -347 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1252 |  | 1600 | -348 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1212 |  | 1600 | -388 | 76 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1136 |  | 1517 | -381 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1180 |  | 1600 | -420 | 74 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 |  | 1600 | -426 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 |  | 1600 | -426 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1170 |  | 1600 | -430 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 |  | 1600 | -433 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 |  | 1600 | -442 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1121 |  | 1600 | -479 | 70 | []

## 0930Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 09:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3423
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1549 | 1600 | 1600 | -51 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1484 | 1600 | 1600 | -116 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 | 1600 | 1600 | -151 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1438 | 1600 | 1600 | -162 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1434 | 1600 | 1600 | -166 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1420 | 1600 | 1600 | -180 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1416 | 1600 | 1600 | -184 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1364 | 1600 | 1600 | -236 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1347 | 1600 | 1600 | -253 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1347 | 1600 | 1600 | -253 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1300 | 1600 | 1600 | -300 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1275 | 1600 | 1600 | -325 | 80 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1273 | 1600 | 1600 | -327 | 80 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1208 | 1600 | 1600 | -392 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 | 1600 | 1600 | -396 | 75 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1171 | 1600 | 1600 | -429 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1108 | 1517 | 1517 | -409 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1153 | 1600 | 1600 | -447 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1151 | 1600 | 1600 | -449 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 | 1600 | 1600 | -451 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 | 1600 | 1600 | -454 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1144 | 1600 | 1600 | -456 | 72 | []

## 0930Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 09:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3423
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1593 |  | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1549 |  | 1600 | -51 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1484 |  | 1600 | -116 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 |  | 1600 | -151 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1438 |  | 1600 | -162 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1434 |  | 1600 | -166 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1420 |  | 1600 | -180 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1416 |  | 1600 | -184 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1364 |  | 1600 | -236 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1347 |  | 1600 | -253 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1347 |  | 1600 | -253 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1302 |  | 1600 | -298 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1300 |  | 1600 | -300 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 |  | 1600 | -310 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1275 |  | 1600 | -325 | 80 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1273 |  | 1600 | -327 | 80 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1254 |  | 1600 | -346 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1208 |  | 1600 | -392 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 |  | 1600 | -396 | 75 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1175 |  | 1600 | -425 | 73 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1171 |  | 1600 | -429 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1108 |  | 1517 | -409 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1153 |  | 1600 | -447 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1151 |  | 1600 | -449 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 |  | 1600 | -451 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 |  | 1600 | -454 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1144 |  | 1600 | -456 | 72 | []

## 1030Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 10:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3340
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1554 | 1600 | 1600 | -46 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1464 | 1600 | 1600 | -136 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1452 | 1600 | 1600 | -148 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1412 | 1600 | 1600 | -188 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1409 | 1600 | 1600 | -191 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1404 | 1600 | 1600 | -196 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 | 1600 | 1600 | -208 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1362 | 1600 | 1600 | -238 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 | 1600 | 1600 | -239 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1355 | 1600 | 1600 | -245 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1300 | 1600 | 1600 | -300 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1278 | 1600 | 1600 | -322 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1264 | 1600 | 1600 | -336 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1252 | 1600 | 1600 | -348 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1197 | 1600 | 1600 | -403 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 | 1600 | 1600 | -424 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 | 1600 | 1600 | -458 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1138 | 1600 | 1600 | -462 | 71 | []

## 1030Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 10:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3340
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 |  | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1554 |  | 1600 | -46 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1464 |  | 1600 | -136 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1452 |  | 1600 | -148 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1412 |  | 1600 | -188 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1409 |  | 1600 | -191 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1404 |  | 1600 | -196 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 |  | 1600 | -208 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1362 |  | 1600 | -238 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 |  | 1600 | -239 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1355 |  | 1600 | -245 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1300 |  | 1600 | -300 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1278 |  | 1600 | -322 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1264 |  | 1600 | -336 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1252 |  | 1600 | -348 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1197 |  | 1600 | -403 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 |  | 1600 | -412 | 74 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 |  | 1600 | -424 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1150 |  | 1600 | -450 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 |  | 1600 | -458 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1138 |  | 1600 | -462 | 71 | []

## 1130Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 11:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3316
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1569 | 1600 | 1600 | -31 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1462 | 1600 | 1600 | -138 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1446 | 1600 | 1600 | -154 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1397 | 1600 | 1600 | -203 | 87 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 | 1600 | 1600 | -208 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1389 | 1600 | 1600 | -211 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1376 | 1600 | 1600 | -224 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1375 | 1600 | 1600 | -225 | 86 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1354 | 1600 | 1600 | -246 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1306 | 1600 | 1600 | -294 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1280 | 1600 | 1600 | -320 | 80 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1268 | 1600 | 1600 | -332 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 | 1600 | 1600 | -408 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 | 1600 | 1600 | -424 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 | 1600 | 1600 | -443 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 | 1600 | 1600 | -454 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1134 | 1600 | 1600 | -466 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1133 | 1600 | 1600 | -467 | 71 | []

## 1130Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 11:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3316
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1569 |  | 1600 | -31 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1462 |  | 1600 | -138 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1446 |  | 1600 | -154 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1397 |  | 1600 | -203 | 87 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 |  | 1600 | -208 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1389 |  | 1600 | -211 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1376 |  | 1600 | -224 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1375 |  | 1600 | -225 | 86 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1370 |  | 1600 | -230 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1354 |  | 1600 | -246 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1306 |  | 1600 | -294 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1280 |  | 1600 | -320 | 80 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1268 |  | 1600 | -332 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 |  | 1600 | -408 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 |  | 1600 | -424 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 |  | 1600 | -436 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 |  | 1600 | -443 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 |  | 1600 | -454 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1134 |  | 1600 | -466 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1133 |  | 1600 | -467 | 71 | []

## 1230Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3317
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1575 | 1600 | 1600 | -25 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1468 | 1600 | 1600 | -132 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1442 | 1600 | 1600 | -158 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 | 1600 | 1600 | -208 | 87 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1387 | 1600 | 1600 | -213 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1384 | 1600 | 1600 | -216 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1371 | 1600 | 1600 | -229 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1371 | 1600 | 1600 | -229 | 86 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1365 | 1600 | 1600 | -235 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1350 | 1600 | 1600 | -250 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1307 | 1600 | 1600 | -293 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 | 1600 | 1600 | -324 | 80 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1216 | 1600 | 1600 | -384 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1195 | 1600 | 1600 | -405 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 | 1600 | 1600 | -433 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 | 1600 | 1600 | -443 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1155 | 1600 | 1600 | -445 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1144 | 1600 | 1600 | -456 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1133 | 1600 | 1600 | -467 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 | 1600 | 1600 | -469 | 71 | []

## 1230Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3317
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 |  | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1575 |  | 1600 | -25 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1468 |  | 1600 | -132 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1442 |  | 1600 | -158 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 |  | 1600 | -208 | 87 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1387 |  | 1600 | -213 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1384 |  | 1600 | -216 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1371 |  | 1600 | -229 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1371 |  | 1600 | -229 | 86 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1365 |  | 1600 | -235 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1350 |  | 1600 | -250 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1307 |  | 1600 | -293 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 |  | 1600 | -324 | 80 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1251 |  | 1600 | -349 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1216 |  | 1600 | -384 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 |  | 1600 | -395 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1195 |  | 1600 | -405 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 |  | 1600 | -418 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1178 |  | 1600 | -422 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 |  | 1600 | -433 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 |  | 1600 | -443 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1155 |  | 1600 | -445 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1144 |  | 1600 | -456 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1133 |  | 1600 | -467 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 |  | 1600 | -469 | 71 | []

## 1330Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3453
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1555 | 1600 | 1600 | -45 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1464 | 1600 | 1600 | -136 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1456 | 1600 | 1600 | -144 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1418 | 1600 | 1600 | -182 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1415 | 1600 | 1600 | -185 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1415 | 1600 | 1600 | -185 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 | 1600 | 1600 | -208 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1359 | 1600 | 1600 | -241 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1304 | 1600 | 1600 | -296 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 | 1600 | 1600 | -324 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1203 | 1600 | 1600 | -397 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1186 | 1600 | 1600 | -414 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1179 | 1600 | 1600 | -421 | 74 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1171 | 1600 | 1600 | -429 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1169 | 1600 | 1600 | -431 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1136 | 1600 | 1600 | -464 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1132 | 1600 | 1600 | -468 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1124 | 1600 | 1600 | -476 | 70 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1122 | 1600 | 1600 | -478 | 70 | []

## 1330Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3453
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1597 |  | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1555 |  | 1600 | -45 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1464 |  | 1600 | -136 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1456 |  | 1600 | -144 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1418 |  | 1600 | -182 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1415 |  | 1600 | -185 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1415 |  | 1600 | -185 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 |  | 1600 | -208 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 |  | 1600 | -230 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 |  | 1600 | -230 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1359 |  | 1600 | -241 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1304 |  | 1600 | -296 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 |  | 1600 | -324 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 |  | 1600 | -340 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 |  | 1600 | -390 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1203 |  | 1600 | -397 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1186 |  | 1600 | -414 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1179 |  | 1600 | -421 | 74 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 |  | 1600 | -425 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1171 |  | 1600 | -429 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1169 |  | 1600 | -431 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 |  | 1600 | -435 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1150 |  | 1600 | -450 | 72 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1136 |  | 1600 | -464 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1132 |  | 1600 | -468 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1124 |  | 1600 | -476 | 70 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1122 |  | 1600 | -478 | 70 | []

## 1430Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3483
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1484 | 1600 | 1600 | -116 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1465 | 1600 | 1600 | -135 | 92 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1433 | 1600 | 1600 | -167 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1424 | 1600 | 1600 | -176 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1409 | 1600 | 1600 | -191 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1394 | 1600 | 1600 | -206 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 | 1600 | 1600 | -239 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 | 1600 | 1600 | -239 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1354 | 1600 | 1600 | -246 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1309 | 1600 | 1600 | -291 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1296 | 1600 | 1600 | -304 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1283 | 1600 | 1600 | -317 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 | 1600 | 1600 | -356 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1184 | 1600 | 1600 | -416 | 74 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1180 | 1600 | 1600 | -420 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1180 | 1600 | 1600 | -420 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 | 1600 | 1600 | -454 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1145 | 1600 | 1600 | -455 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1128 | 1600 | 1600 | -472 | 71 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1127 | 1600 | 1600 | -473 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3483
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 |  | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1594 |  | 1600 | -6 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1484 |  | 1600 | -116 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1465 |  | 1600 | -135 | 92 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1433 |  | 1600 | -167 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1424 |  | 1600 | -176 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1409 |  | 1600 | -191 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1394 |  | 1600 | -206 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 |  | 1600 | -239 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 |  | 1600 | -239 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1354 |  | 1600 | -246 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1309 |  | 1600 | -291 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1296 |  | 1600 | -304 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1283 |  | 1600 | -317 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 |  | 1600 | -331 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1244 |  | 1600 | -356 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1184 |  | 1600 | -416 | 74 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1180 |  | 1600 | -420 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1180 |  | 1600 | -420 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1147 |  | 1600 | -453 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 |  | 1600 | -454 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1145 |  | 1600 | -455 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1128 |  | 1600 | -472 | 71 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1127 |  | 1600 | -473 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3335
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1586 | 1600 | 1600 | -14 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1495 | 1600 | 1600 | -105 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1426 | 1600 | 1600 | -174 | 89 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1406 | 1600 | 1600 | -194 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1378 | 1600 | 1600 | -222 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1372 | 1600 | 1600 | -228 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1362 | 1600 | 1600 | -238 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 | 1600 | 1600 | -239 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1354 | 1600 | 1600 | -246 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1331 | 1600 | 1600 | -269 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1216 | 1600 | 1600 | -384 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 | 1600 | 1600 | -398 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 | 1600 | 1600 | -411 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 | 1600 | 1600 | -427 | 73 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1171 | 1600 | 1600 | -429 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1154 | 1600 | 1600 | -446 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 | 1600 | 1600 | -451 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1144 | 1600 | 1600 | -456 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1141 | 1600 | 1600 | -459 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 | 1600 | 1600 | -465 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3335
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1586 |  | 1600 | -14 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1495 |  | 1600 | -105 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1426 |  | 1600 | -174 | 89 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1406 |  | 1600 | -194 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1378 |  | 1600 | -222 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1372 |  | 1600 | -228 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1362 |  | 1600 | -238 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 |  | 1600 | -239 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1354 |  | 1600 | -246 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1331 |  | 1600 | -269 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 |  | 1600 | -331 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 |  | 1600 | -340 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1216 |  | 1600 | -384 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 |  | 1600 | -398 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 |  | 1600 | -411 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 |  | 1600 | -427 | 73 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1171 |  | 1600 | -429 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1154 |  | 1600 | -446 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 |  | 1600 | -451 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1144 |  | 1600 | -456 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1141 |  | 1600 | -459 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 |  | 1600 | -465 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3193
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1577 | 1600 | 1600 | -23 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1506 | 1600 | 1600 | -94 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1410 | 1600 | 1600 | -190 | 88 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1407 | 1600 | 1600 | -193 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1355 | 1600 | 1600 | -245 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1355 | 1600 | 1600 | -245 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1339 | 1600 | 1600 | -261 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1332 | 1600 | 1600 | -268 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1318 | 1600 | 1600 | -282 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1278 | 1600 | 1600 | -322 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 | 1600 | 1600 | -350 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 | 1600 | 1600 | -383 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 | 1600 | 1600 | -383 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1196 | 1600 | 1600 | -404 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1195 | 1600 | 1600 | -405 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1171 | 1600 | 1600 | -429 | 73 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1162 | 1600 | 1600 | -438 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1144 | 1600 | 1600 | -456 | 72 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 | 1600 | 1600 | -458 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1139 | 1600 | 1600 | -461 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 | 1600 | 1600 | -465 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1133 | 1600 | 1600 | -467 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 | 1600 | 1600 | -469 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3193
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 |  | 1600 | -4 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1577 |  | 1600 | -23 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1506 |  | 1600 | -94 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1410 |  | 1600 | -190 | 88 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1407 |  | 1600 | -193 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1366 |  | 1600 | -234 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1355 |  | 1600 | -245 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1355 |  | 1600 | -245 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1339 |  | 1600 | -261 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1332 |  | 1600 | -268 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1318 |  | 1600 | -282 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1278 |  | 1600 | -322 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 |  | 1600 | -350 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 |  | 1600 | -383 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 |  | 1600 | -383 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 |  | 1600 | -395 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 |  | 1600 | -395 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1196 |  | 1600 | -404 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1195 |  | 1600 | -405 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 |  | 1600 | -406 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1171 |  | 1600 | -429 | 73 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1162 |  | 1600 | -438 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1147 |  | 1600 | -453 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1144 |  | 1600 | -456 | 72 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 |  | 1600 | -458 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1139 |  | 1600 | -461 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 |  | 1600 | -465 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1133 |  | 1600 | -467 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 |  | 1600 | -469 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3341
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1588 | 1600 | 1600 | -12 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1527 | 1600 | 1600 | -73 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1428 | 1600 | 1600 | -172 | 89 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1403 | 1600 | 1600 | -197 | 88 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1384 | 1600 | 1600 | -216 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1376 | 1600 | 1600 | -224 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1372 | 1600 | 1600 | -228 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1371 | 1600 | 1600 | -229 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1339 | 1600 | 1600 | -261 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1321 | 1600 | 1600 | -279 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1262 | 1600 | 1600 | -338 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1207 | 1600 | 1600 | -393 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1207 | 1600 | 1600 | -393 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 | 1600 | 1600 | -398 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 | 1600 | 1600 | -400 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 | 1600 | 1600 | -402 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1170 | 1600 | 1600 | -430 | 73 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 | 1600 | 1600 | -451 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1143 | 1600 | 1600 | -457 | 71 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 | 1600 | 1600 | -458 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1137 | 1600 | 1600 | -463 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 | 1600 | 1600 | -470 | 71 | []

## 1730Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3341
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1588 |  | 1600 | -12 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1527 |  | 1600 | -73 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1428 |  | 1600 | -172 | 89 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1403 |  | 1600 | -197 | 88 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1384 |  | 1600 | -216 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1376 |  | 1600 | -224 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1372 |  | 1600 | -228 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1371 |  | 1600 | -229 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1357 |  | 1600 | -243 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1339 |  | 1600 | -261 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1321 |  | 1600 | -279 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 |  | 1600 | -310 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1262 |  | 1600 | -338 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 |  | 1600 | -390 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1207 |  | 1600 | -393 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1207 |  | 1600 | -393 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 |  | 1600 | -398 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 |  | 1600 | -400 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 |  | 1600 | -402 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 |  | 1600 | -412 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1170 |  | 1600 | -430 | 73 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 |  | 1600 | -436 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 |  | 1600 | -442 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 |  | 1600 | -451 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1143 |  | 1600 | -457 | 71 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 |  | 1600 | -458 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 |  | 1600 | -460 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1137 |  | 1600 | -463 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 |  | 1600 | -470 | 71 | []

## 1830Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3388
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1592 | 1600 | 1600 | -8 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1526 | 1600 | 1600 | -74 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1472 | 1600 | 1600 | -128 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1441 | 1600 | 1600 | -159 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1408 | 1600 | 1600 | -192 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1387 | 1600 | 1600 | -213 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1380 | 1600 | 1600 | -220 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1343 | 1600 | 1600 | -257 | 84 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1317 | 1600 | 1600 | -283 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1306 | 1600 | 1600 | -294 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 | 1600 | 1600 | -316 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1275 | 1600 | 1600 | -325 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1268 | 1600 | 1600 | -332 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 | 1600 | 1600 | -400 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1177 | 1600 | 1600 | -423 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1171 | 1600 | 1600 | -429 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1144 | 1600 | 1600 | -456 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1137 | 1600 | 1600 | -463 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1136 | 1600 | 1600 | -464 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3388
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 |  | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1592 |  | 1600 | -8 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1526 |  | 1600 | -74 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1472 |  | 1600 | -128 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1441 |  | 1600 | -159 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1408 |  | 1600 | -192 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1387 |  | 1600 | -213 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1380 |  | 1600 | -220 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 |  | 1600 | -234 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 |  | 1600 | -234 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1343 |  | 1600 | -257 | 84 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1317 |  | 1600 | -283 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1306 |  | 1600 | -294 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 |  | 1600 | -316 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1275 |  | 1600 | -325 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1268 |  | 1600 | -332 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1230 |  | 1600 | -370 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 |  | 1600 | -400 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 |  | 1600 | -406 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 |  | 1600 | -412 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1177 |  | 1600 | -423 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1171 |  | 1600 | -429 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1163 |  | 1600 | -437 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1144 |  | 1600 | -456 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1137 |  | 1600 | -463 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1136 |  | 1600 | -464 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3357
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1589 | 1600 | 1600 | -11 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1524 | 1600 | 1600 | -76 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1473 | 1600 | 1600 | -127 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1444 | 1600 | 1600 | -156 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1409 | 1600 | 1600 | -191 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1386 | 1600 | 1600 | -214 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1383 | 1600 | 1600 | -217 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1345 | 1600 | 1600 | -255 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1308 | 1600 | 1600 | -292 | 82 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1286 | 1600 | 1600 | -314 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 | 1600 | 1600 | -316 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 | 1600 | 1600 | -324 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1270 | 1600 | 1600 | -330 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 | 1600 | 1600 | -350 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 77 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1172 | 1600 | 1600 | -428 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 | 1600 | 1600 | -454 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1138 | 1600 | 1600 | -462 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3357
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1597 |  | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1589 |  | 1600 | -11 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1524 |  | 1600 | -76 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1473 |  | 1600 | -127 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1444 |  | 1600 | -156 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1409 |  | 1600 | -191 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1386 |  | 1600 | -214 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1383 |  | 1600 | -217 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 |  | 1600 | -234 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 |  | 1600 | -234 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1345 |  | 1600 | -255 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1308 |  | 1600 | -292 | 82 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1286 |  | 1600 | -314 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 |  | 1600 | -316 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 |  | 1600 | -324 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1270 |  | 1600 | -330 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 |  | 1600 | -350 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 77 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1222 |  | 1600 | -378 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 |  | 1600 | -401 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 |  | 1600 | -401 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 |  | 1600 | -413 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1172 |  | 1600 | -428 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 |  | 1600 | -436 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1163 |  | 1600 | -437 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 |  | 1600 | -454 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 |  | 1600 | -460 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1138 |  | 1600 | -462 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3313
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1522 | 1600 | 1600 | -78 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 | 1600 | 1600 | -151 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1428 | 1600 | 1600 | -172 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 | 1600 | 1600 | -208 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1374 | 1600 | 1600 | -226 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1374 | 1600 | 1600 | -226 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1373 | 1600 | 1600 | -227 | 86 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1364 | 1600 | 1600 | -236 | 85 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1341 | 1600 | 1600 | -259 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1334 | 1600 | 1600 | -266 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1301 | 1600 | 1600 | -299 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 | 1600 | 1600 | -326 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1268 | 1600 | 1600 | -332 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 | 1600 | 1600 | -443 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 | 1600 | 1600 | -443 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 | 1600 | 1600 | -454 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1145 | 1600 | 1600 | -455 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1132 | 1600 | 1600 | -468 | 71 | []

## 2030Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3313
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1597 |  | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1591 |  | 1600 | -9 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1522 |  | 1600 | -78 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 |  | 1600 | -151 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1428 |  | 1600 | -172 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 |  | 1600 | -208 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1374 |  | 1600 | -226 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1374 |  | 1600 | -226 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1373 |  | 1600 | -227 | 86 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1364 |  | 1600 | -236 | 85 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1341 |  | 1600 | -259 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1334 |  | 1600 | -266 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1301 |  | 1600 | -299 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 |  | 1600 | -326 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1268 |  | 1600 | -332 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 |  | 1600 | -340 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 |  | 1600 | -406 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 |  | 1600 | -413 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 |  | 1600 | -425 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 |  | 1600 | -439 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 |  | 1600 | -443 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 |  | 1600 | -443 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1147 |  | 1600 | -453 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 |  | 1600 | -454 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1145 |  | 1600 | -455 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1132 |  | 1600 | -468 | 71 | []

## 2130Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3244
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1553 | 1600 | 1600 | -47 | 97 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1483 | 1600 | 1600 | -117 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1435 | 1600 | 1600 | -165 | 90 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1429 | 1600 | 1600 | -171 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1395 | 1600 | 1600 | -205 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1369 | 1600 | 1600 | -231 | 86 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1365 | 1600 | 1600 | -235 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1332 | 1600 | 1600 | -268 | 83 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1331 | 1600 | 1600 | -269 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1279 | 1600 | 1600 | -321 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1270 | 1600 | 1600 | -330 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1266 | 1600 | 1600 | -334 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 | 1600 | 1600 | -398 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 | 1600 | 1600 | -410 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1127 | 1600 | 1600 | -473 | 70 | []

## 2130Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3244
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1593 |  | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1553 |  | 1600 | -47 | 97 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1483 |  | 1600 | -117 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1435 |  | 1600 | -165 | 90 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1429 |  | 1600 | -171 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1395 |  | 1600 | -205 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 |  | 1600 | -230 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 |  | 1600 | -230 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1369 |  | 1600 | -231 | 86 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1365 |  | 1600 | -235 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1332 |  | 1600 | -268 | 83 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1331 |  | 1600 | -269 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1279 |  | 1600 | -321 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1270 |  | 1600 | -330 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1266 |  | 1600 | -334 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 |  | 1600 | -398 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 |  | 1600 | -410 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 |  | 1600 | -425 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 |  | 1600 | -435 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 |  | 1600 | -436 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 |  | 1600 | -441 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1147 |  | 1600 | -453 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 |  | 1600 | -460 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 |  | 1600 | -460 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1127 |  | 1600 | -473 | 70 | []

## 2230Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3352
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1566 | 1600 | 1600 | -34 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1483 | 1600 | 1600 | -117 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1463 | 1600 | 1600 | -137 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1461 | 1600 | 1600 | -139 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1415 | 1600 | 1600 | -185 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1401 | 1600 | 1600 | -199 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1394 | 1600 | 1600 | -206 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1352 | 1600 | 1600 | -248 | 85 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1285 | 1600 | 1600 | -315 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 | 1600 | 1600 | -316 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 | 1600 | 1600 | -324 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1254 | 1600 | 1600 | -346 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 | 1600 | 1600 | -383 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 | 1600 | 1600 | -402 | 75 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1168 | 1600 | 1600 | -432 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1138 | 1600 | 1600 | -462 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 | 1600 | 1600 | -470 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 | 1600 | 1600 | -470 | 71 | []

## 2230Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3352
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 |  | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1566 |  | 1600 | -34 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1483 |  | 1600 | -117 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1463 |  | 1600 | -137 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1461 |  | 1600 | -139 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1415 |  | 1600 | -185 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1401 |  | 1600 | -199 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1394 |  | 1600 | -206 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 |  | 1600 | -234 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 |  | 1600 | -234 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1352 |  | 1600 | -248 | 85 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1285 |  | 1600 | -315 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 |  | 1600 | -316 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 |  | 1600 | -324 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 |  | 1600 | -331 | 79 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1254 |  | 1600 | -346 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 |  | 1600 | -383 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 |  | 1600 | -390 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 |  | 1600 | -402 | 75 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1178 |  | 1600 | -422 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1178 |  | 1600 | -422 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1168 |  | 1600 | -432 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1138 |  | 1600 | -462 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 |  | 1600 | -470 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 |  | 1600 | -470 | 71 | []

## 2330Preventive
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3476
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1590 | 1600 | 1600 | -10 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1499 | 1600 | 1600 | -101 | 94 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1489 | 1600 | 1600 | -111 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1486 | 1600 | 1600 | -114 | 93 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1433 | 1600 | 1600 | -167 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1424 | 1600 | 1600 | -176 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1408 | 1600 | 1600 | -192 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1363 | 1600 | 1600 | -237 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1355 | 1600 | 1600 | -245 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1355 | 1600 | 1600 | -245 | 85 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1338 | 1600 | 1600 | -262 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 | 1600 | 1600 | -316 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1279 | 1600 | 1600 | -321 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1275 | 1600 | 1600 | -325 | 80 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1207 | 1600 | 1600 | -393 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1184 | 1600 | 1600 | -416 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 | 1600 | 1600 | -426 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1168 | 1600 | 1600 | -432 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1155 | 1600 | 1600 | -445 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1152 | 1600 | 1600 | -448 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1121 | 1600 | 1600 | -479 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2026-03-22 19:43
Business day: | 23.03.2026
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3476
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 |  | 1600 | -2 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1590 |  | 1600 | -10 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1499 |  | 1600 | -101 | 94 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1489 |  | 1600 | -111 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1486 |  | 1600 | -114 | 93 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1433 |  | 1600 | -167 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1424 |  | 1600 | -176 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1408 |  | 1600 | -192 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1363 |  | 1600 | -237 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1355 |  | 1600 | -245 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1355 |  | 1600 | -245 | 85 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1338 |  | 1600 | -262 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 |  | 1600 | -316 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1279 |  | 1600 | -321 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1275 |  | 1600 | -325 | 80 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1207 |  | 1600 | -393 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1184 |  | 1600 | -416 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 |  | 1600 | -417 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 |  | 1600 | -426 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1168 |  | 1600 | -432 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1155 |  | 1600 | -445 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1152 |  | 1600 | -448 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1121 |  | 1600 | -479 | 70 | []