## 0030Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3411
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1996 | 2000 | 2000 | -4 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1888 | 2000 | 2000 | -112 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1794 | 2000 | 2000 | -206 | 90 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1749 | 2000 | 2000 | -251 | 87 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1736 | 2000 | 2000 | -264 | 87 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1735 | 2000 | 2000 | -265 | 87 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1726 | 2000 | 2000 | -274 | 86 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1720 | 2000 | 2000 | -280 | 86 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1720 | 2000 | 2000 | -280 | 86 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1717 | 2000 | 2000 | -283 | 86 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1706 | 2000 | 2000 | -294 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1704 | -2000 | -2000 | -296 | 85 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 | 2000 | 2000 | -304 | 85 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1695 | 2000 | 2000 | -305 | 85 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1688 | 2000 | 2000 | -312 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1686 | -2000 | -2000 | -314 | 84 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1539 | 1836 | 1836 | -297 | 84 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1672 | 2000 | 2000 | -328 | 84 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1509 | 1836 | 1836 | -327 | 82 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 | 1836 | 1836 | -349 | 81 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 | 1836 | 1836 | -349 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1612 | 2000 | 2000 | -388 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 | 1836 | 1836 | -373 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1458 | 1836 | 1836 | -378 | 79 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1447 | 1836 | 1836 | -389 | 79 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1447 | 1836 | 1836 | -389 | 79 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 _RARAD22 _3:trf | -785 | -999 | -999 | -214 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1437 | 1836 | 1836 | -399 | 78 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1426 | 1836 | 1836 | -410 | 78 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 | 1836 | 1836 | -414 | 77 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 | 1836 | 1836 | -414 | 77 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1421 | 1836 | 1836 | -415 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1539 | 2000 | 2000 | -461 | 77 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1393 | 1836 | 1836 | -443 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1516 | 2000 | 2000 | -484 | 76 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -893 | -1248 | -1248 | -355 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -893 | -1248 | -1248 | -355 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -879 | -1248 | -1248 | -370 | 70 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -876 | -1248 | -1248 | -373 | 70 | []

## 0030Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 00:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3411
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1996 |  | 2000 | -4 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1888 |  | 2000 | -112 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1794 |  | 2000 | -206 | 90 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1749 |  | 2000 | -251 | 87 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1736 |  | 2000 | -264 | 87 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1735 |  | 2000 | -265 | 87 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1726 |  | 2000 | -274 | 86 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1720 |  | 2000 | -280 | 86 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1720 |  | 2000 | -280 | 86 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1717 |  | 2000 | -283 | 86 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1706 |  | 2000 | -294 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1704 |  | -2000 | -296 | 85 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 |  | 2000 | -304 | 85 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1695 |  | 2000 | -305 | 85 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1688 |  | 2000 | -312 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1686 |  | -2000 | -314 | 84 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1539 |  | 1836 | -297 | 84 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1672 |  | 2000 | -328 | 84 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1509 |  | 1836 | -327 | 82 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 |  | 1836 | -349 | 81 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 |  | 1836 | -349 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1612 |  | 2000 | -388 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 |  | 1836 | -373 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1458 |  | 1836 | -378 | 79 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1447 |  | 1836 | -389 | 79 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1447 |  | 1836 | -389 | 79 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 _RARAD22 _3:trf | -785 |  | -999 | -214 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1437 |  | 1836 | -399 | 78 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1426 |  | 1836 | -410 | 78 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 |  | 1836 | -414 | 77 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 |  | 1836 | -414 | 77 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1421 |  | 1836 | -415 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1539 |  | 2000 | -461 | 77 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1393 |  | 1836 | -443 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1516 |  | 2000 | -484 | 76 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -893 |  | -1248 | -355 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -893 |  | -1248 | -355 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -879 |  | -1248 | -370 | 70 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -876 |  | -1248 | -373 | 70 | []

## 0130Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3432
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 | 2000 | 2000 | -3 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1885 | 2000 | 2000 | -115 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1789 | 2000 | 2000 | -211 | 89 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1748 | 2000 | 2000 | -252 | 87 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1735 | 2000 | 2000 | -265 | 87 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1735 | 2000 | 2000 | -265 | 87 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1726 | 2000 | 2000 | -274 | 86 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1725 | 2000 | 2000 | -275 | 86 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1723 | -2000 | -2000 | -277 | 86 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1719 | 2000 | 2000 | -281 | 86 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1715 | 2000 | 2000 | -285 | 86 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1712 | 2000 | 2000 | -288 | 86 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1706 | 2000 | 2000 | -294 | 85 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1705 | -2000 | -2000 | -295 | 85 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1692 | 2000 | 2000 | -308 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1547 | 1836 | 1836 | -289 | 84 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1680 | 2000 | 2000 | -320 | 84 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1668 | 2000 | 2000 | -332 | 83 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1528 | 1836 | 1836 | -308 | 83 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1513 | 1836 | 1836 | -323 | 82 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1513 | 1836 | 1836 | -323 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1480 | 1836 | 1836 | -356 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1609 | 2000 | 2000 | -391 | 80 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1465 | 1836 | 1836 | -371 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1465 | 1836 | 1836 | -371 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 | 1836 | 1836 | -374 | 80 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 | 1836 | 1836 | -375 | 80 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1440 | 1836 | 1836 | -396 | 78 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 | 1836 | 1836 | -397 | 78 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 | 1836 | 1836 | -397 | 78 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 | 1836 | 1836 | -409 | 78 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1413 | 1836 | 1836 | -423 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1532 | 2000 | 2000 | -468 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1509 | 2000 | 2000 | -491 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -907 | -1248 | -1248 | -342 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -904 | -1248 | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -900 | -1248 | -1248 | -348 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -893 | -1248 | -1248 | -355 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -893 | -1248 | -1248 | -355 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -889 | -1248 | -1248 | -359 | 71 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -889 | -1248 | -1248 | -360 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -880 | -1248 | -1248 | -368 | 71 | []

## 0130Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 01:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3432
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | notApplied
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 |  | 2000 | -3 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1885 |  | 2000 | -115 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1789 |  | 2000 | -211 | 89 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1748 |  | 2000 | -252 | 87 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1735 |  | 2000 | -265 | 87 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1735 |  | 2000 | -265 | 87 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1726 |  | 2000 | -274 | 86 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1725 |  | 2000 | -275 | 86 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1723 |  | -2000 | -277 | 86 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1719 |  | 2000 | -281 | 86 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1715 |  | 2000 | -285 | 86 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1712 |  | 2000 | -288 | 86 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1706 |  | 2000 | -294 | 85 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1705 |  | -2000 | -295 | 85 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1692 |  | 2000 | -308 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1547 |  | 1836 | -289 | 84 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1680 |  | 2000 | -320 | 84 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1668 |  | 2000 | -332 | 83 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1528 |  | 1836 | -308 | 83 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1513 |  | 1836 | -323 | 82 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1513 |  | 1836 | -323 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1480 |  | 1836 | -356 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1609 |  | 2000 | -391 | 80 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1465 |  | 1836 | -371 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1465 |  | 1836 | -371 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 |  | 1836 | -374 | 80 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 |  | 1836 | -375 | 80 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1440 |  | 1836 | -396 | 78 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 |  | 1836 | -397 | 78 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 |  | 1836 | -397 | 78 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1836 | -409 | 78 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1413 |  | 1836 | -423 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1532 |  | 2000 | -468 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1509 |  | 2000 | -491 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -907 |  | -1248 | -342 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -904 |  | -1248 | -345 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -900 |  | -1248 | -348 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -893 |  | -1248 | -355 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -893 |  | -1248 | -355 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -889 |  | -1248 | -359 | 71 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -889 |  | -1248 | -360 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -880 |  | -1248 | -368 | 71 | []

## 0230Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3381
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1993 | 2000 | 2000 | -7 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1872 | 2000 | 2000 | -128 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1772 | 2000 | 2000 | -228 | 89 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1723 | 2000 | 2000 | -277 | 86 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1719 | 2000 | 2000 | -281 | 86 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1711 | 2000 | 2000 | -289 | 86 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1710 | 2000 | 2000 | -290 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1704 | 2000 | 2000 | -296 | 85 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1702 | 2000 | 2000 | -298 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1701 | -2000 | -2000 | -299 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1693 | 2000 | 2000 | -307 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 | 2000 | 2000 | -309 | 85 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1684 | 2000 | 2000 | -316 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1683 | -2000 | -2000 | -317 | 84 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1537 | 1836 | 1836 | -299 | 84 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1664 | 2000 | 2000 | -336 | 83 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 _RARAD22 _3:trf | -830 | -999 | -999 | -169 | 83 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1649 | 2000 | 2000 | -351 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1508 | 1836 | 1836 | -328 | 82 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1640 | 2000 | 2000 | -360 | 82 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1486 | 1836 | 1836 | -350 | 81 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 | 1836 | 1836 | -351 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1460 | 1836 | 1836 | -376 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 | 1836 | 1836 | -383 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1581 | 2000 | 2000 | -419 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 | 1836 | 1836 | -401 | 78 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 | 1836 | 1836 | -403 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 | 1836 | 1836 | -403 | 78 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1421 | 1836 | 1836 | -415 | 77 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 | 1836 | 1836 | -418 | 77 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 | 1836 | 1836 | -419 | 77 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 | 1836 | 1836 | -421 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1513 | 2000 | 2000 | -487 | 76 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1386 | 1836 | 1836 | -450 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1491 | 2000 | 2000 | -509 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -895 | -1248 | -1248 | -354 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -894 | -1248 | -1248 | -354 | 72 | []

## 0230Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 02:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3381
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1993 |  | 2000 | -7 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1872 |  | 2000 | -128 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1772 |  | 2000 | -228 | 89 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1723 |  | 2000 | -277 | 86 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1719 |  | 2000 | -281 | 86 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1711 |  | 2000 | -289 | 86 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1710 |  | 2000 | -290 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1704 |  | 2000 | -296 | 85 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1702 |  | 2000 | -298 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1701 |  | -2000 | -299 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1693 |  | 2000 | -307 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 |  | 2000 | -309 | 85 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1684 |  | 2000 | -316 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1683 |  | -2000 | -317 | 84 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1537 |  | 1836 | -299 | 84 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1664 |  | 2000 | -336 | 83 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 _RARAD22 _3:trf | -830 |  | -999 | -169 | 83 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1649 |  | 2000 | -351 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1508 |  | 1836 | -328 | 82 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1640 |  | 2000 | -360 | 82 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1486 |  | 1836 | -350 | 81 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 |  | 1836 | -351 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1460 |  | 1836 | -376 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 |  | 1836 | -383 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1581 |  | 2000 | -419 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1836 | -401 | 78 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 |  | 1836 | -403 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 |  | 1836 | -403 | 78 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1421 |  | 1836 | -415 | 77 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 |  | 1836 | -418 | 77 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 |  | 1836 | -419 | 77 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 |  | 1836 | -421 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1513 |  | 2000 | -487 | 76 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1386 |  | 1836 | -450 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1491 |  | 2000 | -509 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -895 |  | -1248 | -354 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -894 |  | -1248 | -354 | 72 | []

## 0330Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3382
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1998 | 2000 | 2000 | -2 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1874 | 2000 | 2000 | -126 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1771 | 2000 | 2000 | -229 | 89 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1718 | 2000 | 2000 | -282 | 86 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1717 | 2000 | 2000 | -283 | 86 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1709 | 2000 | 2000 | -291 | 85 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 _RARAD22 _3:trf | -852 | -999 | -999 | -147 | 85 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1705 | 2000 | 2000 | -295 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1703 | 2000 | 2000 | -297 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1555 | 1836 | 1836 | -281 | 85 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1693 | 2000 | 2000 | -307 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1691 | -2000 | -2000 | -309 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1690 | 2000 | 2000 | -310 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1688 | 2000 | 2000 | -312 | 84 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1675 | 2000 | 2000 | -325 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1673 | -2000 | -2000 | -327 | 84 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1527 | 1836 | 1836 | -309 | 83 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1658 | 2000 | 2000 | -342 | 83 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1644 | 2000 | 2000 | -356 | 82 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1503 | 1836 | 1836 | -333 | 82 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1503 | 1836 | 1836 | -333 | 82 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1634 | 2000 | 2000 | -366 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1477 | 1836 | 1836 | -359 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 | 1836 | 1836 | -367 | 80 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 | 1836 | 1836 | -384 | 79 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1446 | 1836 | 1836 | -390 | 79 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1446 | 1836 | 1836 | -390 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1575 | 2000 | 2000 | -425 | 79 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 | 1836 | 1836 | -400 | 78 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 | 1836 | 1836 | -401 | 78 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 | 1836 | 1836 | -403 | 78 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1431 | 1836 | 1836 | -405 | 78 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 | 1836 | 1836 | -436 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1512 | 2000 | 2000 | -488 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1489 | 2000 | 2000 | -511 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -895 | -1248 | -1248 | -353 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -895 | -1248 | -1248 | -354 | 72 | []

## 0330Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 03:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3382
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1998 |  | 2000 | -2 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1874 |  | 2000 | -126 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1771 |  | 2000 | -229 | 89 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1718 |  | 2000 | -282 | 86 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1717 |  | 2000 | -283 | 86 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1709 |  | 2000 | -291 | 85 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 _RARAD22 _3:trf | -852 |  | -999 | -147 | 85 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1705 |  | 2000 | -295 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1703 |  | 2000 | -297 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1555 |  | 1836 | -281 | 85 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1693 |  | 2000 | -307 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1691 |  | -2000 | -309 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1690 |  | 2000 | -310 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1688 |  | 2000 | -312 | 84 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1675 |  | 2000 | -325 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1673 |  | -2000 | -327 | 84 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1527 |  | 1836 | -309 | 83 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1658 |  | 2000 | -342 | 83 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1644 |  | 2000 | -356 | 82 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1503 |  | 1836 | -333 | 82 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1503 |  | 1836 | -333 | 82 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1634 |  | 2000 | -366 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1477 |  | 1836 | -359 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 |  | 1836 | -367 | 80 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1836 | -384 | 79 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1446 |  | 1836 | -390 | 79 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1446 |  | 1836 | -390 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1575 |  | 2000 | -425 | 79 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 |  | 1836 | -400 | 78 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1836 | -401 | 78 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 |  | 1836 | -403 | 78 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1431 |  | 1836 | -405 | 78 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 |  | 1836 | -436 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1512 |  | 2000 | -488 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1489 |  | 2000 | -511 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -895 |  | -1248 | -353 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -895 |  | -1248 | -354 | 72 | []

## 0430Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3281
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 | 2000 | 2000 | -5 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1876 | 2000 | 2000 | -124 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1776 | 2000 | 2000 | -224 | 89 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1714 | 2000 | 2000 | -286 | 86 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1713 | 2000 | 2000 | -287 | 86 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1705 | 2000 | 2000 | -295 | 85 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1700 | 2000 | 2000 | -300 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1698 | 2000 | 2000 | -302 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1693 | 2000 | 2000 | -307 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 | 2000 | 2000 | -309 | 85 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1661 | 2000 | 2000 | -339 | 83 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1660 | 2000 | 2000 | -340 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1658 | -2000 | -2000 | -342 | 83 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1655 | 2000 | 2000 | -345 | 83 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1642 | 2000 | 2000 | -358 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1641 | -2000 | -2000 | -359 | 82 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1506 | 1836 | 1836 | -330 | 82 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1632 | 2000 | 2000 | -368 | 82 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1466 | 1836 | 1836 | -370 | 80 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1454 | 1836 | 1836 | -382 | 79 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 | 1836 | 1836 | -383 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1572 | 2000 | 2000 | -428 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 | 1836 | 1836 | -400 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1424 | -1836 | -1836 | -412 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 | 1836 | 1836 | -431 | 77 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 | 1836 | 1836 | -431 | 77 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1403 | 1836 | 1836 | -433 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1517 | 2000 | 2000 | -483 | 76 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1390 | 1836 | 1836 | -446 | 76 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1387 | 1836 | 1836 | -449 | 76 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1384 | 1836 | 1836 | -452 | 75 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1384 | 1836 | 1836 | -452 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1496 | 2000 | 2000 | -504 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1358 | 1836 | 1836 | -478 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -893 | -1248 | -1248 | -355 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -893 | -1248 | -1248 | -355 | 72 | []

## 0430Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 04:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3281
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 |  | 2000 | -5 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1876 |  | 2000 | -124 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1776 |  | 2000 | -224 | 89 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1714 |  | 2000 | -286 | 86 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1713 |  | 2000 | -287 | 86 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1705 |  | 2000 | -295 | 85 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1700 |  | 2000 | -300 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1698 |  | 2000 | -302 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1693 |  | 2000 | -307 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 |  | 2000 | -309 | 85 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1661 |  | 2000 | -339 | 83 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1660 |  | 2000 | -340 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1658 |  | -2000 | -342 | 83 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1655 |  | 2000 | -345 | 83 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1642 |  | 2000 | -358 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1641 |  | -2000 | -359 | 82 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1506 |  | 1836 | -330 | 82 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1632 |  | 2000 | -368 | 82 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1466 |  | 1836 | -370 | 80 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1836 | -382 | 79 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 |  | 1836 | -383 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1572 |  | 2000 | -428 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 |  | 1836 | -400 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1424 |  | -1836 | -412 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 |  | 1836 | -431 | 77 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 |  | 1836 | -431 | 77 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1403 |  | 1836 | -433 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1517 |  | 2000 | -483 | 76 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1390 |  | 1836 | -446 | 76 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1387 |  | 1836 | -449 | 76 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1384 |  | 1836 | -452 | 75 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1384 |  | 1836 | -452 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1496 |  | 2000 | -504 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1358 |  | 1836 | -478 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -893 |  | -1248 | -355 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -893 |  | -1248 | -355 | 72 | []

## 0530Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2759
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 | 2000 | 2000 | -5 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1881 | 2000 | 2000 | -119 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1781 | 2000 | 2000 | -219 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 | 1836 | 1836 | -266 | 86 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1690 | 2000 | 2000 | -310 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1680 | 2000 | 2000 | -320 | 84 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1679 | 2000 | 2000 | -321 | 84 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1674 | 2000 | 2000 | -326 | 84 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1669 | 2000 | 2000 | -331 | 83 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1661 | 2000 | 2000 | -339 | 83 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1659 | 2000 | 2000 | -341 | 83 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1643 | 2000 | 2000 | -357 | 82 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1599 | 2000 | 2000 | -401 | 80 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1578 | 2000 | 2000 | -422 | 79 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1434 | 1836 | 1836 | -402 | 78 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1527 | 2000 | 2000 | -473 | 76 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1513 | 2000 | 2000 | -487 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1508 | 2000 | 2000 | -492 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1383 | 1836 | 1836 | -453 | 75 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1491 | 2000 | 2000 | -509 | 75 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 | 1836 | 1836 | -468 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1488 | -2000 | -2000 | -512 | 74 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1476 | 2000 | 2000 | -524 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1474 | -2000 | -2000 | -526 | 74 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1353 | 1836 | 1836 | -483 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -919 | -1248 | -1248 | -329 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -918 | -1248 | -1248 | -330 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -913 | -1248 | -1248 | -336 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -906 | -1248 | -1248 | -343 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -897 | -1248 | -1248 | -352 | 72 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1312 | 1836 | 1836 | -524 | 71 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1312 | 1836 | 1836 | -524 | 71 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1308 | 1836 | 1836 | -528 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -888 | -1248 | -1248 | -360 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -888 | -1248 | -1248 | -360 | 71 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1288 | 1836 | 1836 | -548 | 70 | []

## 0530Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 05:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2759
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 |  | 2000 | -5 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1881 |  | 2000 | -119 | 94 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1781 |  | 2000 | -219 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 |  | 1836 | -266 | 86 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1690 |  | 2000 | -310 | 85 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1680 |  | 2000 | -320 | 84 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1679 |  | 2000 | -321 | 84 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1674 |  | 2000 | -326 | 84 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1669 |  | 2000 | -331 | 83 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1661 |  | 2000 | -339 | 83 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1659 |  | 2000 | -341 | 83 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1643 |  | 2000 | -357 | 82 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1599 |  | 2000 | -401 | 80 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1578 |  | 2000 | -422 | 79 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1434 |  | 1836 | -402 | 78 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1527 |  | 2000 | -473 | 76 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1513 |  | 2000 | -487 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1508 |  | 2000 | -492 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1383 |  | 1836 | -453 | 75 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1491 |  | 2000 | -509 | 75 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 |  | 1836 | -468 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1488 |  | -2000 | -512 | 74 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1476 |  | 2000 | -524 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1474 |  | -2000 | -526 | 74 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1353 |  | 1836 | -483 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -919 |  | -1248 | -329 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -918 |  | -1248 | -330 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -913 |  | -1248 | -336 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -906 |  | -1248 | -343 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -897 |  | -1248 | -352 | 72 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1312 |  | 1836 | -524 | 71 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1312 |  | 1836 | -524 | 71 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1308 |  | 1836 | -528 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -888 |  | -1248 | -360 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -888 |  | -1248 | -360 | 71 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1288 |  | 1836 | -548 | 70 | []

## 0630Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2798
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1999 | 2000 | 2000 | -1 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1750 | 1836 | 1836 | -86 | 95 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1893 | 2000 | 2000 | -107 | 95 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1806 | 2000 | 2000 | -194 | 90 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1752 | 2000 | 2000 | -248 | 88 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 | 2000 | 2000 | -304 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1688 | 2000 | 2000 | -312 | 84 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1675 | 2000 | 2000 | -325 | 84 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1532 | 1836 | 1836 | -304 | 83 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1666 | 2000 | 2000 | -334 | 83 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1658 | 2000 | 2000 | -342 | 83 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1645 | 2000 | 2000 | -355 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1498 | 1836 | 1836 | -338 | 82 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1628 | 2000 | 2000 | -372 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1486 | 1836 | 1836 | -350 | 81 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1588 | 2000 | 2000 | -412 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1445 | 1836 | 1836 | -391 | 79 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1572 | 2000 | 2000 | -428 | 79 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 | 1836 | 1836 | -394 | 79 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 | 1836 | 1836 | -394 | 79 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 | 1836 | 1836 | -401 | 78 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1551 | 2000 | 2000 | -449 | 78 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1534 | 2000 | 2000 | -466 | 77 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 | 1836 | 1836 | -436 | 76 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1390 | 1836 | 1836 | -446 | 76 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1508 | 2000 | 2000 | -492 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -936 | -1248 | -1248 | -313 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -934 | -1248 | -1248 | -314 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1370 | 1836 | 1836 | -466 | 75 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1370 | 1836 | 1836 | -466 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -929 | -1248 | -1248 | -320 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -921 | -1248 | -1248 | -328 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -919 | -1248 | -1248 | -330 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -912 | -1248 | -1248 | -337 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -902 | -1248 | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -880 | -1248 | -1248 | -368 | 70 | []

## 0630Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 06:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2798
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1999 |  | 2000 | -1 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1750 |  | 1836 | -86 | 95 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1893 |  | 2000 | -107 | 95 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1806 |  | 2000 | -194 | 90 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1752 |  | 2000 | -248 | 88 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 |  | 2000 | -304 | 85 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1688 |  | 2000 | -312 | 84 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1675 |  | 2000 | -325 | 84 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1532 |  | 1836 | -304 | 83 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1666 |  | 2000 | -334 | 83 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1658 |  | 2000 | -342 | 83 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1645 |  | 2000 | -355 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1498 |  | 1836 | -338 | 82 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1628 |  | 2000 | -372 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1486 |  | 1836 | -350 | 81 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1588 |  | 2000 | -412 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1836 | -391 | 79 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1572 |  | 2000 | -428 | 79 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 |  | 1836 | -394 | 79 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 |  | 1836 | -394 | 79 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1836 | -401 | 78 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1551 |  | 2000 | -449 | 78 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1534 |  | 2000 | -466 | 77 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 |  | 1836 | -436 | 76 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1390 |  | 1836 | -446 | 76 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1508 |  | 2000 | -492 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -936 |  | -1248 | -313 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -934 |  | -1248 | -314 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1370 |  | 1836 | -466 | 75 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1370 |  | 1836 | -466 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -929 |  | -1248 | -320 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -921 |  | -1248 | -328 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -919 |  | -1248 | -330 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -912 |  | -1248 | -337 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -902 |  | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -880 |  | -1248 | -368 | 70 | []

## 0730Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3400
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1387 | 1890 | 1890 | -503 | 73 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1387 | 1890 | 1890 | -503 | 73 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1343 | 1836 | 1836 | -493 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -910 | -1248 | -1248 | -338 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -910 | -1248 | -1248 | -339 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1381 | 1920 | 1920 | -539 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -898 | -1248 | -1248 | -351 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -898 | -1248 | -1248 | -351 | 72 | []
RO_CO_00046 | N-1 OHL 400 kV Djerdap - Drmno | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1379 | 1920 | 1920 | -541 | 72 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1378 | 1920 | 1920 | -542 | 72 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1378 | 1920 | 1920 | -542 | 72 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [DIR] OHL 400 kV Lacu Sarat - Gura Ialomitei | RGIAL11 _RLACS41 _1:line | 1146 | 1600 | 1600 | -454 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -891 | -1248 | -1248 | -357 | 71 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -891 | -1248 | -1248 | -357 | 71 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -887 | -1248 | -1248 | -362 | 71 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -883 | -1248 | -1248 | -366 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -878 | -1248 | -1248 | -371 | 70 | []

## 0730Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 07:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3400
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1387 |  | 1890 | -503 | 73 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1387 |  | 1890 | -503 | 73 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1343 |  | 1836 | -493 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -910 |  | -1248 | -338 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -910 |  | -1248 | -339 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1381 |  | 1920 | -539 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -898 |  | -1248 | -351 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -898 |  | -1248 | -351 | 72 | []
RO_CO_00046 | N-1 OHL 400 kV Djerdap - Drmno | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1379 |  | 1920 | -541 | 72 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1378 |  | 1920 | -542 | 72 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1378 |  | 1920 | -542 | 72 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [DIR] OHL 400 kV Lacu Sarat - Gura Ialomitei | RGIAL11 _RLACS41 _1:line | 1146 |  | 1600 | -454 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -891 |  | -1248 | -357 | 71 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -891 |  | -1248 | -357 | 71 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -887 |  | -1248 | -362 | 71 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -883 |  | -1248 | -366 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -878 |  | -1248 | -371 | 70 | []

## 0830Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3442
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1410 | 1890 | 1890 | -480 | 75 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1410 | 1890 | 1890 | -480 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -912 | -1248 | -1248 | -337 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -912 | -1248 | -1248 | -337 | 73 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1400 | 1920 | 1920 | -520 | 73 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1400 | 1920 | 1920 | -520 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -910 | -1248 | -1248 | -338 | 73 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1339 | 1836 | 1836 | -497 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -910 | -1248 | -1248 | -339 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -905 | -1248 | -1248 | -343 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -901 | -1248 | -1248 | -347 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -897 | -1248 | -1248 | -352 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1376 | 1920 | 1920 | -544 | 72 | []
RO_CO_00046 | N-1 OHL 400 kV Djerdap - Drmno | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1375 | 1920 | 1920 | -545 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -892 | -1248 | -1248 | -356 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -892 | -1248 | -1248 | -357 | 71 | []

## 0830Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 08:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3442
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1410 |  | 1890 | -480 | 75 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1410 |  | 1890 | -480 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -912 |  | -1248 | -337 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -912 |  | -1248 | -337 | 73 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1400 |  | 1920 | -520 | 73 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1400 |  | 1920 | -520 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -910 |  | -1248 | -338 | 73 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1339 |  | 1836 | -497 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -910 |  | -1248 | -339 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -905 |  | -1248 | -343 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -901 |  | -1248 | -347 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -897 |  | -1248 | -352 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1376 |  | 1920 | -544 | 72 | []
RO_CO_00046 | N-1 OHL 400 kV Djerdap - Drmno | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1375 |  | 1920 | -545 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -892 |  | -1248 | -356 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -892 |  | -1248 | -357 | 71 | []

## 0930Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3581
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1491 | 1890 | 1890 | -399 | 79 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1491 | 1890 | 1890 | -399 | 79 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1482 | 1920 | 1920 | -438 | 77 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1482 | 1920 | 1920 | -438 | 77 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -942 | -1248 | -1248 | -307 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -941 | -1248 | -1248 | -307 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -935 | -1248 | -1248 | -314 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -931 | -1248 | -1248 | -317 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -926 | -1248 | -1248 | -322 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -922 | -1248 | -1248 | -326 | 74 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | 1474 | 2000 | 2000 | -526 | 74 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1474 | -2000 | -2000 | -526 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1468 | -2000 | -2000 | -532 | 73 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1468 | 2000 | 2000 | -532 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -907 | -1248 | -1248 | -342 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -906 | -1248 | -1248 | -342 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -889 | -1248 | -1248 | -359 | 71 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1301 | 1836 | 1836 | -535 | 71 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [DIR] OHL 400 kV Isaccea - Tulcea Vest | RTULC41 _RIS1A41 _1:line | -1133 | -1600 | -1600 | -467 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1350 | 1920 | 1920 | -570 | 70 | []
RO_CO_00046 | N-1 OHL 400 kV Djerdap - Drmno | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1349 | 1920 | 1920 | -571 | 70 | []

## 0930Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 09:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3581
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1491 |  | 1890 | -399 | 79 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1491 |  | 1890 | -399 | 79 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1482 |  | 1920 | -438 | 77 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1482 |  | 1920 | -438 | 77 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -942 |  | -1248 | -307 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -941 |  | -1248 | -307 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -935 |  | -1248 | -314 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -931 |  | -1248 | -317 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -926 |  | -1248 | -322 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -922 |  | -1248 | -326 | 74 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | 1474 |  | 2000 | -526 | 74 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1474 |  | -2000 | -526 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1468 |  | -2000 | -532 | 73 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1468 |  | 2000 | -532 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -907 |  | -1248 | -342 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -906 |  | -1248 | -342 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -889 |  | -1248 | -359 | 71 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1301 |  | 1836 | -535 | 71 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [DIR] OHL 400 kV Isaccea - Tulcea Vest | RTULC41 _RIS1A41 _1:line | -1133 |  | -1600 | -467 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1350 |  | 1920 | -570 | 70 | []
RO_CO_00046 | N-1 OHL 400 kV Djerdap - Drmno | [RO-RS] [DIR] TIE 400 kV Resita-Pancevo c1 | RRES141 _XRE_PA11_1:line | 1349 |  | 1920 | -571 | 70 | []

## 1030Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3679
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1637 | 1890 | 1890 | -253 | 87 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1637 | 1890 | 1890 | -253 | 87 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1629 | 1920 | 1920 | -291 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1629 | 1920 | 1920 | -291 | 85 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | 1615 | 2000 | 2000 | -385 | 81 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1615 | -2000 | -2000 | -385 | 81 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1608 | -2000 | -2000 | -392 | 80 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1607 | 2000 | 2000 | -393 | 80 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -964 | -1248 | -1248 | -284 | 77 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -963 | -1248 | -1248 | -286 | 77 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -956 | -1248 | -1248 | -292 | 77 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -955 | -1248 | -1248 | -294 | 76 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -949 | -1248 | -1248 | -300 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -946 | -1248 | -1248 | -303 | 76 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -905 | -1248 | -1248 | -343 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -904 | -1248 | -1248 | -344 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -890 | -1248 | -1248 | -359 | 71 | []

## 1030Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 10:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3679
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1637 |  | 1890 | -253 | 87 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1637 |  | 1890 | -253 | 87 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1629 |  | 1920 | -291 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1629 |  | 1920 | -291 | 85 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | 1615 |  | 2000 | -385 | 81 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1615 |  | -2000 | -385 | 81 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1608 |  | -2000 | -392 | 80 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1607 |  | 2000 | -393 | 80 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -964 |  | -1248 | -284 | 77 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -963 |  | -1248 | -286 | 77 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -956 |  | -1248 | -292 | 77 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -955 |  | -1248 | -294 | 76 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -949 |  | -1248 | -300 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -946 |  | -1248 | -303 | 76 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -905 |  | -1248 | -343 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -904 |  | -1248 | -344 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -890 |  | -1248 | -359 | 71 | []

## 1130Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3784
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1822 | 1890 | 1890 | -68 | 96 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1822 | 1890 | 1890 | -68 | 96 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1815 | 1920 | 1920 | -105 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1815 | 1920 | 1920 | -105 | 95 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | 1736 | 2000 | 2000 | -264 | 87 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1736 | -2000 | -2000 | -264 | 87 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1727 | -2000 | -2000 | -273 | 86 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1727 | 2000 | 2000 | -273 | 86 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -986 | -1248 | -1248 | -263 | 79 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -983 | -1248 | -1248 | -265 | 79 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -978 | -1248 | -1248 | -271 | 78 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -977 | -1248 | -1248 | -272 | 78 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -970 | -1248 | -1248 | -278 | 78 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -968 | -1248 | -1248 | -280 | 78 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -902 | -1248 | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -890 | -1248 | -1248 | -358 | 71 | []

## 1130Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 11:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3784
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1822 |  | 1890 | -68 | 96 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1822 |  | 1890 | -68 | 96 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1815 |  | 1920 | -105 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1815 |  | 1920 | -105 | 95 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | 1736 |  | 2000 | -264 | 87 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1736 |  | -2000 | -264 | 87 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1727 |  | -2000 | -273 | 86 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1727 |  | 2000 | -273 | 86 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -986 |  | -1248 | -263 | 79 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -983 |  | -1248 | -265 | 79 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -978 |  | -1248 | -271 | 78 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -977 |  | -1248 | -272 | 78 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -970 |  | -1248 | -278 | 78 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -968 |  | -1248 | -280 | 78 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -902 |  | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -890 |  | -1248 | -358 | 71 | []

## 1230Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3772
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1848 | 1890 | 1890 | -42 | 98 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1848 | 1890 | 1890 | -42 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1842 | 1920 | 1920 | -78 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1842 | 1920 | 1920 | -78 | 96 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | 1738 | 2000 | 2000 | -262 | 87 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1738 | -2000 | -2000 | -262 | 87 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1730 | -2000 | -2000 | -270 | 86 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1730 | 2000 | 2000 | -270 | 86 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -990 | -1248 | -1248 | -258 | 79 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -988 | -1248 | -1248 | -261 | 79 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -983 | -1248 | -1248 | -266 | 79 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -981 | -1248 | -1248 | -268 | 79 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -975 | -1248 | -1248 | -274 | 78 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -973 | -1248 | -1248 | -275 | 78 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -902 | -1248 | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -891 | -1248 | -1248 | -358 | 71 | []

## 1230Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3772
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1848 |  | 1890 | -42 | 98 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1848 |  | 1890 | -42 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1842 |  | 1920 | -78 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1842 |  | 1920 | -78 | 96 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | 1738 |  | 2000 | -262 | 87 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1738 |  | -2000 | -262 | 87 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1730 |  | -2000 | -270 | 86 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1730 |  | 2000 | -270 | 86 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -990 |  | -1248 | -258 | 79 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -988 |  | -1248 | -261 | 79 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -983 |  | -1248 | -266 | 79 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -981 |  | -1248 | -268 | 79 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -975 |  | -1248 | -274 | 78 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -973 |  | -1248 | -275 | 78 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -902 |  | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -891 |  | -1248 | -358 | 71 | []

## 1330Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3692
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1798 | 1890 | 1890 | -92 | 95 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1798 | 1890 | 1890 | -92 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1792 | 1920 | 1920 | -128 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1792 | 1920 | 1920 | -128 | 93 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -960 | -1248 | -1248 | -289 | 77 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -958 | -1248 | -1248 | -290 | 77 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -952 | -1248 | -1248 | -297 | 76 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -951 | -1248 | -1248 | -298 | 76 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -944 | -1248 | -1248 | -304 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -942 | -1248 | -1248 | -307 | 75 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | 1502 | 2000 | 2000 | -498 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1502 | -2000 | -2000 | -498 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1495 | -2000 | -2000 | -505 | 75 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1495 | 2000 | 2000 | -505 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -904 | -1248 | -1248 | -344 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -889 | -1248 | -1248 | -360 | 71 | []

## 1330Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3692
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1798 |  | 1890 | -92 | 95 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1798 |  | 1890 | -92 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1792 |  | 1920 | -128 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1792 |  | 1920 | -128 | 93 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -960 |  | -1248 | -289 | 77 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -958 |  | -1248 | -290 | 77 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -952 |  | -1248 | -297 | 76 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -951 |  | -1248 | -298 | 76 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -944 |  | -1248 | -304 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -942 |  | -1248 | -307 | 75 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | 1502 |  | 2000 | -498 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1502 |  | -2000 | -498 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1495 |  | -2000 | -505 | 75 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | 1495 |  | 2000 | -505 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -904 |  | -1248 | -344 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -889 |  | -1248 | -360 | 71 | []

## 1430Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3570
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1692 | 1890 | 1890 | -198 | 90 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1692 | 1890 | 1890 | -198 | 90 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1685 | 1920 | 1920 | -235 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1685 | 1920 | 1920 | -235 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -948 | -1248 | -1248 | -301 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -947 | -1248 | -1248 | -302 | 76 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -940 | -1248 | -1248 | -308 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -938 | -1248 | -1248 | -311 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -932 | -1248 | -1248 | -316 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -929 | -1248 | -1248 | -320 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -907 | -1248 | -1248 | -341 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -906 | -1248 | -1248 | -342 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -891 | -1248 | -1248 | -358 | 71 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [DIR] OHL 400 kV Lacu Sarat - Gura Ialomitei | RGIAL11 _RLACS41 _1:line | 1126 | 1600 | 1600 | -474 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3570
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1692 |  | 1890 | -198 | 90 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1692 |  | 1890 | -198 | 90 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1685 |  | 1920 | -235 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1685 |  | 1920 | -235 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -948 |  | -1248 | -301 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -947 |  | -1248 | -302 | 76 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -940 |  | -1248 | -308 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -938 |  | -1248 | -311 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -932 |  | -1248 | -316 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -929 |  | -1248 | -320 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -907 |  | -1248 | -341 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -906 |  | -1248 | -342 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -891 |  | -1248 | -358 | 71 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [DIR] OHL 400 kV Lacu Sarat - Gura Ialomitei | RGIAL11 _RLACS41 _1:line | 1126 |  | 1600 | -474 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3527
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1831 | 1890 | 1890 | -59 | 97 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1831 | 1890 | 1890 | -59 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1824 | 1920 | 1920 | -96 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1824 | 1920 | 1920 | -96 | 95 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -953 | -1248 | -1248 | -296 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -951 | -1248 | -1248 | -297 | 76 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -944 | -1248 | -1248 | -304 | 76 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -944 | -1248 | -1248 | -304 | 76 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -938 | -1248 | -1248 | -311 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -935 | -1248 | -1248 | -313 | 75 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [DIR] OHL 400 kV Lacu Sarat - Gura Ialomitei | RGIAL11 _RLACS41 _1:line | 1197 | 1600 | 1600 | -403 | 75 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [DIR] OHL 400 kV Isaccea - Tulcea Vest | RTULC41 _RIS1A41 _1:line | -1160 | -1600 | -1600 | -440 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 | -1248 | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -902 | -1248 | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -889 | -1248 | -1248 | -360 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3527
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1831 |  | 1890 | -59 | 97 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1831 |  | 1890 | -59 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1824 |  | 1920 | -96 | 95 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1824 |  | 1920 | -96 | 95 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -953 |  | -1248 | -296 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -951 |  | -1248 | -297 | 76 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -944 |  | -1248 | -304 | 76 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -944 |  | -1248 | -304 | 76 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -938 |  | -1248 | -311 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -935 |  | -1248 | -313 | 75 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [DIR] OHL 400 kV Lacu Sarat - Gura Ialomitei | RGIAL11 _RLACS41 _1:line | 1197 |  | 1600 | -403 | 75 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [DIR] OHL 400 kV Isaccea - Tulcea Vest | RTULC41 _RIS1A41 _1:line | -1160 |  | -1600 | -440 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -903 |  | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -902 |  | -1248 | -346 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -889 |  | -1248 | -360 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2861
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 | 2000 | 2000 | -5 | 100 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1994 | 2000 | 2000 | -6 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1968 | 2000 | 2000 | -32 | 98 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1921 | 2000 | 2000 | -79 | 96 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1839 | 2000 | 2000 | -161 | 92 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1825 | 2000 | 2000 | -175 | 91 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1793 | 2000 | 2000 | -207 | 90 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1773 | 2000 | 2000 | -227 | 89 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1762 | 2000 | 2000 | -238 | 88 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1755 | 2000 | 2000 | -245 | 88 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1752 | 2000 | 2000 | -248 | 88 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1743 | 2000 | 2000 | -257 | 87 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1732 | 2000 | 2000 | -268 | 87 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1697 | 2000 | 2000 | -303 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1676 | 2000 | 2000 | -324 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1658 | 2000 | 2000 | -342 | 83 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -937 | -1248 | -1248 | -312 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -933 | -1248 | -1248 | -315 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -930 | -1248 | -1248 | -319 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -927 | -1248 | -1248 | -322 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -921 | -1248 | -1248 | -327 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -921 | -1248 | -1248 | -328 | 74 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1437 | 2000 | 2000 | -563 | 72 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1435 | -2000 | -2000 | -565 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -893 | -1248 | -1248 | -356 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -892 | -1248 | -1248 | -356 | 71 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1423 | 2000 | 2000 | -577 | 71 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1421 | -2000 | -2000 | -579 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -882 | -1248 | -1248 | -367 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2861
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1995 |  | 2000 | -5 | 100 | []
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1994 |  | 2000 | -6 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1968 |  | 2000 | -32 | 98 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1921 |  | 2000 | -79 | 96 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1839 |  | 2000 | -161 | 92 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1825 |  | 2000 | -175 | 91 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1793 |  | 2000 | -207 | 90 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1773 |  | 2000 | -227 | 89 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1762 |  | 2000 | -238 | 88 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1755 |  | 2000 | -245 | 88 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1752 |  | 2000 | -248 | 88 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1743 |  | 2000 | -257 | 87 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1732 |  | 2000 | -268 | 87 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1697 |  | 2000 | -303 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1676 |  | 2000 | -324 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1658 |  | 2000 | -342 | 83 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -937 |  | -1248 | -312 | 75 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -933 |  | -1248 | -315 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -930 |  | -1248 | -319 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -927 |  | -1248 | -322 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -921 |  | -1248 | -327 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -921 |  | -1248 | -328 | 74 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1437 |  | 2000 | -563 | 72 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1435 |  | -2000 | -565 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -893 |  | -1248 | -356 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -892 |  | -1248 | -356 | 71 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1423 |  | 2000 | -577 | 71 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1421 |  | -2000 | -579 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -882 |  | -1248 | -367 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2606
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 | 2000 | 2000 | -3 | 100 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1988 | 2000 | 2000 | -12 | 99 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1962 | 2000 | 2000 | -38 | 98 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1913 | 2000 | 2000 | -87 | 96 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1805 | 2000 | 2000 | -195 | 90 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1791 | 2000 | 2000 | -209 | 90 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1718 | 2000 | 2000 | -282 | 86 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1715 | 2000 | 2000 | -285 | 86 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1711 | 2000 | 2000 | -289 | 86 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1701 | 2000 | 2000 | -299 | 85 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 | 2000 | 2000 | -309 | 85 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1684 | 2000 | 2000 | -316 | 84 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1679 | 2000 | 2000 | -321 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1662 | 2000 | 2000 | -338 | 83 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1647 | 2000 | 2000 | -353 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1622 | 2000 | 2000 | -378 | 81 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -901 | -1248 | -1248 | -347 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -895 | -1248 | -1248 | -353 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -895 | -1248 | -1248 | -353 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -895 | -1248 | -1248 | -354 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -895 | -1248 | -1248 | -354 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -888 | -1248 | -1248 | -360 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -886 | -1248 | -1248 | -362 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -882 | -1248 | -1248 | -367 | 71 | []

## 1730Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2606
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 |  | 2000 | -3 | 100 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1988 |  | 2000 | -12 | 99 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1962 |  | 2000 | -38 | 98 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1913 |  | 2000 | -87 | 96 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1805 |  | 2000 | -195 | 90 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1791 |  | 2000 | -209 | 90 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1718 |  | 2000 | -282 | 86 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1715 |  | 2000 | -285 | 86 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1711 |  | 2000 | -289 | 86 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1701 |  | 2000 | -299 | 85 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1691 |  | 2000 | -309 | 85 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1684 |  | 2000 | -316 | 84 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1679 |  | 2000 | -321 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1662 |  | 2000 | -338 | 83 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1647 |  | 2000 | -353 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1622 |  | 2000 | -378 | 81 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -903 |  | -1248 | -345 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -901 |  | -1248 | -347 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -895 |  | -1248 | -353 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -895 |  | -1248 | -353 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -895 |  | -1248 | -354 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -895 |  | -1248 | -354 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -888 |  | -1248 | -360 | 71 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -886 |  | -1248 | -362 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -882 |  | -1248 | -367 | 71 | []

## 1830Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2747
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 | 2000 | 2000 | -3 | 100 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1959 | 2000 | 2000 | -41 | 98 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1952 | 2000 | 2000 | -48 | 98 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1765 | 1836 | 1836 | -71 | 96 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1890 | 2000 | 2000 | -110 | 95 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1781 | 2000 | 2000 | -219 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1764 | 2000 | 2000 | -236 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1609 | 1836 | 1836 | -227 | 88 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1700 | 2000 | 2000 | -300 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1693 | 2000 | 2000 | -307 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1685 | 2000 | 2000 | -315 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1538 | 1836 | 1836 | -298 | 84 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1672 | 2000 | 2000 | -328 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1648 | 2000 | 2000 | -352 | 82 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1646 | 2000 | 2000 | -354 | 82 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1506 | 1836 | 1836 | -330 | 82 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1638 | 2000 | 2000 | -362 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1634 | 2000 | 2000 | -366 | 82 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1633 | 2000 | 2000 | -367 | 82 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1476 | 1836 | 1836 | -360 | 80 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 | 1836 | 1836 | -367 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 | 1836 | 1836 | -375 | 80 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 | 1836 | 1836 | -375 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 | 2000 | 2000 | -432 | 78 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1425 | 1836 | 1836 | -411 | 78 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 | 1836 | 1836 | -427 | 77 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1392 | 1836 | 1836 | -444 | 76 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1392 | 1836 | 1836 | -444 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -920 | -1248 | -1248 | -329 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -918 | -1248 | -1248 | -331 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -913 | -1248 | -1248 | -336 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -904 | -1248 | -1248 | -344 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -902 | -1248 | -1248 | -346 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -895 | -1248 | -1248 | -353 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -888 | -1248 | -1248 | -361 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -887 | -1248 | -1248 | -361 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2747
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 |  | 2000 | -3 | 100 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1959 |  | 2000 | -41 | 98 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1952 |  | 2000 | -48 | 98 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1765 |  | 1836 | -71 | 96 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1890 |  | 2000 | -110 | 95 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1781 |  | 2000 | -219 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1764 |  | 2000 | -236 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1609 |  | 1836 | -227 | 88 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1700 |  | 2000 | -300 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1693 |  | 2000 | -307 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1685 |  | 2000 | -315 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1538 |  | 1836 | -298 | 84 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1672 |  | 2000 | -328 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1648 |  | 2000 | -352 | 82 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1646 |  | 2000 | -354 | 82 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1506 |  | 1836 | -330 | 82 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1638 |  | 2000 | -362 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1634 |  | 2000 | -366 | 82 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1633 |  | 2000 | -367 | 82 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1476 |  | 1836 | -360 | 80 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 |  | 1836 | -367 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 |  | 1836 | -375 | 80 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 |  | 1836 | -375 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1568 |  | 2000 | -432 | 78 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1425 |  | 1836 | -411 | 78 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 |  | 1836 | -427 | 77 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1392 |  | 1836 | -444 | 76 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1392 |  | 1836 | -444 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -920 |  | -1248 | -329 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -918 |  | -1248 | -331 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -913 |  | -1248 | -336 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -904 |  | -1248 | -344 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -902 |  | -1248 | -346 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -895 |  | -1248 | -353 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -888 |  | -1248 | -361 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -887 |  | -1248 | -361 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2727
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1994 | 2000 | 2000 | -6 | 100 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1950 | 2000 | 2000 | -50 | 97 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1947 | 2000 | 2000 | -53 | 97 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1885 | 2000 | 2000 | -115 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1727 | 1836 | 1836 | -109 | 94 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1775 | 2000 | 2000 | -225 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1759 | 2000 | 2000 | -241 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1583 | 1836 | 1836 | -253 | 86 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 | 2000 | 2000 | -304 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1689 | 2000 | 2000 | -311 | 84 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1680 | 2000 | 2000 | -320 | 84 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1669 | 2000 | 2000 | -331 | 83 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1644 | 2000 | 2000 | -356 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1509 | 1836 | 1836 | -327 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1642 | 2000 | 2000 | -358 | 82 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1634 | 2000 | 2000 | -366 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1629 | 2000 | 2000 | -371 | 81 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1628 | 2000 | 2000 | -372 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 | 1836 | 1836 | -357 | 81 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1448 | 1836 | 1836 | -388 | 79 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 | 1836 | 1836 | -395 | 78 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1564 | 2000 | 2000 | -436 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 | 1836 | 1836 | -400 | 78 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 | 1836 | 1836 | -409 | 78 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1397 | 1836 | 1836 | -439 | 76 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1381 | 1836 | 1836 | -455 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1363 | 1836 | 1836 | -473 | 74 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1363 | 1836 | 1836 | -473 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -918 | -1248 | -1248 | -331 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -916 | -1248 | -1248 | -333 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -911 | -1248 | -1248 | -337 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -903 | -1248 | -1248 | -346 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -901 | -1248 | -1248 | -348 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -894 | -1248 | -1248 | -355 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -888 | -1248 | -1248 | -360 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -888 | -1248 | -1248 | -361 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2727
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1994 |  | 2000 | -6 | 100 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1950 |  | 2000 | -50 | 97 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1947 |  | 2000 | -53 | 97 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1885 |  | 2000 | -115 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1727 |  | 1836 | -109 | 94 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1775 |  | 2000 | -225 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1759 |  | 2000 | -241 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1583 |  | 1836 | -253 | 86 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 |  | 2000 | -304 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1689 |  | 2000 | -311 | 84 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1680 |  | 2000 | -320 | 84 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1669 |  | 2000 | -331 | 83 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1644 |  | 2000 | -356 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1509 |  | 1836 | -327 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1642 |  | 2000 | -358 | 82 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1634 |  | 2000 | -366 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1629 |  | 2000 | -371 | 81 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1628 |  | 2000 | -372 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 |  | 1836 | -357 | 81 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1448 |  | 1836 | -388 | 79 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 |  | 1836 | -395 | 78 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1564 |  | 2000 | -436 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 |  | 1836 | -400 | 78 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1836 | -409 | 78 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1397 |  | 1836 | -439 | 76 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1381 |  | 1836 | -455 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1363 |  | 1836 | -473 | 74 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1363 |  | 1836 | -473 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -918 |  | -1248 | -331 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -916 |  | -1248 | -333 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -911 |  | -1248 | -337 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -903 |  | -1248 | -346 | 72 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -901 |  | -1248 | -348 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -894 |  | -1248 | -355 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -888 |  | -1248 | -360 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -888 |  | -1248 | -361 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2682
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1994 | 2000 | 2000 | -6 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1960 | 2000 | 2000 | -40 | 98 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1951 | 2000 | 2000 | -49 | 98 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1891 | 2000 | 2000 | -109 | 95 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1783 | 2000 | 2000 | -217 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1768 | 2000 | 2000 | -232 | 88 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1617 | 1836 | 1836 | -219 | 88 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1705 | 2000 | 2000 | -295 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1697 | 2000 | 2000 | -303 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1688 | 2000 | 2000 | -312 | 84 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1687 | 2000 | 2000 | -313 | 84 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1663 | 2000 | 2000 | -337 | 83 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1653 | 2000 | 2000 | -347 | 83 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1514 | 1836 | 1836 | -322 | 82 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1647 | 2000 | 2000 | -353 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1646 | 2000 | 2000 | -354 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1632 | 2000 | 2000 | -368 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1583 | 2000 | 2000 | -417 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 | 1836 | 1836 | -414 | 77 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1403 | 1836 | 1836 | -433 | 76 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1363 | 1836 | 1836 | -473 | 74 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1361 | 1836 | 1836 | -475 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -922 | -1248 | -1248 | -327 | 74 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1355 | 1836 | 1836 | -481 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -921 | -1248 | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -915 | -1248 | -1248 | -333 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -908 | -1248 | -1248 | -340 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -906 | -1248 | -1248 | -343 | 73 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1331 | 1836 | 1836 | -505 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -899 | -1248 | -1248 | -349 | 72 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1317 | 1836 | 1836 | -519 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -887 | -1248 | -1248 | -362 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -887 | -1248 | -1248 | -362 | 71 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1302 | 1836 | 1836 | -534 | 71 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1291 | 1836 | 1836 | -545 | 70 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1291 | 1836 | 1836 | -545 | 70 | []

## 2030Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2682
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1994 |  | 2000 | -6 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1960 |  | 2000 | -40 | 98 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1951 |  | 2000 | -49 | 98 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1891 |  | 2000 | -109 | 95 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1783 |  | 2000 | -217 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1768 |  | 2000 | -232 | 88 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1617 |  | 1836 | -219 | 88 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1705 |  | 2000 | -295 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1697 |  | 2000 | -303 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1688 |  | 2000 | -312 | 84 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1687 |  | 2000 | -313 | 84 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1663 |  | 2000 | -337 | 83 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1653 |  | 2000 | -347 | 83 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1514 |  | 1836 | -322 | 82 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1647 |  | 2000 | -353 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1646 |  | 2000 | -354 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1632 |  | 2000 | -368 | 82 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1583 |  | 2000 | -417 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 |  | 1836 | -414 | 77 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1403 |  | 1836 | -433 | 76 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1363 |  | 1836 | -473 | 74 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1361 |  | 1836 | -475 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -922 |  | -1248 | -327 | 74 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1355 |  | 1836 | -481 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -921 |  | -1248 | -328 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -915 |  | -1248 | -333 | 73 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -908 |  | -1248 | -340 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -906 |  | -1248 | -343 | 73 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1331 |  | 1836 | -505 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -899 |  | -1248 | -349 | 72 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1317 |  | 1836 | -519 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -887 |  | -1248 | -362 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -887 |  | -1248 | -362 | 71 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1302 |  | 1836 | -534 | 71 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1291 |  | 1836 | -545 | 70 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1291 |  | 1836 | -545 | 70 | []

## 2130Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2783
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1998 | 2000 | 2000 | -2 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1959 | 2000 | 2000 | -41 | 98 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1939 | 2000 | 2000 | -61 | 97 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1886 | 2000 | 2000 | -114 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1711 | 1836 | 1836 | -125 | 93 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1780 | 2000 | 2000 | -220 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1765 | 2000 | 2000 | -235 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1590 | 1836 | 1836 | -246 | 87 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1706 | 2000 | 2000 | -294 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1698 | 2000 | 2000 | -302 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1689 | 2000 | 2000 | -311 | 84 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1686 | 2000 | 2000 | -314 | 84 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1663 | 2000 | 2000 | -337 | 83 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1651 | 2000 | 2000 | -349 | 83 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1645 | 2000 | 2000 | -355 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1642 | 2000 | 2000 | -358 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1628 | 2000 | 2000 | -372 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1494 | 1836 | 1836 | -342 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 | 1836 | 1836 | -364 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1580 | 2000 | 2000 | -420 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 | 1836 | 1836 | -400 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 | 1836 | 1836 | -409 | 78 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1426 | 1836 | 1836 | -410 | 78 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 | 1836 | 1836 | -421 | 77 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1389 | 1836 | 1836 | -447 | 76 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1375 | 1836 | 1836 | -461 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1360 | 1836 | 1836 | -476 | 74 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1360 | 1836 | 1836 | -476 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -925 | -1248 | -1248 | -324 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -923 | -1248 | -1248 | -325 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -918 | -1248 | -1248 | -330 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -910 | -1248 | -1248 | -338 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -908 | -1248 | -1248 | -340 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -901 | -1248 | -1248 | -347 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -888 | -1248 | -1248 | -360 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -888 | -1248 | -1248 | -360 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2783
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1998 |  | 2000 | -2 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1959 |  | 2000 | -41 | 98 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1939 |  | 2000 | -61 | 97 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1886 |  | 2000 | -114 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1711 |  | 1836 | -125 | 93 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1780 |  | 2000 | -220 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1765 |  | 2000 | -235 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1590 |  | 1836 | -246 | 87 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1706 |  | 2000 | -294 | 85 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1698 |  | 2000 | -302 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1689 |  | 2000 | -311 | 84 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1686 |  | 2000 | -314 | 84 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1663 |  | 2000 | -337 | 83 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1651 |  | 2000 | -349 | 83 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1645 |  | 2000 | -355 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1642 |  | 2000 | -358 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1628 |  | 2000 | -372 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1494 |  | 1836 | -342 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 |  | 1836 | -364 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1580 |  | 2000 | -420 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 |  | 1836 | -400 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1836 | -409 | 78 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1426 |  | 1836 | -410 | 78 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 |  | 1836 | -421 | 77 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1389 |  | 1836 | -447 | 76 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1375 |  | 1836 | -461 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1360 |  | 1836 | -476 | 74 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1360 |  | 1836 | -476 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -925 |  | -1248 | -324 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -923 |  | -1248 | -325 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -918 |  | -1248 | -330 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -910 |  | -1248 | -338 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -908 |  | -1248 | -340 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -901 |  | -1248 | -347 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -888 |  | -1248 | -360 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -888 |  | -1248 | -360 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2979
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 | 2000 | 2000 | -3 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1809 | 1836 | 1836 | -27 | 99 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1954 | 2000 | 2000 | -46 | 98 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1921 | 2000 | 2000 | -79 | 96 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1881 | 2000 | 2000 | -119 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1695 | 1836 | 1836 | -141 | 92 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1786 | 2000 | 2000 | -214 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1772 | 2000 | 2000 | -228 | 89 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1722 | 2000 | 2000 | -278 | 86 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1718 | 2000 | 2000 | -282 | 86 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1713 | 2000 | 2000 | -287 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 | 1836 | 1836 | -271 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1704 | 2000 | 2000 | -296 | 85 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 | 2000 | 2000 | -304 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1554 | 1836 | 1836 | -282 | 85 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1681 | 2000 | 2000 | -319 | 84 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1673 | 2000 | 2000 | -327 | 84 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1522 | 1836 | 1836 | -314 | 83 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1516 | 1836 | 1836 | -320 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1505 | 1836 | 1836 | -331 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1639 | 2000 | 2000 | -361 | 82 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1502 | 1836 | 1836 | -334 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1622 | 2000 | 2000 | -378 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1610 | 2000 | 2000 | -390 | 81 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1473 | 1836 | 1836 | -363 | 80 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 | 1836 | 1836 | -374 | 80 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 | 1836 | 1836 | -392 | 79 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 | 1836 | 1836 | -392 | 79 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -933 | -1248 | -1248 | -316 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -931 | -1248 | -1248 | -318 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -926 | -1248 | -1248 | -322 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -917 | -1248 | -1248 | -332 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -915 | -1248 | -1248 | -333 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -908 | -1248 | -1248 | -341 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -889 | -1248 | -1248 | -359 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -889 | -1248 | -1248 | -360 | 71 | []

## 2230Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2979
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1997 |  | 2000 | -3 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1809 |  | 1836 | -27 | 99 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1954 |  | 2000 | -46 | 98 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1921 |  | 2000 | -79 | 96 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1881 |  | 2000 | -119 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1695 |  | 1836 | -141 | 92 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1786 |  | 2000 | -214 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1772 |  | 2000 | -228 | 89 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1722 |  | 2000 | -278 | 86 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1718 |  | 2000 | -282 | 86 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1713 |  | 2000 | -287 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1836 | -271 | 85 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1704 |  | 2000 | -296 | 85 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1696 |  | 2000 | -304 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1554 |  | 1836 | -282 | 85 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1681 |  | 2000 | -319 | 84 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1673 |  | 2000 | -327 | 84 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1522 |  | 1836 | -314 | 83 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1516 |  | 1836 | -320 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1505 |  | 1836 | -331 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1639 |  | 2000 | -361 | 82 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1502 |  | 1836 | -334 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1622 |  | 2000 | -378 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1610 |  | 2000 | -390 | 81 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1473 |  | 1836 | -363 | 80 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 |  | 1836 | -374 | 80 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1836 | -392 | 79 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1836 | -392 | 79 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -933 |  | -1248 | -316 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -931 |  | -1248 | -318 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -926 |  | -1248 | -322 | 74 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -917 |  | -1248 | -332 | 73 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -915 |  | -1248 | -333 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -908 |  | -1248 | -341 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -889 |  | -1248 | -359 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -889 |  | -1248 | -360 | 71 | []

## 2330Preventive
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3374
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1996 | 2000 | 2000 | -4 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1941 | 2000 | 2000 | -59 | 97 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1867 | 2000 | 2000 | -133 | 93 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1863 | 2000 | 2000 | -137 | 93 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1788 | 2000 | 2000 | -212 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1778 | 2000 | 2000 | -222 | 89 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1767 | 2000 | 2000 | -233 | 88 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1751 | 2000 | 2000 | -249 | 88 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1749 | 2000 | 2000 | -251 | 87 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1742 | 2000 | 2000 | -258 | 87 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1734 | 2000 | 2000 | -266 | 87 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1728 | 2000 | 2000 | -272 | 86 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1716 | 2000 | 2000 | -284 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1655 | 2000 | 2000 | -345 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1497 | 1836 | 1836 | -339 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1615 | 2000 | 2000 | -385 | 81 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 | 1836 | 1836 | -369 | 80 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1596 | 2000 | 2000 | -404 | 80 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 | 1836 | 1836 | -373 | 80 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 | 1836 | 1836 | -374 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 | 1836 | 1836 | -374 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1452 | -1836 | -1836 | -384 | 79 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1452 | -1836 | -1836 | -384 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1425 | 1836 | 1836 | -411 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1418 | -1836 | -1836 | -418 | 77 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1407 | -1836 | -1836 | -429 | 77 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1532 | 2000 | 2000 | -468 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1529 | -2000 | -2000 | -471 | 76 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1396 | -1836 | -1836 | -440 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1516 | 2000 | 2000 | -484 | 76 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1390 | -1836 | -1836 | -446 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1513 | -2000 | -2000 | -487 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -940 | -1248 | -1248 | -308 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -938 | -1248 | -1248 | -310 | 75 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1379 | -1836 | -1836 | -457 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1379 | -1836 | -1836 | -457 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -934 | -1248 | -1248 | -315 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -924 | -1248 | -1248 | -324 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -923 | -1248 | -1248 | -326 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -915 | -1248 | -1248 | -333 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -893 | -1248 | -1248 | -356 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -892 | -1248 | -1248 | -356 | 71 | []

## 2330Curative
Detailed results
Generated at: | 2026-03-22 19:44
Business day: | 23.03.2026
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3374
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00015 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1996 |  | 2000 | -4 | 100 | []
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1941 |  | 2000 | -59 | 97 | []
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1867 |  | 2000 | -133 | 93 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1863 |  | 2000 | -137 | 93 | []
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1788 |  | 2000 | -212 | 89 | []
BC | Base Case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1778 |  | 2000 | -222 | 89 | []
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1767 |  | 2000 | -233 | 88 | []
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1751 |  | 2000 | -249 | 88 | []
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1749 |  | 2000 | -251 | 87 | []
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1742 |  | 2000 | -258 | 87 | []
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1734 |  | 2000 | -266 | 87 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1728 |  | 2000 | -272 | 86 | []
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1716 |  | 2000 | -284 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1655 |  | 2000 | -345 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1497 |  | 1836 | -339 | 82 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1615 |  | 2000 | -385 | 81 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 |  | 1836 | -369 | 80 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1596 |  | 2000 | -404 | 80 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 |  | 1836 | -373 | 80 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 |  | 1836 | -374 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 |  | 1836 | -374 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1452 |  | -1836 | -384 | 79 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1452 |  | -1836 | -384 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1425 |  | 1836 | -411 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1418 |  | -1836 | -418 | 77 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1407 |  | -1836 | -429 | 77 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1532 |  | 2000 | -468 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1529 |  | -2000 | -471 | 76 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1396 |  | -1836 | -440 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1516 |  | 2000 | -484 | 76 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1390 |  | -1836 | -446 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1513 |  | -2000 | -487 | 76 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -940 |  | -1248 | -308 | 75 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -938 |  | -1248 | -310 | 75 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1379 |  | -1836 | -457 | 75 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1379 |  | -1836 | -457 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -934 |  | -1248 | -315 | 75 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -924 |  | -1248 | -324 | 74 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -923 |  | -1248 | -326 | 74 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -915 |  | -1248 | -333 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -893 |  | -1248 | -356 | 71 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -892 |  | -1248 | -356 | 71 | []