## 1230Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3296
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1556 | 1600 | 1600 | -44 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1454 | 1600 | 1600 | -146 | 91 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1453 | 1600 | 1600 | -147 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1400 | 1600 | 1600 | -200 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1399 | 1600 | 1600 | -201 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1397 | 1600 | 1600 | -203 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1379 | 1600 | 1600 | -221 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1369 | 1600 | 1600 | -231 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1369 | 1600 | 1600 | -231 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1355 | 1600 | 1600 | -245 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1303 | 1600 | 1600 | -297 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1285 | 1600 | 1600 | -315 | 80 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 | 1600 | 1600 | -326 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1184 | 1600 | 1600 | -416 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1141 | 1600 | 1600 | -459 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []

## 1230Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3296
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1556 |  | 1600 | -44 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1454 |  | 1600 | -146 | 91 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1453 |  | 1600 | -147 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1400 |  | 1600 | -200 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1399 |  | 1600 | -201 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1397 |  | 1600 | -203 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1379 |  | 1600 | -221 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1369 |  | 1600 | -231 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1369 |  | 1600 | -231 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1355 |  | 1600 | -245 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1303 |  | 1600 | -297 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1285 |  | 1600 | -315 | 80 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 |  | 1600 | -326 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 |  | 1600 | -340 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1184 |  | 1600 | -416 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 |  | 1600 | -418 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 |  | 1600 | -425 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 |  | 1600 | -439 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1150 |  | 1600 | -450 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1141 |  | 1600 | -459 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 |  | 1600 | -460 | 71 | []

## 1330Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3448
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1544 | 1600 | 1600 | -56 | 96 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1473 | 1600 | 1600 | -127 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1446 | 1600 | 1600 | -154 | 90 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1429 | 1600 | 1600 | -171 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1426 | 1600 | 1600 | -174 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1421 | 1600 | 1600 | -179 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1403 | 1600 | 1600 | -197 | 88 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1367 | 1600 | 1600 | -233 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1360 | 1600 | 1600 | -240 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1296 | 1600 | 1600 | -304 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1283 | 1600 | 1600 | -317 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 | 1600 | 1600 | -408 | 74 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1186 | 1600 | 1600 | -414 | 74 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1184 | 1600 | 1600 | -416 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1167 | 1600 | 1600 | -433 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1154 | 1600 | 1600 | -446 | 72 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1087 | 1517 | 1517 | -430 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1136 | 1600 | 1600 | -464 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1133 | 1600 | 1600 | -467 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 | 1600 | 1600 | -470 | 71 | []

## 1330Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3448
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1544 |  | 1600 | -56 | 96 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1473 |  | 1600 | -127 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1446 |  | 1600 | -154 | 90 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1429 |  | 1600 | -171 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1426 |  | 1600 | -174 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1421 |  | 1600 | -179 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1403 |  | 1600 | -197 | 88 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1367 |  | 1600 | -233 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 |  | 1600 | -234 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1360 |  | 1600 | -240 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1302 |  | 1600 | -298 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1296 |  | 1600 | -304 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1283 |  | 1600 | -317 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1267 |  | 1600 | -333 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 |  | 1600 | -408 | 74 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1186 |  | 1600 | -414 | 74 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1184 |  | 1600 | -416 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 |  | 1600 | -425 | 73 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1167 |  | 1600 | -433 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1154 |  | 1600 | -446 | 72 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1087 |  | 1517 | -430 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1136 |  | 1600 | -464 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1133 |  | 1600 | -467 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 |  | 1600 | -470 | 71 | []

## 1430Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3462
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1578 | 1600 | 1600 | -22 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1470 | 1600 | 1600 | -130 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1469 | 1600 | 1600 | -131 | 92 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1439 | 1600 | 1600 | -161 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1430 | 1600 | 1600 | -170 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1409 | 1600 | 1600 | -191 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1399 | 1600 | 1600 | -201 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1352 | 1600 | 1600 | -248 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1303 | 1600 | 1600 | -297 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1299 | 1600 | 1600 | -301 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1286 | 1600 | 1600 | -314 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1272 | 1600 | 1600 | -328 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 | 1600 | 1600 | -408 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 | 1600 | 1600 | -411 | 74 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1179 | 1600 | 1600 | -421 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1151 | 1600 | 1600 | -449 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 | 1600 | 1600 | -451 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 | 1600 | 1600 | -451 | 72 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1146 | 1600 | 1600 | -454 | 72 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1079 | 1517 | 1517 | -438 | 71 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1134 | 1600 | 1600 | -466 | 71 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1125 | 1600 | 1600 | -475 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3462
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1597 |  | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1578 |  | 1600 | -22 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1470 |  | 1600 | -130 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1469 |  | 1600 | -131 | 92 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1439 |  | 1600 | -161 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1430 |  | 1600 | -170 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1409 |  | 1600 | -191 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1399 |  | 1600 | -201 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1357 |  | 1600 | -243 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1357 |  | 1600 | -243 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1352 |  | 1600 | -248 | 85 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1303 |  | 1600 | -297 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1299 |  | 1600 | -301 | 81 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1286 |  | 1600 | -314 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1272 |  | 1600 | -328 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 |  | 1600 | -408 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 |  | 1600 | -411 | 74 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1179 |  | 1600 | -421 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 |  | 1600 | -439 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1151 |  | 1600 | -449 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 |  | 1600 | -451 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 |  | 1600 | -451 | 72 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-BG] [DIR] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1146 |  | 1600 | -454 | 72 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [DIR] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1079 |  | 1517 | -438 | 71 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1134 |  | 1600 | -466 | 71 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1125 |  | 1600 | -475 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3351
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1589 | 1600 | 1600 | -11 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1489 | 1600 | 1600 | -111 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1444 | 1600 | 1600 | -156 | 90 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1424 | 1600 | 1600 | -176 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 | 1600 | 1600 | -208 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 | 1600 | 1600 | -208 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1373 | 1600 | 1600 | -227 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1341 | 1600 | 1600 | -259 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1281 | 1600 | 1600 | -319 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 | 1600 | 1600 | -324 | 80 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1272 | 1600 | 1600 | -328 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 | 1600 | 1600 | -383 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 | 1600 | 1600 | -387 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 | 1600 | 1600 | -402 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1179 | 1600 | 1600 | -421 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1177 | 1600 | 1600 | -423 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1170 | 1600 | 1600 | -430 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 | 1600 | 1600 | -443 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1152 | 1600 | 1600 | -448 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 | 1600 | 1600 | -451 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 | 1600 | 1600 | -458 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3351
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 |  | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1589 |  | 1600 | -11 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1489 |  | 1600 | -111 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1444 |  | 1600 | -156 | 90 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1424 |  | 1600 | -176 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 |  | 1600 | -208 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1392 |  | 1600 | -208 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1373 |  | 1600 | -227 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 |  | 1600 | -230 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1370 |  | 1600 | -230 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1341 |  | 1600 | -259 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1281 |  | 1600 | -319 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 |  | 1600 | -324 | 80 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1272 |  | 1600 | -328 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 |  | 1600 | -383 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1213 |  | 1600 | -387 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 |  | 1600 | -402 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1179 |  | 1600 | -421 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1177 |  | 1600 | -423 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1170 |  | 1600 | -430 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1157 |  | 1600 | -443 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1152 |  | 1600 | -448 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1149 |  | 1600 | -451 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 |  | 1600 | -458 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3212
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1600 | 1600 | 1600 | 0 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1581 | 1600 | 1600 | -19 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1510 | 1600 | 1600 | -90 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1417 | 1600 | 1600 | -183 | 89 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1415 | 1600 | 1600 | -185 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1358 | 1600 | 1600 | -242 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1357 | 1600 | 1600 | -243 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1346 | 1600 | 1600 | -254 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1341 | 1600 | 1600 | -259 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1322 | 1600 | 1600 | -278 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1282 | 1600 | 1600 | -318 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1256 | 1600 | 1600 | -344 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1252 | 1600 | 1600 | -348 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 | 1600 | 1600 | -383 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 | 1600 | 1600 | -398 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 | 1600 | 1600 | -400 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 | 1600 | 1600 | -402 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 | 1600 | 1600 | -426 | 73 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1169 | 1600 | 1600 | -431 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1154 | 1600 | 1600 | -446 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1148 | 1600 | 1600 | -452 | 72 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 | 1600 | 1600 | -458 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1136 | 1600 | 1600 | -464 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1134 | 1600 | 1600 | -466 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3212
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1600 |  | 1600 | 0 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1581 |  | 1600 | -19 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1510 |  | 1600 | -90 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1417 |  | 1600 | -183 | 89 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1415 |  | 1600 | -185 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1370 |  | 1600 | -230 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1358 |  | 1600 | -242 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1357 |  | 1600 | -243 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1346 |  | 1600 | -254 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1341 |  | 1600 | -259 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1322 |  | 1600 | -278 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1282 |  | 1600 | -318 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1256 |  | 1600 | -344 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1252 |  | 1600 | -348 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 |  | 1600 | -383 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 |  | 1600 | -390 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 |  | 1600 | -390 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 |  | 1600 | -398 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 |  | 1600 | -400 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 |  | 1600 | -402 | 75 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 |  | 1600 | -426 | 73 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1169 |  | 1600 | -431 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1154 |  | 1600 | -446 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1148 |  | 1600 | -452 | 72 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1147 |  | 1600 | -453 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 |  | 1600 | -458 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 |  | 1600 | -460 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1136 |  | 1600 | -464 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1134 |  | 1600 | -466 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3357
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1578 | 1600 | 1600 | -22 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1525 | 1600 | 1600 | -75 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1426 | 1600 | 1600 | -174 | 89 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1398 | 1600 | 1600 | -202 | 87 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1378 | 1600 | 1600 | -222 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1369 | 1600 | 1600 | -231 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 | 1600 | 1600 | -239 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 | 1600 | 1600 | -239 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1355 | 1600 | 1600 | -245 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1334 | 1600 | 1600 | -266 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1313 | 1600 | 1600 | -287 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1286 | 1600 | 1600 | -314 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1257 | 1600 | 1600 | -343 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1251 | 1600 | 1600 | -349 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1216 | 1600 | 1600 | -384 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1208 | 1600 | 1600 | -392 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 | 1600 | 1600 | -396 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1197 | 1600 | 1600 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 | 1600 | 1600 | -409 | 74 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1170 | 1600 | 1600 | -430 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1156 | 1600 | 1600 | -444 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1143 | 1600 | 1600 | -457 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1139 | 1600 | 1600 | -461 | 71 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1139 | 1600 | 1600 | -461 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 | 1600 | 1600 | -465 | 71 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1131 | 1600 | 1600 | -469 | 71 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1131 | 1600 | 1600 | -469 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 | 1600 | 1600 | -470 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1125 | 1600 | 1600 | -475 | 70 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1124 | 1600 | 1600 | -476 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3357
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 |  | 1600 | -2 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1578 |  | 1600 | -22 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1525 |  | 1600 | -75 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1426 |  | 1600 | -174 | 89 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1398 |  | 1600 | -202 | 87 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1378 |  | 1600 | -222 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1369 |  | 1600 | -231 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 |  | 1600 | -239 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 |  | 1600 | -239 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1355 |  | 1600 | -245 | 85 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1334 |  | 1600 | -266 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1313 |  | 1600 | -287 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1286 |  | 1600 | -314 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1257 |  | 1600 | -343 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1251 |  | 1600 | -349 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1216 |  | 1600 | -384 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1208 |  | 1600 | -392 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 |  | 1600 | -395 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 |  | 1600 | -396 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1197 |  | 1600 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 |  | 1600 | -406 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 |  | 1600 | -409 | 74 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 |  | 1600 | -417 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1170 |  | 1600 | -430 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 |  | 1600 | -442 | 72 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1156 |  | 1600 | -444 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1143 |  | 1600 | -457 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1139 |  | 1600 | -461 | 71 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1139 |  | 1600 | -461 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 |  | 1600 | -465 | 71 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1131 |  | 1600 | -469 | 71 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1131 |  | 1600 | -469 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1130 |  | 1600 | -470 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1125 |  | 1600 | -475 | 70 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1124 |  | 1600 | -476 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3378
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1585 | 1600 | 1600 | -15 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1529 | 1600 | 1600 | -71 | 96 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1472 | 1600 | 1600 | -128 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1446 | 1600 | 1600 | -154 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1402 | 1600 | 1600 | -198 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1385 | 1600 | 1600 | -215 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1384 | 1600 | 1600 | -216 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1349 | 1600 | 1600 | -251 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1349 | 1600 | 1600 | -251 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1338 | 1600 | 1600 | -262 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1306 | 1600 | 1600 | -294 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1281 | 1600 | 1600 | -319 | 80 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 | 1600 | 1600 | -326 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1273 | 1600 | 1600 | -327 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1266 | 1600 | 1600 | -334 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 | 1600 | 1600 | -351 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 | 1600 | 1600 | -383 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 | 1600 | 1600 | -426 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1170 | 1600 | 1600 | -430 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1145 | 1600 | 1600 | -455 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 | 1600 | 1600 | -465 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 | 1600 | 1600 | -465 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3378
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 |  | 1600 | -4 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1585 |  | 1600 | -15 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1529 |  | 1600 | -71 | 96 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1472 |  | 1600 | -128 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1446 |  | 1600 | -154 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1402 |  | 1600 | -198 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1385 |  | 1600 | -215 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1384 |  | 1600 | -216 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1349 |  | 1600 | -251 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1349 |  | 1600 | -251 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1338 |  | 1600 | -262 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1306 |  | 1600 | -294 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1281 |  | 1600 | -319 | 80 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 |  | 1600 | -326 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1273 |  | 1600 | -327 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1266 |  | 1600 | -334 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1249 |  | 1600 | -351 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1224 |  | 1600 | -376 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1217 |  | 1600 | -383 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 |  | 1600 | -401 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 |  | 1600 | -407 | 75 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 |  | 1600 | -413 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 |  | 1600 | -426 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1170 |  | 1600 | -430 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 |  | 1600 | -439 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 |  | 1600 | -441 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1145 |  | 1600 | -455 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 |  | 1600 | -465 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 |  | 1600 | -465 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3348
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 | 1600 | 1600 | -4 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1582 | 1600 | 1600 | -18 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1528 | 1600 | 1600 | -72 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1468 | 1600 | 1600 | -132 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1443 | 1600 | 1600 | -157 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1398 | 1600 | 1600 | -202 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1382 | 1600 | 1600 | -218 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1378 | 1600 | 1600 | -222 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1346 | 1600 | 1600 | -254 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1346 | 1600 | 1600 | -254 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1336 | 1600 | 1600 | -264 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1305 | 1600 | 1600 | -295 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1277 | 1600 | 1600 | -323 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 | 1600 | 1600 | -331 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1263 | 1600 | 1600 | -337 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 | 1600 | 1600 | -350 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 | 1600 | 1600 | -363 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 | 1600 | 1600 | -410 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 | 1600 | 1600 | -426 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1156 | 1600 | 1600 | -444 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 | 1600 | 1600 | -458 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 | 1600 | 1600 | -465 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1133 | 1600 | 1600 | -467 | 71 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1124 | 1600 | 1600 | -476 | 70 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1124 | 1600 | 1600 | -476 | 70 | []

## 1930Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3348
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1596 |  | 1600 | -4 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1582 |  | 1600 | -18 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1528 |  | 1600 | -72 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1468 |  | 1600 | -132 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1443 |  | 1600 | -157 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1398 |  | 1600 | -202 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1382 |  | 1600 | -218 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1378 |  | 1600 | -222 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1346 |  | 1600 | -254 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1346 |  | 1600 | -254 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1336 |  | 1600 | -264 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1305 |  | 1600 | -295 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1277 |  | 1600 | -323 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1269 |  | 1600 | -331 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1263 |  | 1600 | -337 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1250 |  | 1600 | -350 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1237 |  | 1600 | -363 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1214 |  | 1600 | -386 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1211 |  | 1600 | -389 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 |  | 1600 | -407 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 |  | 1600 | -410 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1178 |  | 1600 | -422 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1174 |  | 1600 | -426 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 |  | 1600 | -435 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 |  | 1600 | -442 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1156 |  | 1600 | -444 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1142 |  | 1600 | -458 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1135 |  | 1600 | -465 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1133 |  | 1600 | -467 | 71 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1124 |  | 1600 | -476 | 70 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1124 |  | 1600 | -476 | 70 | []

## 2030Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3302
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1587 | 1600 | 1600 | -13 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1527 | 1600 | 1600 | -73 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1448 | 1600 | 1600 | -152 | 90 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1430 | 1600 | 1600 | -170 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1386 | 1600 | 1600 | -214 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1360 | 1600 | 1600 | -240 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1360 | 1600 | 1600 | -240 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1329 | 1600 | 1600 | -271 | 83 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1312 | 1600 | 1600 | -288 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1271 | 1600 | 1600 | -329 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1266 | 1600 | 1600 | -334 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1258 | 1600 | 1600 | -342 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 | 1600 | 1600 | -354 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 | 1600 | 1600 | -376 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1208 | 1600 | 1600 | -392 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1184 | 1600 | 1600 | -416 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1172 | 1600 | 1600 | -428 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1154 | 1600 | 1600 | -446 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1154 | 1600 | 1600 | -446 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1145 | 1600 | 1600 | -455 | 72 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1138 | 1600 | 1600 | -462 | 71 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1138 | 1600 | 1600 | -462 | 71 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1134 | 1600 | 1600 | -466 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 | 1600 | 1600 | -469 | 71 | []

## 2030Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3302
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1587 |  | 1600 | -13 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1527 |  | 1600 | -73 | 95 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1448 |  | 1600 | -152 | 90 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1430 |  | 1600 | -170 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1386 |  | 1600 | -214 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1370 |  | 1600 | -230 | 86 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1366 |  | 1600 | -234 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1360 |  | 1600 | -240 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1360 |  | 1600 | -240 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1329 |  | 1600 | -271 | 83 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1312 |  | 1600 | -288 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1302 |  | 1600 | -298 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1271 |  | 1600 | -329 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1266 |  | 1600 | -334 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1258 |  | 1600 | -342 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1246 |  | 1600 | -354 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1234 |  | 1600 | -366 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1224 |  | 1600 | -376 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 |  | 1600 | -390 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1208 |  | 1600 | -392 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 |  | 1600 | -407 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1184 |  | 1600 | -416 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1178 |  | 1600 | -422 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1172 |  | 1600 | -428 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1154 |  | 1600 | -446 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1154 |  | 1600 | -446 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1147 |  | 1600 | -453 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1145 |  | 1600 | -455 | 72 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1138 |  | 1600 | -462 | 71 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1138 |  | 1600 | -462 | 71 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1134 |  | 1600 | -466 | 71 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 |  | 1600 | -469 | 71 | []

## 2130Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3266
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1563 | 1600 | 1600 | -37 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1492 | 1600 | 1600 | -108 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 | 1600 | 1600 | -151 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1444 | 1600 | 1600 | -156 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1403 | 1600 | 1600 | -197 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1380 | 1600 | 1600 | -220 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1380 | 1600 | 1600 | -220 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1371 | 1600 | 1600 | -229 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1371 | 1600 | 1600 | -229 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1340 | 1600 | 1600 | -260 | 84 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1336 | 1600 | 1600 | -264 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1287 | 1600 | 1600 | -313 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1279 | 1600 | 1600 | -321 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 | 1600 | 1600 | -326 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1265 | 1600 | 1600 | -335 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 | 1600 | 1600 | -359 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 | 1600 | 1600 | -375 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 | 1600 | 1600 | -400 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 | 1600 | 1600 | -427 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1172 | 1600 | 1600 | -428 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 | 1600 | 1600 | -433 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 | 1600 | 1600 | -454 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1132 | 1600 | 1600 | -468 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3266
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1563 |  | 1600 | -37 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1492 |  | 1600 | -108 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1449 |  | 1600 | -151 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1444 |  | 1600 | -156 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1403 |  | 1600 | -197 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1380 |  | 1600 | -220 | 86 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1380 |  | 1600 | -220 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1371 |  | 1600 | -229 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1371 |  | 1600 | -229 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1340 |  | 1600 | -260 | 84 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1336 |  | 1600 | -264 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1287 |  | 1600 | -313 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1279 |  | 1600 | -321 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 |  | 1600 | -326 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1265 |  | 1600 | -335 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1241 |  | 1600 | -359 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1225 |  | 1600 | -375 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 |  | 1600 | -390 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 |  | 1600 | -400 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 |  | 1600 | -427 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1172 |  | 1600 | -428 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 |  | 1600 | -433 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1164 |  | 1600 | -436 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1147 |  | 1600 | -453 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 |  | 1600 | -454 | 72 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1132 |  | 1600 | -468 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3372
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1568 | 1600 | 1600 | -32 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1485 | 1600 | 1600 | -115 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1473 | 1600 | 1600 | -127 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1469 | 1600 | 1600 | -131 | 92 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1419 | 1600 | 1600 | -181 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1410 | 1600 | 1600 | -190 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1400 | 1600 | 1600 | -200 | 88 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1367 | 1600 | 1600 | -233 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1356 | 1600 | 1600 | -244 | 85 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1288 | 1600 | 1600 | -312 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1288 | 1600 | 1600 | -312 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1279 | 1600 | 1600 | -321 | 80 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1278 | 1600 | 1600 | -322 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1273 | 1600 | 1600 | -327 | 80 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1168 | 1600 | 1600 | -432 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1156 | 1600 | 1600 | -444 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 | 1600 | 1600 | -469 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1129 | 1600 | 1600 | -471 | 71 | []

## 2230Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3372
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1598 |  | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1568 |  | 1600 | -32 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1485 |  | 1600 | -115 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1473 |  | 1600 | -127 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1469 |  | 1600 | -131 | 92 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1419 |  | 1600 | -181 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1410 |  | 1600 | -190 | 88 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1400 |  | 1600 | -200 | 88 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1367 |  | 1600 | -233 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 |  | 1600 | -234 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1356 |  | 1600 | -244 | 85 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1288 |  | 1600 | -312 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1288 |  | 1600 | -312 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1279 |  | 1600 | -321 | 80 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1278 |  | 1600 | -322 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1273 |  | 1600 | -327 | 80 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1242 |  | 1600 | -358 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1230 |  | 1600 | -370 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1227 |  | 1600 | -373 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1222 |  | 1600 | -378 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1221 |  | 1600 | -379 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1212 |  | 1600 | -388 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 |  | 1600 | -390 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 |  | 1600 | -401 | 75 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1168 |  | 1600 | -432 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 |  | 1600 | -439 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1156 |  | 1600 | -444 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 |  | 1600 | -469 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1129 |  | 1600 | -471 | 71 | []

## 2330Preventive
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3476
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1597 | 1600 | 1600 | -3 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1501 | 1600 | 1600 | -99 | 94 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1498 | 1600 | 1600 | -102 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1491 | 1600 | 1600 | -109 | 93 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1441 | 1600 | 1600 | -159 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1432 | 1600 | 1600 | -168 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1413 | 1600 | 1600 | -187 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1360 | 1600 | 1600 | -240 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1360 | 1600 | 1600 | -240 | 85 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1352 | 1600 | 1600 | -248 | 85 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1295 | 1600 | 1600 | -305 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1289 | 1600 | 1600 | -311 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 | 1600 | 1600 | -316 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1281 | 1600 | 1600 | -319 | 80 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 | 1600 | 1600 | -364 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 | 1600 | 1600 | -367 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 | 1600 | 1600 | -369 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1221 | 1600 | 1600 | -379 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 | 1600 | 1600 | -382 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1179 | 1600 | 1600 | -421 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1162 | 1600 | 1600 | -438 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1123 | 1600 | 1600 | -477 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2026-03-23 08:22
Business day: | 23.03.2026
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3476
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1597 |  | 1600 | -3 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1501 |  | 1600 | -99 | 94 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1498 |  | 1600 | -102 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1491 |  | 1600 | -109 | 93 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1441 |  | 1600 | -159 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1432 |  | 1600 | -168 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1413 |  | 1600 | -187 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1370 |  | 1600 | -230 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1360 |  | 1600 | -240 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1360 |  | 1600 | -240 | 85 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1352 |  | 1600 | -248 | 85 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1295 |  | 1600 | -305 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1289 |  | 1600 | -311 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1284 |  | 1600 | -316 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1281 |  | 1600 | -319 | 80 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1240 |  | 1600 | -360 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1239 |  | 1600 | -361 | 77 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1236 |  | 1600 | -364 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1233 |  | 1600 | -367 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1232 |  | 1600 | -368 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1231 |  | 1600 | -369 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1229 |  | 1600 | -371 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1221 |  | 1600 | -379 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1218 |  | 1600 | -382 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 |  | 1600 | -406 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 |  | 1600 | -413 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 |  | 1600 | -418 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1179 |  | 1600 | -421 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1162 |  | 1600 | -438 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 |  | 1600 | -442 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1123 |  | 1600 | -477 | 70 | []