## 1230Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2697
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1591 | 1600 | 1600 | -9 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1490 | 1600 | 1600 | -110 | 93 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1433 | 1600 | 1600 | -167 | 90 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1347 | 1600 | 1600 | -253 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1344 | 1600 | 1600 | -256 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1344 | 1600 | 1600 | -256 | 84 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1302 | 1600 | 1600 | -298 | 81 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1192 | 1600 | 1600 | -408 | 75 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1170 | 1600 | 1600 | -430 | 73 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1152 | 1600 | 1600 | -448 | 72 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1125 | 1600 | 1600 | -475 | 70 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1123 | 1600 | 1600 | -477 | 70 | []

## 1230Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 12:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2697
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1591 |  | 1600 | -9 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1490 |  | 1600 | -110 | 93 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1433 |  | 1600 | -167 | 90 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1347 |  | 1600 | -253 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1344 |  | 1600 | -256 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1344 |  | 1600 | -256 | 84 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1302 |  | 1600 | -298 | 81 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1226 |  | 1600 | -374 | 77 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1206 |  | 1600 | -394 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1194 |  | 1600 | -406 | 75 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1192 |  | 1600 | -408 | 75 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1170 |  | 1600 | -430 | 73 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1152 |  | 1600 | -448 | 72 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1125 |  | 1600 | -475 | 70 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1123 |  | 1600 | -477 | 70 | []

## 1330Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2661
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1598 | 1600 | 1600 | -2 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1493 | 1600 | 1600 | -107 | 93 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1408 | 1600 | 1600 | -192 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1331 | 1600 | 1600 | -269 | 83 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1322 | 1600 | 1600 | -278 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1322 | 1600 | 1600 | -278 | 83 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1292 | 1600 | 1600 | -308 | 81 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1189 | 1600 | 1600 | -411 | 74 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1184 | 1600 | 1600 | -416 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1155 | 1600 | 1600 | -445 | 72 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1122 | 1600 | 1600 | -478 | 70 | []

## 1330Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 13:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2661
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1598 |  | 1600 | -2 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1493 |  | 1600 | -107 | 93 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1408 |  | 1600 | -192 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1331 |  | 1600 | -269 | 83 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1322 |  | 1600 | -278 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1322 |  | 1600 | -278 | 83 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1292 |  | 1600 | -308 | 81 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1235 |  | 1600 | -365 | 77 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1189 |  | 1600 | -411 | 74 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1184 |  | 1600 | -416 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1175 |  | 1600 | -425 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1155 |  | 1600 | -445 | 72 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1140 |  | 1600 | -460 | 71 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1122 |  | 1600 | -478 | 70 | []

## 1430Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2678
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1592 | 1600 | 1600 | -8 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1491 | 1600 | 1600 | -109 | 93 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1407 | 1600 | 1600 | -193 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1329 | 1600 | 1600 | -271 | 83 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1323 | 1600 | 1600 | -277 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1323 | 1600 | 1600 | -277 | 83 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1287 | 1600 | 1600 | -313 | 80 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1230 | 1600 | 1600 | -370 | 77 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1154 | 1600 | 1600 | -446 | 72 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1136 | 1600 | 1600 | -464 | 71 | []

## 1430Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 14:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2678
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1592 |  | 1600 | -8 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1491 |  | 1600 | -109 | 93 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1407 |  | 1600 | -193 | 88 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1329 |  | 1600 | -271 | 83 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1323 |  | 1600 | -277 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1323 |  | 1600 | -277 | 83 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1287 |  | 1600 | -313 | 80 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1230 |  | 1600 | -370 | 77 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1194 |  | 1600 | -406 | 75 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1181 |  | 1600 | -419 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1175 |  | 1600 | -425 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1154 |  | 1600 | -446 | 72 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1136 |  | 1600 | -464 | 71 | []

## 1530Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2679
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1590 | 1600 | 1600 | -10 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1495 | 1600 | 1600 | -105 | 93 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1419 | 1600 | 1600 | -181 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1338 | 1600 | 1600 | -262 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1334 | 1600 | 1600 | -266 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1333 | 1600 | 1600 | -267 | 83 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1298 | 1600 | 1600 | -302 | 81 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1125 | 1600 | 1600 | -475 | 70 | []

## 1530Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 15:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2679
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1590 |  | 1600 | -10 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1495 |  | 1600 | -105 | 93 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1419 |  | 1600 | -181 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1338 |  | 1600 | -262 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1334 |  | 1600 | -266 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1333 |  | 1600 | -267 | 83 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1298 |  | 1600 | -302 | 81 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1214 |  | 1600 | -386 | 76 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1211 |  | 1600 | -389 | 76 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1194 |  | 1600 | -406 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1181 |  | 1600 | -419 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1166 |  | 1600 | -434 | 73 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1147 |  | 1600 | -453 | 72 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1125 |  | 1600 | -475 | 70 | []

## 1630Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2733
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1592 | 1600 | 1600 | -8 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1501 | 1600 | 1600 | -99 | 94 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1457 | 1600 | 1600 | -143 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1362 | 1600 | 1600 | -238 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 | 1600 | 1600 | -239 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1354 | 1600 | 1600 | -246 | 85 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1135 | 1600 | 1600 | -465 | 71 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1131 | 1600 | 1600 | -469 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 16:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2733
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1592 |  | 1600 | -8 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1501 |  | 1600 | -99 | 94 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1457 |  | 1600 | -143 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1362 |  | 1600 | -238 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1361 |  | 1600 | -239 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1354 |  | 1600 | -246 | 85 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [DIR] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1267 |  | 1600 | -333 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1205 |  | 1600 | -395 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1199 |  | 1600 | -401 | 75 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1193 |  | 1600 | -407 | 75 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1187 |  | 1600 | -413 | 74 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1166 |  | 1600 | -434 | 73 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1135 |  | 1600 | -465 | 71 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1131 |  | 1600 | -469 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2506
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1477 | 1600 | 1600 | -123 | 92 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1373 | 1600 | 1600 | -227 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1292 | 1600 | 1600 | -308 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1267 | 1600 | 1600 | -333 | 79 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1234 | 1600 | 1600 | -366 | 77 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1178 | 1600 | 1600 | -422 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1141 | 1600 | 1600 | -459 | 71 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1129 | 1600 | 1600 | -471 | 71 | []

## 1730Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 17:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2506
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1593 |  | 1600 | -7 | 100 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1477 |  | 1600 | -123 | 92 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1373 |  | 1600 | -227 | 86 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1292 |  | 1600 | -308 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1267 |  | 1600 | -333 | 79 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1267 |  | 1600 | -333 | 79 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1234 |  | 1600 | -366 | 77 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1187 |  | 1600 | -413 | 74 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1178 |  | 1600 | -422 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1141 |  | 1600 | -459 | 71 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1129 |  | 1600 | -471 | 71 | []

## 1830Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3216
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1593 | 1600 | 1600 | -7 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1542 | 1600 | 1600 | -58 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1503 | 1600 | 1600 | -97 | 94 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1349 | 1600 | 1600 | -251 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1349 | 1600 | 1600 | -251 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1322 | 1600 | 1600 | -278 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1319 | 1600 | 1600 | -281 | 82 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1293 | 1600 | 1600 | -307 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 | 1600 | 1600 | -310 | 81 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1287 | 1600 | 1600 | -313 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1275 | 1600 | 1600 | -325 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1261 | 1600 | 1600 | -339 | 79 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 | 1600 | 1600 | -355 | 78 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1242 | 1600 | 1600 | -358 | 78 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1240 | 1600 | 1600 | -360 | 77 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 | 1600 | 1600 | -391 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 | 1600 | 1600 | -394 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1192 | 1600 | 1600 | -408 | 75 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 | 1600 | 1600 | -424 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 | 1600 | 1600 | -425 | 73 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1172 | 1600 | 1600 | -428 | 73 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 | 1600 | 1600 | -433 | 73 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 | 1600 | 1600 | -439 | 73 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 72 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 72 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1152 | 1600 | 1600 | -448 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1148 | 1600 | 1600 | -452 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 | 1600 | 1600 | -454 | 72 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1141 | 1600 | 1600 | -459 | 71 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1137 | 1600 | 1600 | -463 | 71 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1129 | 1600 | 1600 | -471 | 71 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1121 | 1600 | 1600 | -479 | 70 | []

## 1830Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 18:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3216
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1593 |  | 1600 | -7 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1542 |  | 1600 | -58 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1503 |  | 1600 | -97 | 94 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1349 |  | 1600 | -251 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1349 |  | 1600 | -251 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1322 |  | 1600 | -278 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1319 |  | 1600 | -281 | 82 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1293 |  | 1600 | -307 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1290 |  | 1600 | -310 | 81 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1287 |  | 1600 | -313 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1275 |  | 1600 | -325 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1261 |  | 1600 | -339 | 79 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1245 |  | 1600 | -355 | 78 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1242 |  | 1600 | -358 | 78 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1242 |  | 1600 | -358 | 78 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1240 |  | 1600 | -360 | 77 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1209 |  | 1600 | -391 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1206 |  | 1600 | -394 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1192 |  | 1600 | -408 | 75 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 |  | 1600 | -424 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1175 |  | 1600 | -425 | 73 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1172 |  | 1600 | -428 | 73 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 |  | 1600 | -433 | 73 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1166 |  | 1600 | -434 | 73 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1166 |  | 1600 | -434 | 73 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1166 |  | 1600 | -434 | 73 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 |  | 1600 | -435 | 73 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 |  | 1600 | -435 | 73 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1163 |  | 1600 | -437 | 73 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1161 |  | 1600 | -439 | 73 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 72 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 72 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 |  | 1600 | -441 | 72 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1158 |  | 1600 | -442 | 72 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1152 |  | 1600 | -448 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1148 |  | 1600 | -452 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1146 |  | 1600 | -454 | 72 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1141 |  | 1600 | -459 | 71 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 |  | 1600 | -460 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1137 |  | 1600 | -463 | 71 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1129 |  | 1600 | -471 | 71 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1121 |  | 1600 | -479 | 70 | []

## 1930Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3287
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 | 1600 | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1564 | 1600 | 1600 | -36 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1516 | 1600 | 1600 | -84 | 95 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1368 | 1600 | 1600 | -232 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1368 | 1600 | 1600 | -232 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1347 | 1600 | 1600 | -253 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1343 | 1600 | 1600 | -257 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1313 | 1600 | 1600 | -287 | 82 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1310 | 1600 | 1600 | -290 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1293 | 1600 | 1600 | -307 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 | 1600 | 1600 | -326 | 80 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1270 | 1600 | 1600 | -330 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1253 | 1600 | 1600 | -347 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 | 1600 | 1600 | -381 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1202 | 1600 | 1600 | -398 | 75 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 | 1600 | 1600 | -402 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 | 1600 | 1600 | -408 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 | 1600 | 1600 | -409 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 | 1600 | 1600 | -419 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1179 | 1600 | 1600 | -421 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 | 1600 | 1600 | -424 | 73 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 | 1600 | 1600 | -424 | 73 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1173 | 1600 | 1600 | -427 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1168 | 1600 | 1600 | -432 | 73 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 | 1600 | 1600 | -433 | 73 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 | 1600 | 1600 | -435 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1143 | 1600 | 1600 | -457 | 71 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1139 | 1600 | 1600 | -461 | 71 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1126 | 1600 | 1600 | -474 | 70 | []

## 1930Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 19:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3287
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1599 |  | 1600 | -1 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1564 |  | 1600 | -36 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1516 |  | 1600 | -84 | 95 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1368 |  | 1600 | -232 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1368 |  | 1600 | -232 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1347 |  | 1600 | -253 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1343 |  | 1600 | -257 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1313 |  | 1600 | -287 | 82 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1310 |  | 1600 | -290 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1293 |  | 1600 | -307 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1274 |  | 1600 | -326 | 80 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1270 |  | 1600 | -330 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1253 |  | 1600 | -347 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1227 |  | 1600 | -373 | 77 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1227 |  | 1600 | -373 | 77 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1219 |  | 1600 | -381 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1202 |  | 1600 | -398 | 75 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 |  | 1600 | -402 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 |  | 1600 | -408 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 |  | 1600 | -409 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 |  | 1600 | -412 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 |  | 1600 | -417 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 |  | 1600 | -417 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 |  | 1600 | -418 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 |  | 1600 | -418 | 74 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 |  | 1600 | -418 | 74 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1181 |  | 1600 | -419 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1179 |  | 1600 | -421 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 |  | 1600 | -424 | 73 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1176 |  | 1600 | -424 | 73 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1173 |  | 1600 | -427 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1168 |  | 1600 | -432 | 73 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 |  | 1600 | -433 | 73 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1166 |  | 1600 | -434 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1165 |  | 1600 | -435 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 |  | 1600 | -441 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1143 |  | 1600 | -457 | 71 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1139 |  | 1600 | -461 | 71 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1126 |  | 1600 | -474 | 70 | []

## 2030Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3327
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1592 | 1600 | 1600 | -8 | 99 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1585 | 1600 | 1600 | -15 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1510 | 1600 | 1600 | -90 | 94 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1385 | 1600 | 1600 | -215 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1379 | 1600 | 1600 | -221 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1379 | 1600 | 1600 | -221 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1378 | 1600 | 1600 | -222 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1349 | 1600 | 1600 | -251 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1345 | 1600 | 1600 | -255 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1323 | 1600 | 1600 | -277 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1313 | 1600 | 1600 | -287 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1287 | 1600 | 1600 | -313 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 | 1600 | 1600 | -345 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 | 1600 | 1600 | -357 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 | 1600 | 1600 | -377 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 | 1600 | 1600 | -385 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 | 1600 | 1600 | -389 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1207 | 1600 | 1600 | -393 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 | 1600 | 1600 | -395 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 | 1600 | 1600 | -396 | 75 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1203 | 1600 | 1600 | -397 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1203 | 1600 | 1600 | -397 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1203 | 1600 | 1600 | -397 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 | 1600 | 1600 | -401 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 | 1600 | 1600 | -408 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 | 1600 | 1600 | -410 | 74 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1184 | 1600 | 1600 | -416 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1180 | 1600 | 1600 | -420 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 | 1600 | 1600 | -427 | 73 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 | 1600 | 1600 | -427 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 72 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1150 | 1600 | 1600 | -450 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1132 | 1600 | 1600 | -468 | 71 | []

## 2030Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 20:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3327
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1592 |  | 1600 | -8 | 99 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1585 |  | 1600 | -15 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1510 |  | 1600 | -90 | 94 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1385 |  | 1600 | -215 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1379 |  | 1600 | -221 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1379 |  | 1600 | -221 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1378 |  | 1600 | -222 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1349 |  | 1600 | -251 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1345 |  | 1600 | -255 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1323 |  | 1600 | -277 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1313 |  | 1600 | -287 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1287 |  | 1600 | -313 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1255 |  | 1600 | -345 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1243 |  | 1600 | -357 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1223 |  | 1600 | -377 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1215 |  | 1600 | -385 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1211 |  | 1600 | -389 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1207 |  | 1600 | -393 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 |  | 1600 | -395 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1205 |  | 1600 | -395 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 |  | 1600 | -396 | 75 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1203 |  | 1600 | -397 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1203 |  | 1600 | -397 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1203 |  | 1600 | -397 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1201 |  | 1600 | -399 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 |  | 1600 | -401 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1199 |  | 1600 | -401 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 |  | 1600 | -408 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 |  | 1600 | -410 | 74 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 |  | 1600 | -413 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1184 |  | 1600 | -416 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1180 |  | 1600 | -420 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 |  | 1600 | -427 | 73 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 |  | 1600 | -427 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 72 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1150 |  | 1600 | -450 | 72 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1150 |  | 1600 | -450 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1132 |  | 1600 | -468 | 71 | []

## 2130Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3155
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1581 | 1600 | 1600 | -19 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1507 | 1600 | 1600 | -93 | 94 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1393 | 1600 | 1600 | -207 | 87 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1392 | 1600 | 1600 | -208 | 87 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1348 | 1600 | 1600 | -252 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1346 | 1600 | 1600 | -254 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1303 | 1600 | 1600 | -297 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1299 | 1600 | 1600 | -301 | 81 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1296 | 1600 | 1600 | -304 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 | 1600 | 1600 | -324 | 80 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1273 | 1600 | 1600 | -327 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 | 1600 | 1600 | -380 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1216 | 1600 | 1600 | -384 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 | 1600 | 1600 | -398 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 | 1600 | 1600 | -400 | 75 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1198 | 1600 | 1600 | -402 | 75 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1198 | 1600 | 1600 | -402 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1197 | 1600 | 1600 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 | 1600 | 1600 | -406 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 | 1600 | 1600 | -408 | 74 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 | 1600 | 1600 | -409 | 74 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 | 1600 | 1600 | -411 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 | 1600 | 1600 | -411 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1186 | 1600 | 1600 | -414 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1186 | 1600 | 1600 | -414 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1184 | 1600 | 1600 | -416 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 | 1600 | 1600 | -433 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1166 | 1600 | 1600 | -434 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 | 1600 | 1600 | -440 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1155 | 1600 | 1600 | -445 | 72 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1153 | 1600 | 1600 | -447 | 72 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1143 | 1600 | 1600 | -457 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1136 | 1600 | 1600 | -464 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 21:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3155
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 |  | 1600 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1581 |  | 1600 | -19 | 99 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1507 |  | 1600 | -93 | 94 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1393 |  | 1600 | -207 | 87 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1392 |  | 1600 | -208 | 87 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1348 |  | 1600 | -252 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1346 |  | 1600 | -254 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1303 |  | 1600 | -297 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1299 |  | 1600 | -301 | 81 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1296 |  | 1600 | -304 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1276 |  | 1600 | -324 | 80 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1273 |  | 1600 | -327 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1220 |  | 1600 | -380 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1216 |  | 1600 | -384 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1202 |  | 1600 | -398 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 |  | 1600 | -400 | 75 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1198 |  | 1600 | -402 | 75 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1198 |  | 1600 | -402 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1197 |  | 1600 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1194 |  | 1600 | -406 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 |  | 1600 | -407 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 |  | 1600 | -407 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 |  | 1600 | -408 | 74 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 |  | 1600 | -409 | 74 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 |  | 1600 | -411 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 |  | 1600 | -411 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 |  | 1600 | -412 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 |  | 1600 | -412 | 74 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 |  | 1600 | -412 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 |  | 1600 | -413 | 74 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1186 |  | 1600 | -414 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1186 |  | 1600 | -414 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 |  | 1600 | -415 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1184 |  | 1600 | -416 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1167 |  | 1600 | -433 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1166 |  | 1600 | -434 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1160 |  | 1600 | -440 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1155 |  | 1600 | -445 | 72 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1153 |  | 1600 | -447 | 72 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1143 |  | 1600 | -457 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1136 |  | 1600 | -464 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3336
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1594 | 1600 | 1600 | -6 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1576 | 1600 | 1600 | -24 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1494 | 1600 | 1600 | -106 | 93 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1382 | 1600 | 1600 | -218 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1382 | 1600 | 1600 | -218 | 86 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1380 | 1600 | 1600 | -220 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1370 | 1600 | 1600 | -230 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1333 | 1600 | 1600 | -267 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1329 | 1600 | 1600 | -271 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1319 | 1600 | 1600 | -281 | 82 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1310 | 1600 | 1600 | -290 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 | 1600 | 1600 | -340 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 | 1600 | 1600 | -353 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 | 1600 | 1600 | -362 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 | 1600 | 1600 | -390 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 | 1600 | 1600 | -396 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 | 1600 | 1600 | -396 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 | 1600 | 1600 | -402 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1197 | 1600 | 1600 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 | 1600 | 1600 | -408 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 | 1600 | 1600 | -409 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 | 1600 | 1600 | -410 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 | 1600 | 1600 | -410 | 74 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 | 1600 | 1600 | -411 | 74 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 | 1600 | 1600 | -411 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 | 1600 | 1600 | -411 | 74 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 | 1600 | 1600 | -411 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1186 | 1600 | 1600 | -414 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1180 | 1600 | 1600 | -420 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1168 | 1600 | 1600 | -432 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 | 1600 | 1600 | -436 | 73 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 | 1600 | 1600 | -460 | 71 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1134 | 1600 | 1600 | -466 | 71 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1124 | 1600 | 1600 | -476 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 22:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3336
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1594 |  | 1600 | -6 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1576 |  | 1600 | -24 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1494 |  | 1600 | -106 | 93 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1382 |  | 1600 | -218 | 86 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1382 |  | 1600 | -218 | 86 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1380 |  | 1600 | -220 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1370 |  | 1600 | -230 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1333 |  | 1600 | -267 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1329 |  | 1600 | -271 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1319 |  | 1600 | -281 | 82 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1310 |  | 1600 | -290 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1260 |  | 1600 | -340 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1247 |  | 1600 | -353 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1238 |  | 1600 | -362 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1228 |  | 1600 | -372 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1210 |  | 1600 | -390 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 |  | 1600 | -396 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 |  | 1600 | -396 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1198 |  | 1600 | -402 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1197 |  | 1600 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1193 |  | 1600 | -407 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1192 |  | 1600 | -408 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 |  | 1600 | -409 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 |  | 1600 | -410 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1190 |  | 1600 | -410 | 74 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 |  | 1600 | -411 | 74 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 |  | 1600 | -411 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 |  | 1600 | -411 | 74 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1189 |  | 1600 | -411 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1186 |  | 1600 | -414 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 |  | 1600 | -418 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1180 |  | 1600 | -420 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1168 |  | 1600 | -432 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 |  | 1600 | -436 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1164 |  | 1600 | -436 | 73 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1163 |  | 1600 | -437 | 73 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1163 |  | 1600 | -437 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 |  | 1600 | -441 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1140 |  | 1600 | -460 | 71 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1134 |  | 1600 | -466 | 71 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1124 |  | 1600 | -476 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3379
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 | 1600 | 1600 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1564 | 1600 | 1600 | -36 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1483 | 1600 | 1600 | -117 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1389 | 1600 | 1600 | -211 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1371 | 1600 | 1600 | -229 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 | 1600 | 1600 | -234 | 85 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1336 | 1600 | 1600 | -264 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1333 | 1600 | 1600 | -267 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1321 | 1600 | 1600 | -279 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1318 | 1600 | 1600 | -282 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 | 1600 | 1600 | -352 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 | 1600 | 1600 | -365 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1208 | 1600 | 1600 | -392 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 | 1600 | 1600 | -396 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 | 1600 | 1600 | -400 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1195 | 1600 | 1600 | -405 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 | 1600 | 1600 | -409 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 | 1600 | 1600 | -412 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 | 1600 | 1600 | -413 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1186 | 1600 | 1600 | -414 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 | 1600 | 1600 | -417 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 | 1600 | 1600 | -427 | 73 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 | 1600 | 1600 | -427 | 73 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1162 | 1600 | 1600 | -438 | 73 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1160 | 1600 | 1600 | -440 | 72 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1160 | 1600 | 1600 | -440 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 | 1600 | 1600 | -442 | 72 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1153 | 1600 | 1600 | -447 | 72 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 | 1600 | 1600 | -469 | 71 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1130 | 1600 | 1600 | -470 | 71 | []

## 2330Curative
Detailed results
Generated at: | 2026-04-03 08:25
Business day: | 03.04.2026
Timestamp: | 23:30
Border & direction: | North-Greece Importing
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3379
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1595 |  | 1600 | -5 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1564 |  | 1600 | -36 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1483 |  | 1600 | -117 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1389 |  | 1600 | -211 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1371 |  | 1600 | -229 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 |  | 1600 | -234 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1366 |  | 1600 | -234 | 85 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1336 |  | 1600 | -264 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1333 |  | 1600 | -267 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1321 |  | 1600 | -279 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1318 |  | 1600 | -282 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1248 |  | 1600 | -352 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1235 |  | 1600 | -365 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1226 |  | 1600 | -374 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1208 |  | 1600 | -392 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1204 |  | 1600 | -396 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1200 |  | 1600 | -400 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1195 |  | 1600 | -405 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1191 |  | 1600 | -409 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1188 |  | 1600 | -412 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 |  | 1600 | -413 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1187 |  | 1600 | -413 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1186 |  | 1600 | -414 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 |  | 1600 | -415 | 74 | []
BC | Base Case | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 |  | 1600 | -415 | 74 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 |  | 1600 | -415 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1185 |  | 1600 | -415 | 74 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1183 |  | 1600 | -417 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1182 |  | 1600 | -418 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 |  | 1600 | -427 | 73 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1173 |  | 1600 | -427 | 73 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1163 |  | 1600 | -437 | 73 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1162 |  | 1600 | -438 | 73 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1160 |  | 1600 | -440 | 72 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1160 |  | 1600 | -440 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1159 |  | 1600 | -441 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1158 |  | 1600 | -442 | 72 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1153 |  | 1600 | -447 | 72 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1147 |  | 1600 | -453 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [DIR] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1131 |  | 1600 | -469 | 71 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [DIR] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1130 |  | 1600 | -470 | 71 | []