## 1230Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3194
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1597 | 1600 | 1600 | -3 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1575 | 1600 | 1600 | -25 | 98 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1544 | 1600 | 1600 | -56 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1515 | 1600 | 1600 | -85 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1505 | 1600 | 1600 | -95 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1423 | 1600 | 1600 | -177 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1420 | 1600 | 1600 | -180 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1399 | 1600 | 1600 | -201 | 87 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1323 | 1600 | 1600 | -277 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1319 | 1600 | 1600 | -281 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1314 | 1600 | 1600 | -286 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1312 | 1600 | 1600 | -288 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1306 | 1600 | 1600 | -294 | 82 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1297 | 1600 | 1600 | -303 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 | 1600 | 1600 | -314 | 80 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1279 | 1600 | 1600 | -321 | 80 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1273 | 1600 | 1600 | -327 | 80 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1268 | 1600 | 1600 | -332 | 79 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1268 | 1600 | 1600 | -332 | 79 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1268 | 1600 | 1600 | -332 | 79 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1265 | 1600 | 1600 | -335 | 79 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1265 | 1600 | 1600 | -335 | 79 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1257 | 1600 | 1600 | -343 | 79 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 | 1600 | 1600 | -349 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 | 1600 | 1600 | -350 | 78 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1247 | 1600 | 1600 | -353 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 | 1600 | 1600 | -382 | 76 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 | 1600 | 1600 | -426 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1171 | 1600 | 1600 | -429 | 73 | []

## 1230Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3194
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1597 |  | 1600 | -3 | 100 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1575 |  | 1600 | -25 | 98 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1544 |  | 1600 | -56 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1515 |  | 1600 | -85 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1505 |  | 1600 | -95 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1423 |  | 1600 | -177 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1420 |  | 1600 | -180 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1399 |  | 1600 | -201 | 87 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1323 |  | 1600 | -277 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1319 |  | 1600 | -281 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1314 |  | 1600 | -286 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1312 |  | 1600 | -288 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1306 |  | 1600 | -294 | 82 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1297 |  | 1600 | -303 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 |  | 1600 | -314 | 80 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1279 |  | 1600 | -321 | 80 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 |  | 1600 | -323 | 80 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1273 |  | 1600 | -327 | 80 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1268 |  | 1600 | -332 | 79 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1268 |  | 1600 | -332 | 79 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1268 |  | 1600 | -332 | 79 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1265 |  | 1600 | -335 | 79 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1265 |  | 1600 | -335 | 79 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1257 |  | 1600 | -343 | 79 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 |  | 1600 | -349 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 |  | 1600 | -350 | 78 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1247 |  | 1600 | -353 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 |  | 1600 | -382 | 76 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 |  | 1600 | -426 | 73 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1171 |  | 1600 | -429 | 73 | []

## 1330Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3302
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1598 | 1600 | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1577 | 1600 | 1600 | -23 | 99 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1558 | 1600 | 1600 | -42 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1530 | 1600 | 1600 | -70 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1486 | 1600 | 1600 | -114 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1437 | 1600 | 1600 | -163 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1434 | 1600 | 1600 | -166 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1422 | 1600 | 1600 | -178 | 89 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1397 | 1600 | 1600 | -203 | 87 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1381 | 1600 | 1600 | -219 | 86 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1372 | 1600 | 1600 | -228 | 86 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1348 | 1600 | 1600 | -252 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1344 | 1600 | 1600 | -256 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1336 | 1600 | 1600 | -264 | 83 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1329 | 1600 | 1600 | -271 | 83 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1316 | 1600 | 1600 | -284 | 82 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1309 | 1600 | 1600 | -291 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1305 | 1600 | 1600 | -295 | 82 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1303 | 1600 | 1600 | -297 | 81 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1303 | 1600 | 1600 | -297 | 81 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1298 | 1600 | 1600 | -302 | 81 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1294 | 1600 | 1600 | -306 | 81 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1293 | 1600 | 1600 | -307 | 81 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1291 | 1600 | 1600 | -309 | 81 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 | 1600 | 1600 | -314 | 80 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 | 1600 | 1600 | -314 | 80 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 | 1600 | 1600 | -314 | 80 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1278 | 1600 | 1600 | -322 | 80 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1272 | 1600 | 1600 | -328 | 80 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1192 | 1517 | 1517 | -325 | 79 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1240 | 1600 | 1600 | -360 | 77 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 | 1600 | 1600 | -387 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1180 | 1600 | 1600 | -420 | 74 | []

## 1330Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3302
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1598 |  | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1577 |  | 1600 | -23 | 99 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1558 |  | 1600 | -42 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1530 |  | 1600 | -70 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1486 |  | 1600 | -114 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1437 |  | 1600 | -163 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1434 |  | 1600 | -166 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1422 |  | 1600 | -178 | 89 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1397 |  | 1600 | -203 | 87 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1381 |  | 1600 | -219 | 86 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1372 |  | 1600 | -228 | 86 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1348 |  | 1600 | -252 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1344 |  | 1600 | -256 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1336 |  | 1600 | -264 | 83 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1329 |  | 1600 | -271 | 83 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1316 |  | 1600 | -284 | 82 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1309 |  | 1600 | -291 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1305 |  | 1600 | -295 | 82 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1303 |  | 1600 | -297 | 81 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1303 |  | 1600 | -297 | 81 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1298 |  | 1600 | -302 | 81 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1294 |  | 1600 | -306 | 81 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1293 |  | 1600 | -307 | 81 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1291 |  | 1600 | -309 | 81 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 |  | 1600 | -314 | 80 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 |  | 1600 | -314 | 80 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 |  | 1600 | -314 | 80 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1278 |  | 1600 | -322 | 80 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1277 |  | 1600 | -323 | 80 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1277 |  | 1600 | -323 | 80 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1272 |  | 1600 | -328 | 80 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1192 |  | 1517 | -325 | 79 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1240 |  | 1600 | -360 | 77 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 |  | 1600 | -387 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1180 |  | 1600 | -420 | 74 | []

## 1430Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3289
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1598 | 1600 | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1574 | 1600 | 1600 | -26 | 98 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1570 | 1600 | 1600 | -30 | 98 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1540 | 1600 | 1600 | -60 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1485 | 1600 | 1600 | -115 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1453 | 1600 | 1600 | -147 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1450 | 1600 | 1600 | -150 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1430 | 1600 | 1600 | -170 | 89 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1401 | 1600 | 1600 | -199 | 88 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1389 | 1600 | 1600 | -211 | 87 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1380 | 1600 | 1600 | -220 | 86 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1351 | 1600 | 1600 | -249 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1347 | 1600 | 1600 | -253 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1342 | 1600 | 1600 | -258 | 84 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1332 | 1600 | 1600 | -268 | 83 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1322 | 1600 | 1600 | -278 | 83 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1312 | 1600 | 1600 | -288 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1309 | 1600 | 1600 | -291 | 82 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1305 | 1600 | 1600 | -295 | 82 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1305 | 1600 | 1600 | -295 | 82 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1301 | 1600 | 1600 | -299 | 81 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1297 | 1600 | 1600 | -303 | 81 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1295 | 1600 | 1600 | -305 | 81 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1294 | 1600 | 1600 | -306 | 81 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1291 | 1600 | 1600 | -309 | 81 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1291 | 1600 | 1600 | -309 | 81 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 | 1600 | 1600 | -310 | 81 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 | 1600 | 1600 | -310 | 81 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 | 1600 | 1600 | -310 | 81 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1289 | 1600 | 1600 | -311 | 81 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1289 | 1600 | 1600 | -311 | 81 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1282 | 1600 | 1600 | -318 | 80 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1275 | 1600 | 1600 | -325 | 80 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1273 | 1600 | 1600 | -327 | 80 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1272 | 1600 | 1600 | -328 | 80 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1257 | 1600 | 1600 | -343 | 79 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1179 | 1517 | 1517 | -338 | 78 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 | 1600 | 1600 | -367 | 77 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1166 | 1600 | 1600 | -434 | 73 | []

## 1430Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3289
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1598 |  | 1600 | -2 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1574 |  | 1600 | -26 | 98 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1570 |  | 1600 | -30 | 98 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1540 |  | 1600 | -60 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1485 |  | 1600 | -115 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1453 |  | 1600 | -147 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1450 |  | 1600 | -150 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1430 |  | 1600 | -170 | 89 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1401 |  | 1600 | -199 | 88 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1389 |  | 1600 | -211 | 87 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1380 |  | 1600 | -220 | 86 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1351 |  | 1600 | -249 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1347 |  | 1600 | -253 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1342 |  | 1600 | -258 | 84 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1332 |  | 1600 | -268 | 83 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1322 |  | 1600 | -278 | 83 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1312 |  | 1600 | -288 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1309 |  | 1600 | -291 | 82 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1305 |  | 1600 | -295 | 82 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1305 |  | 1600 | -295 | 82 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1301 |  | 1600 | -299 | 81 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1297 |  | 1600 | -303 | 81 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1295 |  | 1600 | -305 | 81 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1294 |  | 1600 | -306 | 81 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1291 |  | 1600 | -309 | 81 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1291 |  | 1600 | -309 | 81 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 |  | 1600 | -310 | 81 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 |  | 1600 | -310 | 81 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 |  | 1600 | -310 | 81 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1289 |  | 1600 | -311 | 81 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1289 |  | 1600 | -311 | 81 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1282 |  | 1600 | -318 | 80 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1275 |  | 1600 | -325 | 80 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1273 |  | 1600 | -327 | 80 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1272 |  | 1600 | -328 | 80 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1257 |  | 1600 | -343 | 79 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1179 |  | 1517 | -338 | 78 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 |  | 1600 | -367 | 77 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1166 |  | 1600 | -434 | 73 | []

## 1530Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3160
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1593 | 1600 | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1593 | 1600 | 1600 | -7 | 100 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1568 | 1600 | 1600 | -32 | 98 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1542 | 1600 | 1600 | -58 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1499 | 1600 | 1600 | -101 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1455 | 1600 | 1600 | -145 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1451 | 1600 | 1600 | -149 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1415 | 1600 | 1600 | -185 | 88 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1383 | 1600 | 1600 | -217 | 86 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1361 | 1600 | 1600 | -239 | 85 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1352 | 1600 | 1600 | -248 | 84 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1341 | 1600 | 1600 | -259 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 | 1600 | 1600 | -262 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1333 | 1600 | 1600 | -267 | 83 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1322 | 1600 | 1600 | -278 | 83 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1321 | 1600 | 1600 | -279 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1313 | 1600 | 1600 | -287 | 82 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1303 | 1600 | 1600 | -297 | 81 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1296 | 1600 | 1600 | -304 | 81 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1292 | 1600 | 1600 | -308 | 81 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1292 | 1600 | 1600 | -308 | 81 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1291 | 1600 | 1600 | -309 | 81 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 | 1600 | 1600 | -310 | 81 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 | 1600 | 1600 | -310 | 81 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 | 1600 | 1600 | -314 | 80 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 | 1600 | 1600 | -314 | 80 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1284 | 1600 | 1600 | -316 | 80 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1284 | 1600 | 1600 | -316 | 80 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1283 | 1600 | 1600 | -317 | 80 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1280 | 1600 | 1600 | -320 | 80 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1275 | 1600 | 1600 | -325 | 80 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1274 | 1600 | 1600 | -326 | 80 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1268 | 1600 | 1600 | -332 | 79 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []

## 1530Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3160
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1593 |  | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1593 |  | 1600 | -7 | 100 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1568 |  | 1600 | -32 | 98 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1542 |  | 1600 | -58 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1499 |  | 1600 | -101 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1455 |  | 1600 | -145 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1451 |  | 1600 | -149 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1415 |  | 1600 | -185 | 88 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1383 |  | 1600 | -217 | 86 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1361 |  | 1600 | -239 | 85 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1352 |  | 1600 | -248 | 84 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1341 |  | 1600 | -259 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 |  | 1600 | -262 | 84 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1333 |  | 1600 | -267 | 83 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1322 |  | 1600 | -278 | 83 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1321 |  | 1600 | -279 | 83 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1313 |  | 1600 | -287 | 82 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1303 |  | 1600 | -297 | 81 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1296 |  | 1600 | -304 | 81 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1292 |  | 1600 | -308 | 81 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1292 |  | 1600 | -308 | 81 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1291 |  | 1600 | -309 | 81 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 |  | 1600 | -310 | 81 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1290 |  | 1600 | -310 | 81 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 |  | 1600 | -314 | 80 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 |  | 1600 | -314 | 80 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1284 |  | 1600 | -316 | 80 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1284 |  | 1600 | -316 | 80 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1283 |  | 1600 | -317 | 80 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1280 |  | 1600 | -320 | 80 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1275 |  | 1600 | -325 | 80 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1274 |  | 1600 | -326 | 80 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1268 |  | 1600 | -332 | 79 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1266 |  | 1600 | -334 | 79 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1266 |  | 1600 | -334 | 79 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 |  | 1600 | -342 | 79 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1600 | -385 | 76 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []

## 1630Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3270
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1595 | 1600 | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1569 | 1600 | 1600 | -31 | 98 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1523 | 1600 | 1600 | -77 | 95 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1499 | 1600 | 1600 | -101 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1481 | 1600 | 1600 | -119 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1446 | 1600 | 1600 | -154 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1442 | 1600 | 1600 | -158 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1404 | 1600 | 1600 | -196 | 88 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1327 | 1600 | 1600 | -273 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1321 | 1600 | 1600 | -279 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1316 | 1600 | 1600 | -284 | 82 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1316 | 1600 | 1600 | -284 | 82 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1314 | 1600 | 1600 | -286 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1309 | 1600 | 1600 | -291 | 82 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1297 | 1600 | 1600 | -303 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1294 | 1600 | 1600 | -306 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 | 1600 | 1600 | -314 | 80 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1281 | 1600 | 1600 | -319 | 80 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1271 | 1600 | 1600 | -329 | 79 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1270 | 1600 | 1600 | -330 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1265 | 1600 | 1600 | -335 | 79 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1257 | 1600 | 1600 | -343 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 | 1600 | 1600 | -344 | 79 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 | 1600 | 1600 | -344 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 | 1600 | 1600 | -351 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 | 1600 | 1600 | -357 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 | 1600 | 1600 | -394 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 | 1600 | 1600 | -418 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1600 | 1600 | -425 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 | 1600 | 1600 | -436 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1064 | 1517 | 1517 | -453 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3270
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1595 |  | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1569 |  | 1600 | -31 | 98 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1523 |  | 1600 | -77 | 95 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1499 |  | 1600 | -101 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1481 |  | 1600 | -119 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1446 |  | 1600 | -154 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1442 |  | 1600 | -158 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1404 |  | 1600 | -196 | 88 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1327 |  | 1600 | -273 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1321 |  | 1600 | -279 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1316 |  | 1600 | -284 | 82 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1316 |  | 1600 | -284 | 82 | []
GR_TR_CO_00001, TR_GR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski, N-1 TIE 400 kV BABAESKI-N SANTA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1314 |  | 1600 | -286 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1309 |  | 1600 | -291 | 82 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1297 |  | 1600 | -303 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1294 |  | 1600 | -306 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1286 |  | 1600 | -314 | 80 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1281 |  | 1600 | -319 | 80 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1271 |  | 1600 | -329 | 79 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1270 |  | 1600 | -330 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1265 |  | 1600 | -335 | 79 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 |  | 1600 | -342 | 79 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1257 |  | 1600 | -343 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 |  | 1600 | -344 | 79 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 |  | 1600 | -344 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 |  | 1600 | -351 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 |  | 1600 | -357 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 |  | 1600 | -394 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 |  | 1600 | -418 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1600 | -425 | 73 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 |  | 1600 | -436 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1064 |  | 1517 | -453 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3460
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1596 | 1600 | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1594 | 1600 | 1600 | -6 | 100 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1541 | 1600 | 1600 | -59 | 96 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1540 | 1600 | 1600 | -60 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1497 | 1600 | 1600 | -103 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1459 | 1600 | 1600 | -141 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1455 | 1600 | 1600 | -145 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1421 | 1600 | 1600 | -179 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1329 | 1600 | 1600 | -271 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1326 | 1600 | 1600 | -274 | 83 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1325 | 1600 | 1600 | -275 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1315 | 1600 | 1600 | -285 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1308 | 1600 | 1600 | -292 | 82 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1307 | 1600 | 1600 | -293 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1297 | 1600 | 1600 | -303 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1297 | 1600 | 1600 | -303 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1279 | 1600 | 1600 | -321 | 80 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1257 | 1600 | 1600 | -343 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 | 1600 | 1600 | -350 | 78 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 | 1600 | 1600 | -351 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 | 1600 | 1600 | -351 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1238 | 1600 | 1600 | -362 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 | 1600 | 1600 | -368 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1227 | 1600 | 1600 | -373 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 | 1600 | 1600 | -419 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1117 | 1517 | 1517 | -400 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 | 1600 | 1600 | -431 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 | 1600 | 1600 | -440 | 72 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1152 | 1600 | 1600 | -448 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1135 | 1600 | 1600 | -465 | 71 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1133 | 1600 | 1600 | -467 | 71 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1131 | 1600 | 1600 | -469 | 71 | []

## 1730Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3460
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1596 |  | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1594 |  | 1600 | -6 | 100 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1541 |  | 1600 | -59 | 96 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1540 |  | 1600 | -60 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1497 |  | 1600 | -103 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1459 |  | 1600 | -141 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1455 |  | 1600 | -145 | 91 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1421 |  | 1600 | -179 | 89 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1329 |  | 1600 | -271 | 83 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1326 |  | 1600 | -274 | 83 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1325 |  | 1600 | -275 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1315 |  | 1600 | -285 | 82 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1308 |  | 1600 | -292 | 82 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1307 |  | 1600 | -293 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1297 |  | 1600 | -303 | 81 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1297 |  | 1600 | -303 | 81 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1279 |  | 1600 | -321 | 80 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 |  | 1600 | -342 | 79 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 |  | 1600 | -342 | 79 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1257 |  | 1600 | -343 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 |  | 1600 | -350 | 78 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 |  | 1600 | -351 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 |  | 1600 | -351 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1238 |  | 1600 | -362 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 |  | 1600 | -368 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 |  | 1600 | -368 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1227 |  | 1600 | -373 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 |  | 1600 | -419 | 74 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1117 |  | 1517 | -400 | 74 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 |  | 1600 | -431 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 |  | 1600 | -440 | 72 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1152 |  | 1600 | -448 | 72 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1135 |  | 1600 | -465 | 71 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1133 |  | 1600 | -467 | 71 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1131 |  | 1600 | -469 | 71 | []

## 1830Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3117
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1596 | 1600 | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1545 | 1600 | 1600 | -55 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1476 | 1600 | 1600 | -124 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1452 | 1600 | 1600 | -148 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1437 | 1600 | 1600 | -163 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1374 | 1600 | 1600 | -226 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1367 | 1600 | 1600 | -233 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1367 | 1600 | 1600 | -233 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1366 | 1600 | 1600 | -234 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1363 | 1600 | 1600 | -237 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1295 | 1600 | 1600 | -305 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1280 | 1600 | 1600 | -320 | 80 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1280 | 1600 | 1600 | -320 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 | 1600 | 1600 | -349 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 | 1600 | 1600 | -351 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 | 1600 | 1600 | -368 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 | 1600 | 1600 | -368 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 | 1600 | 1600 | -370 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1225 | 1600 | 1600 | -375 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 | 1600 | 1600 | -377 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 | 1600 | 1600 | -377 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 | 1600 | 1600 | -377 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 | 1600 | 1600 | -377 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 | 1600 | 1600 | -379 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1600 | 1600 | -388 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 | 1600 | 1600 | -391 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 75 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 | 1600 | 1600 | -424 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1145 | 1600 | 1600 | -455 | 72 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1133 | 1600 | 1600 | -467 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3117
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1596 |  | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1545 |  | 1600 | -55 | 97 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1476 |  | 1600 | -124 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1452 |  | 1600 | -148 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1437 |  | 1600 | -163 | 90 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1374 |  | 1600 | -226 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1367 |  | 1600 | -233 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1367 |  | 1600 | -233 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1366 |  | 1600 | -234 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1363 |  | 1600 | -237 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1295 |  | 1600 | -305 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1280 |  | 1600 | -320 | 80 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1280 |  | 1600 | -320 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 |  | 1600 | -349 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 |  | 1600 | -351 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 |  | 1600 | -368 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 |  | 1600 | -368 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 |  | 1600 | -368 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 |  | 1600 | -370 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1225 |  | 1600 | -375 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 |  | 1600 | -377 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 |  | 1600 | -377 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 |  | 1600 | -377 | 76 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1223 |  | 1600 | -377 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 |  | 1600 | -379 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1600 | -381 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1600 | -388 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 |  | 1600 | -391 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 75 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 |  | 1600 | -424 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1145 |  | 1600 | -455 | 72 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1133 |  | 1600 | -467 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3036
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1596 | 1600 | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1566 | 1600 | 1600 | -34 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1458 | 1600 | 1600 | -142 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1429 | 1600 | 1600 | -171 | 89 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1401 | 1600 | 1600 | -199 | 88 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1401 | 1600 | 1600 | -199 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1353 | 1600 | 1600 | -247 | 85 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1324 | 1600 | 1600 | -276 | 83 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1321 | 1600 | 1600 | -279 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1318 | 1600 | 1600 | -282 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 | 1600 | 1600 | -379 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1600 | 1600 | -393 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1600 | 1600 | -393 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 | 1600 | 1600 | -398 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 | 1600 | 1600 | -399 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 | 1600 | 1600 | -400 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1600 | 1600 | -402 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 | 1600 | 1600 | -410 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1600 | 1600 | -412 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 | 1600 | 1600 | -422 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 | 1600 | 1600 | -423 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 | 1600 | 1600 | -434 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1152 | 1600 | 1600 | -448 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 | 1600 | 1600 | -466 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3036
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1596 |  | 1600 | -4 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1566 |  | 1600 | -34 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1458 |  | 1600 | -142 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1429 |  | 1600 | -171 | 89 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1401 |  | 1600 | -199 | 88 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1401 |  | 1600 | -199 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1353 |  | 1600 | -247 | 85 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1324 |  | 1600 | -276 | 83 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1321 |  | 1600 | -279 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1318 |  | 1600 | -282 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 |  | 1600 | -379 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1600 | -393 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1600 | -393 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 |  | 1600 | -398 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 |  | 1600 | -399 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 |  | 1600 | -400 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1600 | -402 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 |  | 1600 | -410 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1600 | -412 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 |  | 1600 | -422 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 |  | 1600 | -423 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 |  | 1600 | -434 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1152 |  | 1600 | -448 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 |  | 1600 | -466 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2960
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1595 | 1600 | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1569 | 1600 | 1600 | -31 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1458 | 1600 | 1600 | -142 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1417 | 1600 | 1600 | -183 | 89 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1404 | 1600 | 1600 | -196 | 88 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1404 | 1600 | 1600 | -196 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 | 1600 | 1600 | -262 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1311 | 1600 | 1600 | -289 | 82 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1308 | 1600 | 1600 | -292 | 82 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1305 | 1600 | 1600 | -295 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 | 1600 | 1600 | -350 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1238 | 1600 | 1600 | -362 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1600 | 1600 | -388 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1600 | 1600 | -396 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 | 1600 | 1600 | -399 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 | 1600 | 1600 | -400 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1600 | 1600 | -402 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1600 | 1600 | -403 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1187 | 1600 | 1600 | -413 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 | 1600 | 1600 | -424 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 | 1600 | 1600 | -426 | 73 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 | 1600 | 1600 | -440 | 72 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1146 | 1600 | 1600 | -454 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 | 1600 | 1600 | -468 | 71 | []

## 2030Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2960
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1595 |  | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1569 |  | 1600 | -31 | 98 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1458 |  | 1600 | -142 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1417 |  | 1600 | -183 | 89 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1404 |  | 1600 | -196 | 88 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1404 |  | 1600 | -196 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 |  | 1600 | -262 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1311 |  | 1600 | -289 | 82 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1308 |  | 1600 | -292 | 82 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1305 |  | 1600 | -295 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 |  | 1600 | -350 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1238 |  | 1600 | -362 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1600 | -385 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1600 | -388 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1600 | -396 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 |  | 1600 | -399 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 |  | 1600 | -400 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1600 | -402 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1600 | -403 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1187 |  | 1600 | -413 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 |  | 1600 | -424 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 |  | 1600 | -426 | 73 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 |  | 1600 | -440 | 72 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1146 |  | 1600 | -454 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 |  | 1600 | -468 | 71 | []

## 2130Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2993
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1594 | 1600 | 1600 | -6 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1544 | 1600 | 1600 | -56 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1441 | 1600 | 1600 | -159 | 90 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1434 | 1600 | 1600 | -166 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1398 | 1600 | 1600 | -202 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1397 | 1600 | 1600 | -203 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1346 | 1600 | 1600 | -254 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1322 | 1600 | 1600 | -278 | 83 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1321 | 1600 | 1600 | -279 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1317 | 1600 | 1600 | -283 | 82 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 | 1600 | 1600 | -349 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1227 | 1600 | 1600 | -373 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 | 1600 | 1600 | -379 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1220 | 1600 | 1600 | -380 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1600 | 1600 | -393 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1600 | 1600 | -393 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 | 1600 | 1600 | -398 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 | 1600 | 1600 | -398 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 | 1600 | 1600 | -399 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1600 | 1600 | -402 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1600 | 1600 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1600 | 1600 | -403 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 | 1600 | 1600 | -408 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1600 | 1600 | -412 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1600 | 1600 | -412 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 | 1600 | 1600 | -415 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 | 1600 | 1600 | -423 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1135 | 1600 | 1600 | -465 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2993
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1594 |  | 1600 | -6 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1544 |  | 1600 | -56 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1441 |  | 1600 | -159 | 90 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1434 |  | 1600 | -166 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1398 |  | 1600 | -202 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1397 |  | 1600 | -203 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1346 |  | 1600 | -254 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1322 |  | 1600 | -278 | 83 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1321 |  | 1600 | -279 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1317 |  | 1600 | -283 | 82 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 |  | 1600 | -349 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1227 |  | 1600 | -373 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 |  | 1600 | -379 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1220 |  | 1600 | -380 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1600 | -393 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1600 | -393 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 |  | 1600 | -398 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 |  | 1600 | -398 | 75 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 |  | 1600 | -399 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1600 | -402 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1600 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1600 | -403 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 |  | 1600 | -408 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1600 | -412 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1600 | -412 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 |  | 1600 | -415 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 |  | 1600 | -423 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1135 |  | 1600 | -465 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2983
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1593 | 1600 | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1543 | 1600 | 1600 | -57 | 96 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1444 | 1600 | 1600 | -156 | 90 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1442 | 1600 | 1600 | -158 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1392 | 1600 | 1600 | -208 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1391 | 1600 | 1600 | -209 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1358 | 1600 | 1600 | -242 | 85 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1329 | 1600 | 1600 | -271 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1326 | 1600 | 1600 | -274 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1326 | 1600 | 1600 | -274 | 83 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1276 | 1600 | 1600 | -324 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 | 1600 | 1600 | -366 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 | 1600 | 1600 | -374 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 | 1600 | 1600 | -374 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1224 | 1600 | 1600 | -376 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1600 | 1600 | -393 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1600 | 1600 | -393 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1600 | 1600 | -393 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 | 1600 | 1600 | -394 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 | 1600 | 1600 | -394 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1600 | 1600 | -402 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1600 | 1600 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 | 1600 | 1600 | -407 | 75 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1187 | 1600 | 1600 | -413 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 | 1600 | 1600 | -418 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 | 1600 | 1600 | -466 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1125 | 1600 | 1600 | -475 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2983
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1593 |  | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1543 |  | 1600 | -57 | 96 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1444 |  | 1600 | -156 | 90 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1442 |  | 1600 | -158 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1392 |  | 1600 | -208 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1391 |  | 1600 | -209 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1358 |  | 1600 | -242 | 85 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1329 |  | 1600 | -271 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1326 |  | 1600 | -274 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1326 |  | 1600 | -274 | 83 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1276 |  | 1600 | -324 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 |  | 1600 | -366 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 |  | 1600 | -374 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 |  | 1600 | -374 | 77 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1224 |  | 1600 | -376 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1600 | -393 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1600 | -393 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1600 | -393 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 |  | 1600 | -394 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 |  | 1600 | -394 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1600 | -402 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1600 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 |  | 1600 | -407 | 75 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1187 |  | 1600 | -413 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 |  | 1600 | -418 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 |  | 1600 | -466 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1125 |  | 1600 | -475 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2898
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1595 | 1600 | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1567 | 1600 | 1600 | -33 | 98 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1477 | 1600 | 1600 | -123 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1462 | 1600 | 1600 | -138 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1396 | 1600 | 1600 | -204 | 87 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1373 | 1600 | 1600 | -227 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1373 | 1600 | 1600 | -227 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 | 1600 | 1600 | -262 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1334 | 1600 | 1600 | -266 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1331 | 1600 | 1600 | -269 | 83 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1301 | 1600 | 1600 | -299 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1252 | 1600 | 1600 | -348 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1247 | 1600 | 1600 | -353 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 | 1600 | 1600 | -369 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 | 1600 | 1600 | -374 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 | 1600 | 1600 | -374 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1225 | 1600 | 1600 | -375 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1224 | 1600 | 1600 | -376 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 | 1600 | 1600 | -379 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 | 1600 | 1600 | -379 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1600 | 1600 | -388 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 | 1600 | 1600 | -394 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1600 | 1600 | -396 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 | 1600 | 1600 | -398 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 | 1600 | 1600 | -398 | 75 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 | 1600 | 1600 | -449 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1139 | 1600 | 1600 | -461 | 71 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1129 | 1600 | 1600 | -471 | 71 | []

## 2330Curative
Detailed results
Generated at: | 2026-04-05 08:20
Business day: | 05.04.2026
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2898
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1595 |  | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1567 |  | 1600 | -33 | 98 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1477 |  | 1600 | -123 | 92 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1462 |  | 1600 | -138 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1396 |  | 1600 | -204 | 87 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1373 |  | 1600 | -227 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1373 |  | 1600 | -227 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 |  | 1600 | -262 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1334 |  | 1600 | -266 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1331 |  | 1600 | -269 | 83 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1301 |  | 1600 | -299 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1252 |  | 1600 | -348 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1247 |  | 1600 | -353 | 78 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 |  | 1600 | -369 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 |  | 1600 | -374 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 |  | 1600 | -374 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1225 |  | 1600 | -375 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1224 |  | 1600 | -376 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 |  | 1600 | -379 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 |  | 1600 | -379 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1600 | -381 | 76 | []
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1600 | -381 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1600 | -381 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1600 | -388 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 |  | 1600 | -394 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1600 | -396 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 |  | 1600 | -398 | 75 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 |  | 1600 | -398 | 75 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 |  | 1600 | -449 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1139 |  | 1600 | -461 | 71 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1129 |  | 1600 | -471 | 71 | []