## SRO borders-exports
SUBMISSION DATE: | 07.04.2026
BUSINESS DATE: | 09.04.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC RO-BG
00:00 | 01:00 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 98 | 3417 | 3217 | 2252
01:00 | 02:00 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 98 | 3404 | 3204 | 2242
02:00 | 03:00 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 98 | 3470 | 3270 | 2289
03:00 | 04:00 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 98 | 3559 | 3359 | 2351
04:00 | 05:00 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 98 | 3545 | 3345 | 2342
05:00 | 06:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3574 | 3374 | 2362
06:00 | 07:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 92 | 3526 | 3326 | 2328
07:00 | 08:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3168 | 2968 | 2078
08:00 | 09:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2870 | 2670 | 1869
09:00 | 10:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2479 | 2279 | 1595
10:00 | 11:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2799 | 2599 | 1819
11:00 | 12:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2891 | 2691 | 1884
12:00 | 13:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3418 | 3218 | 2253
13:00 | 14:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3470 | 3270 | 2289
14:00 | 15:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3672 | 3472 | 2430
15:00 | 16:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3599 | 3399 | 2379
16:00 | 17:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3343 | 3143 | 2200
17:00 | 18:00 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 2947 | 2747 | 1923
18:00 | 19:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 2835 | 2635 | 1844
19:00 | 20:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 2646 | 2446 | 1712
20:00 | 21:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 2800 | 2600 | 1820
21:00 | 22:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 2682 | 2482 | 1737
22:00 | 23:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 3002 | 2802 | 1961
23:00 | 00:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 3106 | 2906 | 2034

## SRO borders-imports
SUBMISSION DATE: | 07.04.2026
BUSINESS DATE: | 09.04.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC BG-RO
00:00 | 01:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3206 | 3006 | 2104
01:00 | 02:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3012 | 2812 | 1968
02:00 | 03:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3078 | 2878 | 2015
03:00 | 04:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3335 | 3135 | 2194
04:00 | 05:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3424 | 3224 | 2257
05:00 | 06:00 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | 104 | 3531 | 3331 | 2332
06:00 | 07:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 95 | 3221 | 3021 | 2115
07:00 | 08:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 2681 | 2481 | 1737
08:00 | 09:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 2715 | 2515 | 1760
09:00 | 10:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2386 | 2186 | 1530
10:00 | 11:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2356 | 2156 | 1509
11:00 | 12:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2483 | 2283 | 1598
12:00 | 13:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 95 | 2748 | 2548 | 1784
13:00 | 14:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 96 | 2928 | 2728 | 1910
14:00 | 15:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 96 | 3060 | 2860 | 2002
15:00 | 16:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 96 | 2961 | 2761 | 1933
16:00 | 17:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 96 | 3404 | 3204 | 2243
17:00 | 18:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 4072 | 3872 | 2710
18:00 | 19:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 4102 | 3902 | 2731
19:00 | 20:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3845 | 3645 | 2552
20:00 | 21:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3921 | 3721 | 2605
21:00 | 22:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3889 | 3689 | 2582
22:00 | 23:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3785 | 3585 | 2510
23:00 | 00:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3466 | 3266 | 2286

## SRO borders-exports RAs
SUBMISSION DATE: | 07.04.2026
BUSINESS DATE: | 09.04.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400 kV TINTARENI-KOZLODUI 1 | BG_RA_00001 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  |  |  | helpful | helpful | helpful | helpful | helpful
PRA 400 kV TINTARENI-KOZLODUI 2 | BG_RA_00002 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | [8 empty] | notApplied
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | [8 empty] | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | [8 empty] | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | [8 empty] | notApplied | notApplied
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | [6 empty] | notApplied | notApplied |  |  |  |  | notApplied | notApplied | notApplied | notApplied | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400 kV TINTARENI-KOZLODUI 1 | BG_RA_00001 | topological_ra | [17 empty] | applied
PRA 110 kV S4 | RO_RA_00003 | topological_ra | [17 empty] | applied
PRA 110 kV Dobrogea | RO_RA_00006 | topological_ra | [17 empty] | applied
PRA 110 kV Resita | RO_RA_00007 | topological_ra | [17 empty] | applied
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological_ra | [17 empty] | applied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological_ra | [17 empty] | applied
TOP_CLOSE_400kV_Tantareni _ Kozlodui_c1 | RO_RA_00103 | topological_ra | [17 empty] | applied
TOP_CLOSE_400kV_Resita_Pancevo_c2 | RO_RA_00104 | topological_ra | [17 empty] | applied
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst_ra | [17 empty] | applied
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst_ra | [17 empty] | applied
PST_ARAD 400/220_3 | RO_RA_00101 | pst_ra | [17 empty] | applied
PST_URECHESTI 400/220_1 | RO_RA_00102 | pst_ra | [17 empty] | applied
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
RROVI31 _generator | RO_RA_00105 | costly_ra | [17 empty] | 1
RVMAR_5 _generator | RO_RA_00116 | costly_ra | [17 empty] | 0
RGODI_5 _generator | RO_RA_00117 | costly_ra | [17 empty] | 0
RTOPV_5 _generator | RO_RA_00120 | costly_ra | [17 empty] | 0
RFMEP_5 _generator | RO_RA_00121 | costly_ra | [17 empty] | 0
RVLCE15 _generator | RO_RA_00122 | costly_ra | [17 empty] | 0
RVALD_5 _generator | RO_RA_00123 | costly_ra | [17 empty] | 0
RELAR_5 _generator | RO_RA_00124 | costly_ra | [17 empty] | 0
RAREF_5 _generator | RO_RA_00125 | costly_ra | [17 empty] | 0
RARGS_5 _generator | RO_RA_00126 | costly_ra | [17 empty] | 0
RALBE_5 _generator | RO_RA_00127 | costly_ra | [17 empty] | 0
RCERB_5 _generator | RO_RA_00128 | costly_ra | [17 empty] | 0
RVLCE25 _generator | RO_RA_00129 | costly_ra | [17 empty] | 0
RCLNG_5 _generator | RO_RA_00130 | costly_ra | [17 empty] | 0
RSTUP_5 _generator | RO_RA_00134 | costly_ra | [17 empty] | 0
RDAIES5 _generator | RO_RA_00135 | costly_ra | [17 empty] | 0
RVILN_5 _generator | RO_RA_00136 | costly_ra | [17 empty] | 0
RRIUR15 _generator | RO_RA_00137 | costly_ra | [17 empty] | 0
RMARC_5 _generator | RO_RA_00138 | costly_ra | [17 empty] | 0
RIONE_5 _generator | RO_RA_00139 | costly_ra | [17 empty] | 0
RJIBL_5 _generator | RO_RA_00140 | costly_ra | [17 empty] | 0
RZAVI_5 _generator | RO_RA_00141 | costly_ra | [17 empty] | 0
RCHTU_5 _generator | RO_RA_00142 | costly_ra | [17 empty] | 0
RTRAI_5 _generator | RO_RA_00143 | costly_ra | [17 empty] | 0
RHGLOT5 _generator | RO_RA_00144 | costly_ra | [17 empty] | 0
RCHESJ5 _generator | RO_RA_00145 | costly_ra | [17 empty] | 0
RCHEAC5 _generator | RO_RA_00146 | costly_ra | [17 empty] | 0
RCHEST5 _generator | RO_RA_00147 | costly_ra | [17 empty] | 0
RCHEIO5 _generator | RO_RA_00148 | costly_ra | [17 empty] | 0
RCHDO_5 _generator | RO_RA_00149 | costly_ra | [17 empty] | 0
RFRUN_5 _generator | RO_RA_00150 | costly_ra | [17 empty] | 0
RCIZBI5 _generator | RO_RA_00151 | costly_ra | [17 empty] | 0
RRUSA_5 _generator | RO_RA_00152 | costly_ra | [17 empty] | 0
RHCORN5 _generator | RO_RA_00153 | costly_ra | [17 empty] | 0
RFAGA_5 _generator | RO_RA_00154 | costly_ra | [17 empty] | 0
RUCEA25 _generator | RO_RA_00155 | costly_ra | [17 empty] | 0
RUCEA15 _generator | RO_RA_00156 | costly_ra | [17 empty] | 0
RCIRT_5 _generator | RO_RA_00157 | costly_ra | [17 empty] | 45
RSTEJ25 _generator | RO_RA_00159 | costly_ra | [17 empty] | 32
RVADU_5 _generator | RO_RA_00160 | costly_ra | [17 empty] | 67
RIZVO_5 _generator | RO_RA_00161 | costly_ra | [17 empty] | 9
RDUMB_5 _generator | RO_RA_00162 | costly_ra | [17 empty] | 23
RCOST_5 _generator | RO_RA_00163 | costly_ra | [17 empty] | 24
RBUHU_5 _generator | RO_RA_00164 | costly_ra | [17 empty] | 13
RRACO_5 _generator | RO_RA_00165 | costly_ra | [17 empty] | 23
RGARL_5 _generator | RO_RA_00166 | costly_ra | [17 empty] | 23
RLILI_5 _generator | RO_RA_00167 | costly_ra | [17 empty] | 23
RBACS_5 _generator | RO_RA_00168 | costly_ra | [17 empty] | 98
RFARA_5 _generator | RO_RA_00169 | costly_ra | [17 empty] | 30
RSISC_5 _generator | RO_RA_00170 | costly_ra | [17 empty] | 44
RMARA_5 _generator | RO_RA_00171 | costly_ra | [17 empty] | 0
RTECU_5 _generator | RO_RA_00172 | costly_ra | [17 empty] | 0
RSUGA22 _generator | RO_RA_00174 | costly_ra | [17 empty] | 150
RGILC22 _generator | RO_RA_00175 | costly_ra | [17 empty] | 150
RSEBE_5 _generator | RO_RA_00176 | costly_ra | [17 empty] | 55
RIAZUA5 _generator | RO_RA_00177 | costly_ra | [17 empty] | 71
RRETE22 _generator | RO_RA_00180 | costly_ra | [17 empty] | 222
RCIRNA5 _generator | RO_RA_00182 | costly_ra | [17 empty] | 29
RCIRNB5 _generator | RO_RA_00183 | costly_ra | [17 empty] | 27
RHATE_5 _generator | RO_RA_00184 | costly_ra | [17 empty] | 52

## SRO borders-imports RAs
SUBMISSION DATE: | 07.04.2026
BUSINESS DATE: | 09.04.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400 kV TINTARENI-KOZLODUI 1 | BG_RA_00001 | topological | helpful |  | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | [9 empty] | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | [9 empty] | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | notApplied | helpful | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | helpful
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | [9 empty] | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | [9 empty] | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | [9 empty] | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 110 kV S4 | RO_RA_00003 | topological_ra | [17 empty] | applied | [5 empty] | applied
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst_ra | [17 empty] | applied | [5 empty] | applied
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst_ra | [17 empty] | applied | [5 empty] | applied
PST_ARAD 400/220_3 | RO_RA_00101 | pst_ra | [17 empty] | applied | [5 empty] | applied
PST_URECHESTI 400/220_1 | RO_RA_00102 | pst_ra | [17 empty] | applied | [5 empty] | applied
PRA 110 kV S5 | RO_RA_00004 | topological_ra | [23 empty] | applied
PRA 110 kV Pelicanu | RO_RA_00005 | topological_ra | [23 empty] | applied
PRA 110 kV Dobrogea | RO_RA_00006 | topological_ra | [23 empty] | applied
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst_ra |  |  |  |  | applied
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst_ra |  |  |  |  | applied
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
RPDF222 _generator | RO_RA_00114 | costly_ra |  | 336
RGODI_5 _generator | RO_RA_00117 | costly_ra |  | 0 | [5 empty] | 114 | 114 | 114 | 114 | 114
RTOPV_5 _generator | RO_RA_00120 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RFMEP_5 _generator | RO_RA_00121 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RVLCE15 _generator | RO_RA_00122 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RVALD_5 _generator | RO_RA_00123 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RELAR_5 _generator | RO_RA_00124 | costly_ra |  | 0 | [5 empty] | 0 | 10
RAREF_5 _generator | RO_RA_00125 | costly_ra |  | 0 | [5 empty] | 10 | 10 | 0 | 0 | 0
RARGS_5 _generator | RO_RA_00126 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RALBE_5 _generator | RO_RA_00127 | costly_ra |  | 0 | [5 empty] | 30 | 30 | 0 | 0 | 0
RCERB_5 _generator | RO_RA_00128 | costly_ra |  | 0 | [5 empty] | 15 | 15 | 0 | 0 | 0
RVLCE25 _generator | RO_RA_00129 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RCLNG_5 _generator | RO_RA_00130 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RSTUP_5 _generator | RO_RA_00134 | costly_ra |  | 0 | [5 empty] | 45 | 45 | 0 | 0 | 0
RDAIES5 _generator | RO_RA_00135 | costly_ra |  | 0 | [5 empty] | 0 | 37 | 0 | 0 | 0
RVILN_5 _generator | RO_RA_00136 | costly_ra |  | 0 | [5 empty] | 0 | 46 | 0 | 0 | 0
RRIUR15 _generator | RO_RA_00137 | costly_ra |  | 0 | [5 empty] | 48 | 48 | 0 | 0 | 0
RMARC_5 _generator | RO_RA_00138 | costly_ra |  | 0 | [5 empty] | 39 | 39 | 0 | 0 | 0
RIONE_5 _generator | RO_RA_00139 | costly_ra |  | 0 | [5 empty] | 38 | 38 | 0 | 0 | 0
RJIBL_5 _generator | RO_RA_00140 | costly_ra |  | 0 | [5 empty] | 0 | 38 | 0 | 0 | 0
RZAVI_5 _generator | RO_RA_00141 | costly_ra |  | 0 | [5 empty] | 0 | 38 | 0 | 0 | 0
RCHTU_5 _generator | RO_RA_00142 | costly_ra |  | 0 | [5 empty] | 0 | 74 | 0 | 0 | 0
RTRAI_5 _generator | RO_RA_00143 | costly_ra |  | 0 | [5 empty] | 36 | 45 | 0 | 0 | 0
RHGLOT5 _generator | RO_RA_00144 | costly_ra |  | 0 | [5 empty] | 0 | 18 | 0 | 0 | 0
RCHESJ5 _generator | RO_RA_00145 | costly_ra |  | 0 | [5 empty] | 50 | 50 | 18 | 3 | 0
RCHEAC5 _generator | RO_RA_00146 | costly_ra |  | 0 | [5 empty] | 38 | 0 | 0 | 0 | 0
RCHEST5 _generator | RO_RA_00147 | costly_ra |  | 0 | [5 empty] | 26 | 14 | 0 | 0 | 0
RCHEIO5 _generator | RO_RA_00148 | costly_ra |  | 0 | [5 empty] | 53 | 0 | 53 | 53 | 51
RCHDO_5 _generator | RO_RA_00149 | costly_ra |  | 0 | [5 empty] | 53 | 0 | 53 | 53 | 53
RFRUN_5 _generator | RO_RA_00150 | costly_ra |  | 0 | [5 empty] | 53 | 0 | 53 | 53 | 53
RCIZBI5 _generator | RO_RA_00151 | costly_ra |  | 0 | [5 empty] | 53 | 0 | 53 | 53 | 53
RRUSA_5 _generator | RO_RA_00152 | costly_ra |  | 0 | [5 empty] | 53 | 0 | 53 | 53 | 53
RHCORN5 _generator | RO_RA_00153 | costly_ra |  | 0 | [5 empty] | 0 | 59 | 0 | 0 | 0
RFAGA_5 _generator | RO_RA_00154 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RUCEA25 _generator | RO_RA_00155 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RUCEA15 _generator | RO_RA_00156 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RCIRT_5 _generator | RO_RA_00157 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RRACO_5 _generator | RO_RA_00165 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RGARL_5 _generator | RO_RA_00166 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RLILI_5 _generator | RO_RA_00167 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RBACS_5 _generator | RO_RA_00168 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RFARA_5 _generator | RO_RA_00169 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RSISC_5 _generator | RO_RA_00170 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RMARA_5 _generator | RO_RA_00171 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RTECU_5 _generator | RO_RA_00172 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RSUGA22 _generator | RO_RA_00174 | costly_ra |  | 121
RSEBE_5 _generator | RO_RA_00176 | costly_ra |  | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0
RRETE22 _generator | RO_RA_00180 | costly_ra |  | 222
RRETE_5 _generator | RO_RA_00181 | costly_ra |  | 20 | [5 empty] | 0
RCIRNA5 _generator | RO_RA_00182 | costly_ra |  | 29 | [5 empty] | 0
RCIRNB5 _generator | RO_RA_00183 | costly_ra |  | 27 | [5 empty] | 0
RHATE_5 _generator | RO_RA_00184 | costly_ra |  | 52 | [5 empty] | 0
RVMAR_5 _generator | RO_RA_00116 | costly_ra | [7 empty] | 50 | 50 | 50 | 50 | 50
RVADU_5 _generator | RO_RA_00160 | costly_ra | [7 empty] | 0 | 0
RDUMB_5 _generator | RO_RA_00162 | costly_ra | [8 empty] | 0 | 0 | 0 | 0
RCOST_5 _generator | RO_RA_00163 | costly_ra | [8 empty] | 0 | 0 | 0 | 0
RBUHU_5 _generator | RO_RA_00164 | costly_ra | [8 empty] | 0 | 0 | 0 | 0