## SRO borders-exports
SUBMISSION DATE: | 10.04.2026
BUSINESS DATE: | 12.04.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC RO-BG
00:00 | 01:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 98 | 3812 | 3612 | 2528
01:00 | 02:00 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 97 | 3849 | 3649 | 2554
02:00 | 03:00 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 97 | 3941 | 3741 | 2619
03:00 | 04:00 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 96 | 3880 | 3680 | 2576
04:00 | 05:00 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 96 | 3841 | 3641 | 2549
05:00 | 06:00 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 96 | 3852 | 3652 | 2556
06:00 | 07:00 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 98 | 3818 | 3618 | 2533
07:00 | 08:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 3692 | 3492 | 2444
08:00 | 09:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3655 | 3455 | 2418
09:00 | 10:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3682 | 3482 | 2437
10:00 | 11:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3956 | 3756 | 2629
11:00 | 12:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 3746 | 3546 | 2482
12:00 | 13:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 3655 | 3455 | 2418
13:00 | 14:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 3321 | 3121 | 2185
14:00 | 15:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3288 | 3088 | 2162
15:00 | 16:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 3688 | 3488 | 2442
16:00 | 17:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3074 | 2874 | 2012
17:00 | 18:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3044 | 2844 | 1991
18:00 | 19:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3121 | 2921 | 2045
19:00 | 20:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3307 | 3107 | 2175
20:00 | 21:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3256 | 3056 | 2139
21:00 | 22:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3313 | 3113 | 2179
22:00 | 23:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 98 | 3815 | 3615 | 2530
23:00 | 00:00 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 97 | 3825 | 3625 | 2538

## SRO borders-imports
SUBMISSION DATE: | 10.04.2026
BUSINESS DATE: | 12.04.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC BG-RO
00:00 | 01:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3513 | 3313 | 2319
01:00 | 02:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3521 | 3321 | 2325
02:00 | 03:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3560 | 3360 | 2352
03:00 | 04:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3625 | 3425 | 2398
04:00 | 05:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3617 | 3417 | 2392
05:00 | 06:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3646 | 3446 | 2412
06:00 | 07:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3475 | 3275 | 2292
07:00 | 08:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3582 | 3382 | 2367
08:00 | 09:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 97 | 3708 | 3508 | 2456
09:00 | 10:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3761 | 3561 | 2493
10:00 | 11:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 96 | 3705 | 3505 | 2454
11:00 | 12:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 99 | 3598 | 3398 | 2379
12:00 | 13:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 99 | 3594 | 3394 | 2376
13:00 | 14:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3533 | 3333 | 2333
14:00 | 15:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3508 | 3308 | 2316
15:00 | 16:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3714 | 3514 | 2460
16:00 | 17:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3745 | 3545 | 2482
17:00 | 18:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3540 | 3340 | 2338
18:00 | 19:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3798 | 3598 | 2519
19:00 | 20:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3617 | 3417 | 2392
20:00 | 21:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3612 | 3412 | 2388
21:00 | 22:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3866 | 3666 | 2566
22:00 | 23:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3620 | 3420 | 2394
23:00 | 00:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3620 | 3420 | 2394

## SRO borders-exports RAs
SUBMISSION DATE: | 10.04.2026
BUSINESS DATE: | 12.04.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400 kV TINTARENI-KOZLODUI 1 | BG_RA_00001 | topological | helpful | helpful | helpful | helpful | helpful |  | helpful | [15 empty] | helpful | helpful
PRA 400 kV TINTARENI-KOZLODUI 2 | BG_RA_00002 | topological | notApplied | notApplied | notApplied | notApplied | notApplied |  | notApplied | [15 empty] | notApplied | notApplied
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  | helpful |  |  |  | helpful | helpful | helpful | helpful | helpful
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  | helpful |  |  |  | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | helpful | notApplied | helpful | helpful | helpful | helpful | helpful | helpful |  |  | helpful |  |  |  | helpful | helpful | helpful | notApplied | notApplied
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  | notApplied |  |  |  | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  | helpful |  |  |  | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  | notApplied |  |  |  | notApplied | notApplied | notApplied | notApplied | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 110 kV S4 | RO_RA_00003 | topological_ra | [8 empty] | applied
PRA 110 kV S5 | RO_RA_00004 | topological_ra | [8 empty] | applied
PRA 110 kV Pelicanu | RO_RA_00005 | topological_ra | [8 empty] | applied
PRA 110 kV Dobrogea | RO_RA_00006 | topological_ra | [8 empty] | applied
PRA 110 kV Resita | RO_RA_00007 | topological_ra | [8 empty] | applied
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst_ra | [8 empty] | applied
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst_ra | [8 empty] | applied
PST_ARAD 400/220_3 | RO_RA_00101 | pst_ra | [8 empty] | applied
PST_URECHESTI 400/220_1 | RO_RA_00102 | pst_ra | [8 empty] | applied
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
RROVI31 _generator | RO_RA_00105 | costly_ra | [10 empty] | 1 | [9 empty] | 1
RPDF212 _generator | RO_RA_00115 | costly_ra | [10 empty] | 224
RTOPV_5 _generator | RO_RA_00120 | costly_ra | [10 empty] | 0 | [9 empty] | 0
RFMEP_5 _generator | RO_RA_00121 | costly_ra | [10 empty] | 0 | [9 empty] | 0
RVLCE15 _generator | RO_RA_00122 | costly_ra | [10 empty] | 0 | [9 empty] | 0
RVALD_5 _generator | RO_RA_00123 | costly_ra | [10 empty] | 0 | [9 empty] | 0
RARGS_5 _generator | RO_RA_00126 | costly_ra | [10 empty] | 0 | [9 empty] | 0
RALBE_5 _generator | RO_RA_00127 | costly_ra | [10 empty] | 0 | [9 empty] | 0
RCERB_5 _generator | RO_RA_00128 | costly_ra | [10 empty] | 0 | [9 empty] | 0
RVLCE25 _generator | RO_RA_00129 | costly_ra | [10 empty] | 0 | [9 empty] | 0
RCLNG_5 _generator | RO_RA_00130 | costly_ra | [10 empty] | 0 | [9 empty] | 0
RLOTR22 _generator | RO_RA_00131 | costly_ra | [10 empty] | 0 | [9 empty] | 0
RUCEA25 _generator | RO_RA_00155 | costly_ra | [10 empty] | 0
RUCEA15 _generator | RO_RA_00156 | costly_ra | [10 empty] | 0
RSTEJ_5 _generator | RO_RA_00158 | costly_ra | [10 empty] | 0
RDUMB_5 _generator | RO_RA_00162 | costly_ra | [10 empty] | 0 | [9 empty] | 23
RCOST_5 _generator | RO_RA_00163 | costly_ra | [10 empty] | 0 | [9 empty] | 24
RRACO_5 _generator | RO_RA_00165 | costly_ra | [10 empty] | 0 | [9 empty] | 23
RGARL_5 _generator | RO_RA_00166 | costly_ra | [10 empty] | 0 | [9 empty] | 23
RLILI_5 _generator | RO_RA_00167 | costly_ra | [10 empty] | 0 | [9 empty] | 23
RBACS_5 _generator | RO_RA_00168 | costly_ra | [10 empty] | 0 | [9 empty] | 39
RFARA_5 _generator | RO_RA_00169 | costly_ra | [10 empty] | 5 | [9 empty] | 30
RSISC_5 _generator | RO_RA_00170 | costly_ra | [10 empty] | 44 | [9 empty] | 44
RMARA_5 _generator | RO_RA_00171 | costly_ra | [10 empty] | 46 | [9 empty] | 46
RTECU_5 _generator | RO_RA_00172 | costly_ra | [10 empty] | 34 | [9 empty] | 34
RMARI22 _generator | RO_RA_00173 | costly_ra | [10 empty] | 217
RSUGA22 _generator | RO_RA_00174 | costly_ra | [10 empty] | 150
RGILC22 _generator | RO_RA_00175 | costly_ra | [10 empty] | 150
RSEBE_5 _generator | RO_RA_00176 | costly_ra | [10 empty] | 55 | [9 empty] | 55
RIAZUA5 _generator | RO_RA_00177 | costly_ra | [10 empty] | 71 | [9 empty] | 71
RREME_5 _generator | RO_RA_00178 | costly_ra | [10 empty] | 96
RMUNT_5 _generator | RO_RA_00179 | costly_ra | [10 empty] | 58
RELAR_5 _generator | RO_RA_00124 | costly_ra | [20 empty] | 0
RAREF_5 _generator | RO_RA_00125 | costly_ra | [20 empty] | 0
RSTEJ25 _generator | RO_RA_00159 | costly_ra | [20 empty] | 32
RVADU_5 _generator | RO_RA_00160 | costly_ra | [20 empty] | 67
RIZVO_5 _generator | RO_RA_00161 | costly_ra | [20 empty] | 9
RBUHU_5 _generator | RO_RA_00164 | costly_ra | [20 empty] | 13
RRETE22 _generator | RO_RA_00180 | costly_ra | [20 empty] | 111
RCIRNA5 _generator | RO_RA_00182 | costly_ra | [20 empty] | 29
RCIRNB5 _generator | RO_RA_00183 | costly_ra | [20 empty] | 27
RHATE_5 _generator | RO_RA_00184 | costly_ra | [20 empty] | 52

## SRO borders-imports RAs
SUBMISSION DATE: | 10.04.2026
BUSINESS DATE: | 12.04.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400 kV TINTARENI-KOZLODUI 1 | BG_RA_00001 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
RTOPV_5 _generator | RO_RA_00120 | costly_ra | [19 empty] | 0 | 0 | 0
RFMEP_5 _generator | RO_RA_00121 | costly_ra | [19 empty] | 0 | 0 | 0
RVLCE15 _generator | RO_RA_00122 | costly_ra | [19 empty] | 0 | 0 | 0
RVALD_5 _generator | RO_RA_00123 | costly_ra | [19 empty] | 0 | 0 | 0
RELAR_5 _generator | RO_RA_00124 | costly_ra | [19 empty] | 0 | 0 | 0
RAREF_5 _generator | RO_RA_00125 | costly_ra | [19 empty] | 0 | 0 | 0
RARGS_5 _generator | RO_RA_00126 | costly_ra | [19 empty] | 0 | 0 | 0
RALBE_5 _generator | RO_RA_00127 | costly_ra | [19 empty] | 0 | 0 | 0
RCERB_5 _generator | RO_RA_00128 | costly_ra | [19 empty] | 0 | 0 | 0
RVLCE25 _generator | RO_RA_00129 | costly_ra | [19 empty] | 0 | 0 | 0
RCLNG_5 _generator | RO_RA_00130 | costly_ra | [19 empty] | 0 | 0 | 0
RCHEAC5 _generator | RO_RA_00146 | costly_ra | [19 empty] | 15 | 31
RCHEIO5 _generator | RO_RA_00148 | costly_ra | [19 empty] | 53 | 53 | 9
RCHDO_5 _generator | RO_RA_00149 | costly_ra | [19 empty] | 53 | 53 | 53
RFRUN_5 _generator | RO_RA_00150 | costly_ra | [19 empty] | 53 | 53 | 53
RCIZBI5 _generator | RO_RA_00151 | costly_ra | [19 empty] | 53 | 53 | 53
RRUSA_5 _generator | RO_RA_00152 | costly_ra | [19 empty] | 53 | 53 | 53
RRACO_5 _generator | RO_RA_00165 | costly_ra | [19 empty] | 0 | 0 | 0
RGARL_5 _generator | RO_RA_00166 | costly_ra | [19 empty] | 0 | 0 | 0
RLILI_5 _generator | RO_RA_00167 | costly_ra | [19 empty] | 0 | 0 | 0
RBACS_5 _generator | RO_RA_00168 | costly_ra | [19 empty] | 0 | 0 | 0
RFARA_5 _generator | RO_RA_00169 | costly_ra | [19 empty] | 0 | 0 | 0
RSISC_5 _generator | RO_RA_00170 | costly_ra | [19 empty] | 0 | 0 | 0
RMARA_5 _generator | RO_RA_00171 | costly_ra | [19 empty] | 0 | 0 | 0
RTECU_5 _generator | RO_RA_00172 | costly_ra | [19 empty] | 0 | 0 | 0
RSEBE_5 _generator | RO_RA_00176 | costly_ra | [19 empty] | 0 | 0 | 0
RRETE_5 _generator | RO_RA_00181 | costly_ra | [19 empty] | 0
RCIRNA5 _generator | RO_RA_00182 | costly_ra | [19 empty] | 0
RCIRNB5 _generator | RO_RA_00183 | costly_ra | [19 empty] | 0
RHATE_5 _generator | RO_RA_00184 | costly_ra | [19 empty] | 0