## 0030
Detailed results
Generated at: | 10/04/2026 20:51:02
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3131.47
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1596 | 1600 | -4 | 100 | 1137 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1582 | 1600 | -18 | 99 | 1129 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1496 | 1600 | -104 | 94 | 1067 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1425 | 1600 | -175 | 89 | 1013 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1386 | 1600 | -214 | 87 | 978 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1385 | 1600 | -215 | 87 | 978 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1358 | 1600 | -242 | 85 | 970 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1321 | 1600 | -279 | 83 | 943 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1321 | 1600 | -279 | 83 | 942 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1316 | 1600 | -284 | 82 | 940 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1275 | 1600 | -325 | 80 | 911 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1600 | -334 | 79 | 905 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 884 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 871 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 870 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1600 | -383 | 76 | 869 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 861 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 860 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 856 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 855 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 855 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 854 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 854 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 854 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 853 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 75 | 852 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 74 | 852 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 851 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 849 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 846 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 844 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 837 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 836 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1167 | 1600 | -433 | 73 | 812 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1162 | 1600 | -438 | 73 | 809 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1162 | 1600 | -438 | 73 | 808 | AC

## 0130
Detailed results
Generated at: | 10/04/2026 20:51:02
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3035.35
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1597 | 1600 | -3 | 100 | 1139 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1493 | 1600 | -107 | 93 | 1065 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1452 | 1600 | -148 | 91 | 1033 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1380 | 1600 | -220 | 86 | 986 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1318 | 1600 | -282 | 82 | 934 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1317 | 1600 | -283 | 82 | 934 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1312 | 1600 | -288 | 82 | 937 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1309 | 1600 | -291 | 82 | 935 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1306 | 1600 | -294 | 82 | 934 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1600 | -334 | 79 | 905 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1600 | -335 | 79 | 905 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 872 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1600 | -383 | 76 | 869 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 866 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 865 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 863 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 861 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 861 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 861 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 860 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 859 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 859 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 858 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 858 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 857 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 856 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 856 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 74 | 852 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1600 | -414 | 74 | 847 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 847 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 847 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 845 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1600 | -429 | 73 | 836 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1156 | 1600 | -444 | 72 | 826 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 820 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1148 | 1600 | -452 | 72 | 799 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1143 | 1600 | -457 | 71 | 796 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1143 | 1600 | -457 | 71 | 795 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1600 | -479 | 70 | 802 | AC

## 0230
Detailed results
Generated at: | 10/04/2026 20:51:02
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3094.24
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1597 | 1600 | -3 | 100 | 1139 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1553 | 1600 | -47 | 97 | 1109 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1491 | 1600 | -109 | 93 | 1064 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1448 | 1600 | -152 | 91 | 1030 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1377 | 1600 | -223 | 86 | 983 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1318 | 1600 | -282 | 82 | 935 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1317 | 1600 | -283 | 82 | 934 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1315 | 1600 | -285 | 82 | 939 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1312 | 1600 | -288 | 82 | 938 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1311 | 1600 | -289 | 82 | 938 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1600 | -336 | 79 | 903 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1260 | 1600 | -340 | 79 | 901 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1600 | -354 | 78 | 891 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 878 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1600 | -375 | 77 | 876 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 873 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 871 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 865 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 865 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 863 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 862 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 861 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 861 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 860 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 860 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 858 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 859 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 858 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 858 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 857 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 857 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 857 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 854 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 850 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1600 | -413 | 74 | 848 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 847 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 846 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 821 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1140 | 1600 | -460 | 71 | 793 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1138 | 1600 | -462 | 71 | 792 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1138 | 1600 | -462 | 71 | 792 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1600 | -474 | 70 | 805 | AC

## 0330
Detailed results
Generated at: | 10/04/2026 20:51:02
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3096.37
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1599 | 1600 | -1 | 100 | 1141 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1554 | 1600 | -46 | 97 | 1110 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1492 | 1600 | -108 | 93 | 1065 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1441 | 1600 | -159 | 90 | 1026 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1368 | 1600 | -232 | 86 | 977 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1322 | 1600 | -278 | 83 | 938 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1321 | 1600 | -279 | 83 | 937 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1311 | 1600 | -289 | 82 | 936 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1309 | 1600 | -291 | 82 | 936 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1307 | 1600 | -293 | 82 | 935 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1276 | 1600 | -324 | 80 | 912 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1261 | 1600 | -339 | 79 | 901 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 900 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 890 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 877 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 877 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 871 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 865 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 864 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 864 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 862 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 862 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 860 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 860 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 859 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 859 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 858 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 858 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 857 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 856 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 856 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 854 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 854 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 851 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1600 | -414 | 74 | 848 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 846 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 846 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 846 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 822 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1149 | 1600 | -451 | 72 | 799 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1149 | 1600 | -451 | 72 | 799 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1147 | 1600 | -453 | 72 | 797 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1128 | 1600 | -472 | 70 | 806 | AC

## 0430
Detailed results
Generated at: | 10/04/2026 20:51:02
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3094.77
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1600 | 1600 | 0 | 100 | 1142 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1551 | 1600 | -49 | 97 | 1108 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1493 | 1600 | -107 | 93 | 1065 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1447 | 1600 | -153 | 90 | 1030 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1376 | 1600 | -224 | 86 | 982 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1315 | 1600 | -285 | 82 | 933 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1315 | 1600 | -285 | 82 | 932 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1315 | 1600 | -285 | 82 | 939 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1311 | 1600 | -289 | 82 | 937 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1311 | 1600 | -289 | 82 | 937 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1600 | -338 | 79 | 902 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1259 | 1600 | -341 | 79 | 900 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 890 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 877 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1600 | -375 | 77 | 876 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 872 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 866 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 865 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 864 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 863 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 862 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 861 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 860 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 860 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 859 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 859 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 858 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 858 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 857 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 856 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 856 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 854 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 853 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 850 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 846 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 846 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1151 | 1600 | -449 | 72 | 800 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1149 | 1600 | -451 | 72 | 799 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 820 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1149 | 1600 | -451 | 72 | 799 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1600 | -474 | 70 | 805 | AC

## 0530
Detailed results
Generated at: | 10/04/2026 20:51:02
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3079.17
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1597 | 1600 | -3 | 100 | 1139 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1545 | 1600 | -55 | 97 | 1104 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1490 | 1600 | -110 | 93 | 1063 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1441 | 1600 | -159 | 90 | 1025 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1370 | 1600 | -230 | 86 | 978 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1312 | 1600 | -288 | 82 | 937 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1310 | 1600 | -290 | 82 | 930 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1309 | 1600 | -291 | 82 | 929 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1308 | 1600 | -292 | 82 | 936 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1305 | 1600 | -295 | 82 | 933 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1261 | 1600 | -339 | 79 | 901 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 899 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1240 | 1600 | -360 | 77 | 886 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 874 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1600 | -383 | 76 | 869 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 869 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 868 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 864 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 860 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 859 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 857 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 857 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 856 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 856 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 856 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 856 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 853 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 853 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 851 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 851 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 851 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 850 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 846 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 846 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 844 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 74 | 841 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1155 | 1600 | -445 | 72 | 803 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1154 | 1600 | -446 | 72 | 803 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1154 | 1600 | -446 | 72 | 803 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 817 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1120 | 1600 | -480 | 70 | 801 | AC

## 0630
Detailed results
Generated at: | 10/04/2026 20:51:03
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3196.12
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1596 | 1600 | -4 | 100 | 1138 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1570 | 1600 | -30 | 98 | 1121 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1485 | 1600 | -115 | 93 | 1059 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1438 | 1600 | -162 | 90 | 1024 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1366 | 1600 | -234 | 85 | 976 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1346 | 1600 | -254 | 84 | 954 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1345 | 1600 | -255 | 84 | 953 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1330 | 1600 | -270 | 83 | 949 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1327 | 1600 | -273 | 83 | 948 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1326 | 1600 | -274 | 83 | 948 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1280 | 1600 | -320 | 80 | 915 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1280 | 1600 | -320 | 80 | 915 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1259 | 1600 | -341 | 79 | 900 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1600 | -346 | 78 | 897 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1600 | -363 | 77 | 885 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 882 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1600 | -377 | 76 | 875 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 873 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 867 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 865 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 864 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 864 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 864 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 75 | 864 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 863 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 863 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 863 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 862 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 862 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 862 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 859 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 859 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 858 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 858 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 857 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 854 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 853 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1600 | -413 | 74 | 849 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1600 | -413 | 74 | 849 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 844 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 827 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1126 | 1600 | -474 | 70 | 784 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1126 | 1600 | -474 | 70 | 784 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1600 | -478 | 70 | 803 | AC

## 0730
Detailed results
Generated at: | 10/04/2026 20:51:03
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3127.38
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1598 | 1600 | -2 | 100 | 1140 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1571 | 1600 | -29 | 98 | 1122 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1487 | 1600 | -113 | 93 | 1062 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1427 | 1600 | -173 | 89 | 1016 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1372 | 1600 | -228 | 86 | 980 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1337 | 1600 | -263 | 84 | 948 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1337 | 1600 | -263 | 84 | 948 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1336 | 1600 | -264 | 84 | 954 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1332 | 1600 | -268 | 83 | 953 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1329 | 1600 | -271 | 83 | 950 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1288 | 1600 | -312 | 80 | 920 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1281 | 1600 | -319 | 80 | 917 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1600 | -334 | 79 | 906 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1600 | -343 | 79 | 899 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1243 | 1600 | -357 | 78 | 890 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1600 | -361 | 77 | 886 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 878 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 873 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 872 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 871 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1600 | -384 | 76 | 871 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1600 | -384 | 76 | 870 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 869 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 869 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 868 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 868 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 867 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 867 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 867 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 865 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 75 | 864 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 864 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 864 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 863 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 863 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 860 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 858 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 855 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 855 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 852 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 835 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1138 | 1600 | -462 | 71 | 814 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1124 | 1600 | -476 | 70 | 781 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1124 | 1600 | -476 | 70 | 780 | AC

## 0830
Detailed results
Generated at: | 10/04/2026 20:51:03
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2844.76
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1596 | 1600 | -4 | 100 | 1139 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1525 | 1600 | -75 | 95 | 1090 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1492 | 1600 | -108 | 93 | 1066 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1395 | 1600 | -205 | 87 | 996 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1369 | 1600 | -231 | 86 | 979 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1294 | 1600 | -306 | 81 | 926 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1288 | 1600 | -312 | 81 | 922 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1286 | 1600 | -314 | 80 | 921 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1271 | 1600 | -329 | 79 | 905 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1271 | 1600 | -329 | 79 | 910 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1271 | 1600 | -329 | 79 | 904 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1263 | 1600 | -337 | 79 | 904 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1251 | 1600 | -349 | 78 | 896 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | 878 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1600 | -383 | 76 | 871 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 867 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 867 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 864 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 861 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 861 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 857 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 856 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 855 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 855 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 855 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 855 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 855 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 853 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 853 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 853 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 852 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 851 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 848 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 847 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 847 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 846 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 846 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 840 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1158 | 1600 | -442 | 72 | 822 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1158 | 1600 | -442 | 72 | 822 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 825 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1131 | 1600 | -469 | 71 | 810 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1127 | 1600 | -473 | 70 | 807 | AC

## 0930
Detailed results
Generated at: | 10/04/2026 20:51:03
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2857.92
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1595 | 1600 | -5 | 100 | 1139 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1560 | 1600 | -40 | 98 | 1116 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1505 | 1600 | -95 | 94 | 1076 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1390 | 1600 | -210 | 87 | 993 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1376 | 1600 | -224 | 86 | 984 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1315 | 1600 | -285 | 82 | 942 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1315 | 1600 | -285 | 82 | 937 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1314 | 1600 | -286 | 82 | 936 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1303 | 1600 | -297 | 81 | 932 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1300 | 1600 | -300 | 81 | 931 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1283 | 1600 | -317 | 80 | 919 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1275 | 1600 | -325 | 80 | 913 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1241 | 1600 | -359 | 78 | 889 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 887 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 882 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1600 | -371 | 77 | 880 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 878 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 875 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1600 | -383 | 76 | 872 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 870 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 868 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 868 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 868 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 868 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 867 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 866 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 866 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 866 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 75 | 865 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 865 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 862 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 861 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 861 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 861 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 860 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 74 | 854 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 854 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 844 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 842 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 813 | AC

## 1030
Detailed results
Generated at: | 10/04/2026 20:51:03
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3103.48
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1599 | 1600 | -1 | 100 | 1141 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1570 | 1600 | -30 | 98 | 1122 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1513 | 1600 | -87 | 95 | 1081 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1452 | 1600 | -148 | 91 | 1038 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1438 | 1600 | -162 | 90 | 1026 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1386 | 1600 | -214 | 87 | 991 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1383 | 1600 | -217 | 86 | 990 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1346 | 1600 | -254 | 84 | 963 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1306 | 1600 | -294 | 82 | 934 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1303 | 1600 | -297 | 81 | 932 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1297 | 1600 | -303 | 81 | 921 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1296 | 1600 | -304 | 81 | 921 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1284 | 1600 | -316 | 80 | 919 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1600 | -334 | 79 | 906 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1600 | -336 | 79 | 904 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1600 | -343 | 79 | 900 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1249 | 1600 | -351 | 78 | 894 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1242 | 1600 | -358 | 78 | 889 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1241 | 1600 | -359 | 78 | 888 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 886 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1600 | -365 | 77 | 884 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1600 | -365 | 77 | 884 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1600 | -365 | 77 | 884 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1600 | -365 | 77 | 884 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1600 | -366 | 77 | 883 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1600 | -366 | 77 | 883 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1232 | 1600 | -368 | 77 | 882 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 881 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1600 | -370 | 77 | 881 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1600 | -371 | 77 | 880 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | 878 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1600 | -375 | 77 | 877 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 875 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 875 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 874 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 873 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 873 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 863 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 851 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 825 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1128 | 1600 | -472 | 70 | 807 | AC

## 1130
Detailed results
Generated at: | 10/04/2026 20:51:03
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3346.7
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1599 | 1600 | -1 | 100 | 1141 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1576 | 1600 | -24 | 98 | 1125 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1512 | 1600 | -88 | 95 | 1080 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1490 | 1600 | -110 | 93 | 1064 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1444 | 1600 | -156 | 90 | 1029 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1443 | 1600 | -157 | 90 | 1030 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1440 | 1600 | -160 | 90 | 1029 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1380 | 1600 | -220 | 86 | 986 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1336 | 1600 | -264 | 84 | 955 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1317 | 1600 | -283 | 82 | 941 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1310 | 1600 | -290 | 82 | 937 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1295 | 1600 | -305 | 81 | 926 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1286 | 1600 | -314 | 80 | 919 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1284 | 1600 | -316 | 80 | 910 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1283 | 1600 | -317 | 80 | 909 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1600 | -334 | 79 | 906 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1260 | 1600 | -340 | 79 | 901 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1260 | 1600 | -340 | 79 | 901 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 900 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1600 | -343 | 79 | 899 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1255 | 1600 | -345 | 78 | 898 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1600 | -347 | 78 | 896 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1600 | -347 | 78 | 896 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1252 | 1600 | -348 | 78 | 896 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1252 | 1600 | -348 | 78 | 896 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1251 | 1600 | -349 | 78 | 895 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1251 | 1600 | -349 | 78 | 895 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1251 | 1600 | -349 | 78 | 895 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1248 | 1600 | -352 | 78 | 893 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1248 | 1600 | -352 | 78 | 893 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1600 | -354 | 78 | 891 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1600 | -356 | 78 | 890 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1243 | 1600 | -357 | 78 | 889 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 885 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1600 | -366 | 77 | 883 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1168 | 1517 | -349 | 77 | 824 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 877 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | 877 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 867 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 858 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 854 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 837 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1121 | 1600 | -479 | 70 | 802 | AC

## 1230
Detailed results
Generated at: | 10/04/2026 20:51:03
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3379.48
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1597 | 1600 | -3 | 100 | 1139 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1562 | 1600 | -38 | 98 | 1116 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1508 | 1600 | -92 | 94 | 1076 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1487 | 1600 | -113 | 93 | 1062 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1442 | 1600 | -158 | 90 | 1030 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1439 | 1600 | -161 | 90 | 1029 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1439 | 1600 | -161 | 90 | 1026 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1370 | 1600 | -230 | 86 | 979 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1326 | 1600 | -274 | 83 | 948 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1315 | 1600 | -285 | 82 | 941 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1243 | 1517 | -274 | 82 | 876 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1303 | 1600 | -297 | 81 | 932 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1287 | 1600 | -313 | 80 | 920 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1281 | 1600 | -319 | 80 | 915 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1269 | 1600 | -331 | 79 | 899 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1268 | 1600 | -332 | 79 | 898 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 900 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1600 | -346 | 78 | 897 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1600 | -347 | 78 | 896 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1600 | -350 | 78 | 894 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1600 | -350 | 78 | 894 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1248 | 1600 | -352 | 78 | 893 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1247 | 1600 | -353 | 78 | 892 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1600 | -354 | 78 | 891 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 891 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 891 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1600 | -356 | 78 | 890 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1600 | -356 | 78 | 890 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1241 | 1600 | -359 | 78 | 888 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1241 | 1600 | -359 | 78 | 888 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1240 | 1600 | -360 | 78 | 887 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 885 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1600 | -363 | 77 | 885 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1600 | -366 | 77 | 882 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1600 | -370 | 77 | 880 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 878 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 872 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 871 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1152 | 1517 | -365 | 76 | 814 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1150 | 1517 | -367 | 76 | 813 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 863 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 852 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 850 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 842 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 833 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1098 | 1517 | -419 | 72 | 776 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1066 | 1517 | -451 | 70 | 751 | AC

## 1330
Detailed results
Generated at: | 10/04/2026 20:51:03
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3485.46
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1595 | 1600 | -5 | 100 | 1137 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1581 | 1600 | -19 | 99 | 1128 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1522 | 1600 | -78 | 95 | 1088 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1510 | 1600 | -90 | 94 | 1078 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1480 | 1600 | -120 | 92 | 1056 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1476 | 1600 | -124 | 92 | 1055 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1475 | 1600 | -125 | 92 | 1050 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1376 | 1517 | -141 | 91 | 967 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1397 | 1600 | -203 | 87 | 998 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1352 | 1600 | -248 | 85 | 967 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1276 | 1517 | -241 | 84 | 899 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1275 | 1517 | -242 | 84 | 898 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1341 | 1600 | -259 | 84 | 958 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1316 | 1600 | -284 | 82 | 941 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1307 | 1600 | -293 | 82 | 934 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1301 | 1600 | -299 | 81 | 930 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1283 | 1600 | -317 | 80 | 918 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1217 | 1517 | -300 | 80 | 857 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1281 | 1600 | -319 | 80 | 906 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1280 | 1600 | -320 | 80 | 905 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1272 | 1600 | -328 | 80 | 910 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1269 | 1600 | -331 | 79 | 907 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1600 | -334 | 79 | 905 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1600 | -335 | 79 | 905 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1600 | -336 | 79 | 904 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1263 | 1600 | -337 | 79 | 903 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1600 | -338 | 79 | 903 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1600 | -338 | 79 | 903 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1261 | 1600 | -339 | 79 | 902 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1261 | 1600 | -339 | 79 | 901 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 900 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 900 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1600 | -343 | 79 | 899 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1255 | 1600 | -345 | 78 | 898 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1255 | 1600 | -345 | 78 | 898 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1600 | -346 | 78 | 897 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1600 | -350 | 78 | 894 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1185 | 1517 | -332 | 78 | 832 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 890 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 890 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1600 | -366 | 77 | 882 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1600 | -366 | 77 | 882 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1166 | 1517 | -351 | 77 | 820 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1164 | 1517 | -353 | 77 | 816 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1164 | 1517 | -353 | 77 | 816 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1163 | 1517 | -354 | 77 | 817 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1163 | 1517 | -354 | 77 | 818 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1224 | 1600 | -376 | 76 | 875 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1152 | 1517 | -365 | 76 | 810 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 869 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 868 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1212 | 1600 | -388 | 76 | 853 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1146 | 1517 | -371 | 76 | 805 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 859 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1139 | 1517 | -378 | 75 | 802 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1139 | 1517 | -378 | 75 | 802 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1134 | 1517 | -383 | 75 | 798 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1117 | 1517 | -400 | 74 | 787 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1115 | 1517 | -402 | 73 | 786 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1113 | 1517 | -404 | 73 | 785 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 838 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1110 | 1517 | -407 | 73 | 782 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1109 | 1517 | -408 | 73 | 782 | AC
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1106 | 1517 | -411 | 73 | 780 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1105 | 1517 | -412 | 73 | 779 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1105 | 1517 | -412 | 73 | 780 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1103 | 1517 | -414 | 73 | 778 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1102 | 1517 | -415 | 73 | 778 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1101 | 1517 | -416 | 73 | 777 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1101 | 1517 | -416 | 73 | 777 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1098 | 1517 | -419 | 72 | 775 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1098 | 1517 | -419 | 72 | 774 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1098 | 1517 | -419 | 72 | 775 | AC
Base case | Base case | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1098 | 1517 | -419 | 72 | 775 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1097 | 1517 | -420 | 72 | 775 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1097 | 1517 | -420 | 72 | 774 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1095 | 1517 | -422 | 72 | 773 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1095 | 1517 | -422 | 72 | 773 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1087 | 1517 | -430 | 72 | 767 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1086 | 1517 | -431 | 72 | 767 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1600 | -457 | 71 | 817 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1076 | 1517 | -441 | 71 | 756 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1071 | 1517 | -446 | 71 | 754 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1070 | 1517 | -447 | 71 | 753 | AC

## 1430
Detailed results
Generated at: | 10/04/2026 20:51:03
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3453.49
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1596 | 1600 | -4 | 100 | 1138 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1582 | 1600 | -18 | 99 | 1129 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1525 | 1600 | -75 | 95 | 1089 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1510 | 1600 | -90 | 94 | 1078 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1481 | 1600 | -119 | 93 | 1057 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1478 | 1600 | -122 | 92 | 1052 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1478 | 1600 | -122 | 92 | 1056 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1357 | 1517 | -160 | 89 | 953 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1397 | 1600 | -203 | 87 | 998 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1353 | 1600 | -247 | 85 | 967 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1343 | 1600 | -257 | 84 | 960 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1257 | 1517 | -260 | 83 | 886 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1254 | 1517 | -263 | 83 | 884 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1318 | 1600 | -282 | 82 | 942 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1311 | 1600 | -289 | 82 | 937 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1305 | 1600 | -295 | 82 | 933 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1296 | 1600 | -304 | 81 | 926 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1277 | 1600 | -323 | 80 | 913 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1277 | 1600 | -323 | 80 | 903 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1276 | 1600 | -324 | 80 | 902 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1272 | 1600 | -328 | 80 | 910 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1271 | 1600 | -329 | 79 | 909 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1269 | 1600 | -331 | 79 | 907 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1269 | 1600 | -331 | 79 | 908 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1600 | -334 | 79 | 905 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1600 | -334 | 79 | 905 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1600 | -334 | 79 | 905 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1600 | -335 | 79 | 904 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1600 | -335 | 79 | 904 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1197 | 1517 | -320 | 79 | 844 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1600 | -338 | 79 | 902 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1261 | 1600 | -339 | 79 | 902 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1261 | 1600 | -339 | 79 | 902 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1260 | 1600 | -340 | 79 | 901 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 900 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 900 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1600 | -346 | 78 | 897 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1252 | 1600 | -348 | 78 | 895 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1249 | 1600 | -351 | 78 | 893 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1600 | -354 | 78 | 891 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 885 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1600 | -363 | 77 | 885 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1236 | 1600 | -364 | 77 | 884 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1166 | 1517 | -351 | 77 | 818 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 873 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1150 | 1517 | -367 | 76 | 808 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1147 | 1517 | -370 | 76 | 804 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1147 | 1517 | -370 | 76 | 804 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 862 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1146 | 1517 | -371 | 76 | 804 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1144 | 1517 | -373 | 75 | 804 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11 GNSANT15 1 | 1198 | 1600 | -402 | 75 | 843 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1134 | 1517 | -383 | 75 | 798 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1128 | 1517 | -389 | 74 | 793 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1123 | 1517 | -394 | 74 | 790 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1122 | 1517 | -395 | 74 | 790 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 845 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1115 | 1517 | -402 | 74 | 785 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1099 | 1517 | -418 | 72 | 775 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1098 | 1517 | -420 | 72 | 774 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1097 | 1517 | -420 | 72 | 774 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1092 | 1517 | -425 | 72 | 770 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 823 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1090 | 1517 | -427 | 72 | 769 | AC
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1089 | 1517 | -428 | 72 | 768 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1088 | 1517 | -429 | 72 | 767 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1086 | 1517 | -431 | 72 | 766 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1086 | 1517 | -431 | 72 | 766 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1085 | 1517 | -432 | 72 | 766 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1085 | 1517 | -432 | 72 | 766 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1084 | 1517 | -433 | 71 | 765 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1082 | 1517 | -435 | 71 | 763 | AC
Base case | Base case | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1082 | 1517 | -435 | 71 | 763 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1082 | 1517 | -435 | 71 | 763 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1081 | 1517 | -436 | 71 | 763 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1081 | 1517 | -436 | 71 | 763 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1080 | 1517 | -437 | 71 | 762 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1078 | 1517 | -439 | 71 | 761 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1078 | 1517 | -439 | 71 | 760 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1070 | 1517 | -447 | 71 | 755 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1069 | 1517 | -448 | 70 | 755 | AC

## 1530
Detailed results
Generated at: | 10/04/2026 20:51:04
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3272.31
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1594 | 1600 | -6 | 100 | 1137 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1568 | 1600 | -32 | 98 | 1120 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1506 | 1600 | -94 | 94 | 1075 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1496 | 1600 | -104 | 94 | 1069 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1455 | 1600 | -145 | 91 | 1037 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1441 | 1600 | -159 | 90 | 1029 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1438 | 1600 | -162 | 90 | 1028 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1372 | 1600 | -228 | 86 | 981 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1326 | 1600 | -274 | 83 | 948 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1317 | 1600 | -283 | 82 | 942 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1308 | 1600 | -292 | 82 | 935 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1293 | 1600 | -307 | 81 | 925 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1288 | 1600 | -312 | 80 | 921 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1272 | 1600 | -328 | 80 | 910 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1269 | 1600 | -331 | 79 | 899 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1268 | 1600 | -332 | 79 | 899 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1259 | 1600 | -341 | 79 | 901 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1259 | 1600 | -341 | 79 | 900 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 900 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1256 | 1600 | -344 | 79 | 899 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1256 | 1600 | -344 | 79 | 899 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1256 | 1600 | -344 | 79 | 899 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1600 | -346 | 78 | 897 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1600 | -347 | 78 | 896 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1600 | -347 | 78 | 896 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1600 | -347 | 78 | 896 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1600 | -347 | 78 | 896 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1600 | -350 | 78 | 894 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1249 | 1600 | -351 | 78 | 893 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1247 | 1600 | -353 | 78 | 892 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 891 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 891 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1600 | -356 | 78 | 890 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1236 | 1600 | -364 | 77 | 884 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 882 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 882 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1232 | 1600 | -368 | 77 | 881 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 874 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 869 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11 GNSANT11 1 | 1148 | 1517 | -369 | 76 | 811 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 861 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 859 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 73 | 841 | AC

## 1630
Detailed results
Generated at: | 10/04/2026 20:51:04
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3197.65
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1597 | 1600 | -3 | 100 | 1138 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1586 | 1600 | -14 | 99 | 1132 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1509 | 1600 | -91 | 94 | 1076 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1501 | 1600 | -99 | 94 | 1072 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1473 | 1600 | -127 | 92 | 1048 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1439 | 1600 | -161 | 90 | 1027 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1435 | 1600 | -165 | 90 | 1025 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1380 | 1600 | -220 | 86 | 985 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1336 | 1600 | -264 | 84 | 955 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1318 | 1600 | -282 | 82 | 942 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1313 | 1600 | -287 | 82 | 939 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1300 | 1600 | -300 | 81 | 929 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1299 | 1600 | -301 | 81 | 913 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1298 | 1600 | -302 | 81 | 912 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1295 | 1600 | -305 | 81 | 925 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1289 | 1600 | -311 | 81 | 921 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1274 | 1600 | -326 | 80 | 911 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1266 | 1600 | -334 | 79 | 905 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1600 | -335 | 79 | 904 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1600 | -336 | 79 | 903 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1263 | 1600 | -337 | 79 | 903 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1263 | 1600 | -337 | 79 | 903 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1600 | -338 | 79 | 902 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1600 | -338 | 79 | 902 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1261 | 1600 | -339 | 79 | 901 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1261 | 1600 | -339 | 79 | 901 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1261 | 1600 | -339 | 79 | 901 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 900 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1600 | -343 | 79 | 898 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1256 | 1600 | -344 | 78 | 898 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1600 | -346 | 78 | 897 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1600 | -346 | 78 | 896 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1600 | -346 | 78 | 896 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1600 | -350 | 78 | 894 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 890 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1243 | 1600 | -357 | 78 | 889 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1243 | 1600 | -357 | 78 | 889 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1600 | -365 | 77 | 883 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 882 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | 876 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 864 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 844 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 820 | AC

## 1730
Detailed results
Generated at: | 10/04/2026 20:51:04
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3041.87
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1594 | 1600 | -6 | 100 | 1139 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1550 | 1600 | -50 | 97 | 1106 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1464 | 1600 | -136 | 92 | 1046 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1413 | 1600 | -187 | 88 | 1011 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1408 | 1600 | -192 | 88 | 1004 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1372 | 1600 | -228 | 86 | 980 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1368 | 1600 | -232 | 86 | 979 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1356 | 1600 | -244 | 85 | 969 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1354 | 1600 | -246 | 85 | 958 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1354 | 1600 | -246 | 85 | 957 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1310 | 1600 | -290 | 82 | 937 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1276 | 1600 | -324 | 80 | 913 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1276 | 1600 | -324 | 80 | 913 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1600 | -335 | 79 | 905 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1600 | -338 | 79 | 903 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1600 | -343 | 79 | 899 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1600 | -350 | 78 | 894 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 883 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 883 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 883 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 883 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 882 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1232 | 1600 | -368 | 77 | 882 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1232 | 1600 | -368 | 77 | 882 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1232 | 1600 | -368 | 77 | 882 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 881 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 881 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1600 | -371 | 77 | 880 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1600 | -371 | 77 | 880 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 879 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 879 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 879 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1600 | -375 | 77 | 877 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1600 | -377 | 76 | 875 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 870 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 869 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 869 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 868 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 864 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 862 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 836 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 72 | 819 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1600 | -477 | 70 | 804 | AC

## 1830
Detailed results
Generated at: | 10/04/2026 20:51:04
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3118.14
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1596 | 1600 | -4 | 100 | 1140 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1581 | 1600 | -19 | 99 | 1128 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1394 | 1600 | -206 | 87 | 985 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1393 | 1600 | -207 | 87 | 985 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1389 | 1600 | -211 | 87 | 990 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1357 | 1600 | -243 | 85 | 970 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1336 | 1600 | -264 | 84 | 954 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1334 | 1600 | -266 | 83 | 954 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1332 | 1600 | -268 | 83 | 953 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1295 | 1600 | -305 | 81 | 926 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1270 | 1600 | -330 | 79 | 908 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1600 | -346 | 78 | 897 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 881 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 877 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 874 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 873 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 869 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 867 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 867 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 867 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 867 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 866 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 865 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 865 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 75 | 864 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 864 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 864 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 862 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 862 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 861 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 861 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 857 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 852 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 852 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 850 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 822 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1600 | -477 | 70 | 803 | AC

## 1930
Detailed results
Generated at: | 10/04/2026 20:51:04
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3059.64
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1596 | 1600 | -4 | 100 | 1138 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1573 | 1600 | -27 | 98 | 1123 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1481 | 1600 | -119 | 93 | 1057 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1400 | 1600 | -200 | 88 | 990 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1399 | 1600 | -201 | 87 | 990 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1355 | 1600 | -245 | 85 | 966 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1297 | 1600 | -303 | 81 | 927 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1290 | 1600 | -310 | 81 | 922 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1278 | 1600 | -322 | 80 | 913 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1274 | 1600 | -326 | 80 | 911 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1255 | 1600 | -345 | 78 | 897 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 891 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1225 | 1600 | -375 | 77 | 850 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1215 | 1600 | -385 | 76 | 842 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1214 | 1600 | -386 | 76 | 841 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 867 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 861 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 856 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 852 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 850 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 849 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1184 | 1600 | -416 | 74 | 820 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 845 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 842 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 842 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 74 | 842 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1600 | -426 | 73 | 840 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1600 | -427 | 73 | 839 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1600 | -427 | 73 | 839 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 839 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 838 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 837 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 837 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 837 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 836 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 836 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 834 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 831 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 828 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1600 | -452 | 72 | 821 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1141 | 1600 | -459 | 71 | 816 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1140 | 1600 | -460 | 71 | 790 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1135 | 1600 | -465 | 71 | 787 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 810 | AC

## 2030
Detailed results
Generated at: | 10/04/2026 20:51:04
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3027.53
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1596 | 1600 | -4 | 100 | 1138 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1554 | 1600 | -46 | 97 | 1109 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1476 | 1600 | -124 | 92 | 1053 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1384 | 1600 | -216 | 87 | 979 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1383 | 1600 | -217 | 86 | 979 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1347 | 1600 | -253 | 84 | 960 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1281 | 1600 | -319 | 80 | 915 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1273 | 1600 | -327 | 80 | 883 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1271 | 1600 | -329 | 79 | 909 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1257 | 1600 | -343 | 79 | 898 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1600 | -347 | 78 | 896 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1243 | 1600 | -357 | 78 | 861 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1243 | 1600 | -357 | 78 | 861 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 885 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 882 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1226 | 1600 | -374 | 77 | 849 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 854 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 852 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1600 | -413 | 74 | 849 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1182 | 1600 | -418 | 74 | 819 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 841 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 838 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 838 | AC
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1168 | 1600 | -432 | 73 | 810 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1600 | -439 | 73 | 831 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1600 | -439 | 73 | 831 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1600 | -439 | 73 | 831 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1600 | -440 | 72 | 830 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 829 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 828 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 828 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 828 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1156 | 1600 | -444 | 72 | 827 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1600 | -446 | 72 | 826 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1600 | -446 | 72 | 826 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1600 | -446 | 72 | 826 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 825 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 824 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1148 | 1600 | -452 | 72 | 795 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 821 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 71 | 818 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 810 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1120 | 1600 | -480 | 70 | 801 | AC

## 2130
Detailed results
Generated at: | 10/04/2026 20:51:04
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3168.36
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1598 | 1600 | -2 | 100 | 1139 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1588 | 1600 | -12 | 99 | 1133 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1486 | 1600 | -114 | 93 | 1061 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1409 | 1600 | -191 | 88 | 995 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1408 | 1600 | -192 | 88 | 995 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1393 | 1600 | -207 | 87 | 991 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1326 | 1600 | -274 | 83 | 947 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1319 | 1600 | -281 | 82 | 943 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1308 | 1600 | -292 | 82 | 933 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1303 | 1600 | -297 | 81 | 932 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1279 | 1600 | -321 | 80 | 914 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1259 | 1600 | -341 | 79 | 900 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1232 | 1600 | -368 | 77 | 881 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 867 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 862 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 861 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 862 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 856 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 854 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 75 | 852 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 851 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 851 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 850 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 849 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1600 | -413 | 74 | 849 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1600 | -413 | 74 | 848 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1600 | -414 | 74 | 848 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 847 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1184 | 1600 | -416 | 74 | 820 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1184 | 1600 | -416 | 74 | 819 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 845 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 840 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 840 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1173 | 1600 | -427 | 73 | 812 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1173 | 1600 | -427 | 73 | 813 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 834 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 834 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 833 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 823 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1600 | -478 | 70 | 801 | AC

## 2230
Detailed results
Generated at: | 10/04/2026 20:51:04
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3086.17
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1597 | 1600 | -3 | 100 | 1139 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1579 | 1600 | -21 | 99 | 1127 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1489 | 1600 | -111 | 93 | 1062 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1395 | 1600 | -205 | 87 | 985 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1394 | 1600 | -206 | 87 | 984 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1389 | 1600 | -211 | 87 | 988 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1316 | 1600 | -284 | 82 | 940 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1304 | 1600 | -296 | 82 | 932 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1260 | 1600 | -340 | 79 | 900 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1256 | 1600 | -344 | 79 | 898 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 877 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1207 | 1600 | -393 | 75 | 863 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 861 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 859 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 855 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 854 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 75 | 852 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1190 | 1600 | -410 | 74 | 825 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1190 | 1600 | -410 | 74 | 825 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 850 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1600 | -413 | 74 | 848 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1600 | -413 | 74 | 848 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1600 | -414 | 74 | 848 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1600 | -414 | 74 | 848 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1600 | -414 | 74 | 848 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 847 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 846 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 845 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 845 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 844 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 844 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1180 | 1600 | -420 | 74 | 818 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1600 | -426 | 73 | 839 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 838 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1600 | -429 | 73 | 837 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1600 | -429 | 73 | 837 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 831 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1151 | 1600 | -449 | 72 | 800 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1600 | -477 | 70 | 801 | AC

## 2330
Detailed results
Generated at: | 10/04/2026 20:51:04
Business day: | 2026-04-12
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3094.07
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1599 | 1600 | -1 | 100 | 1140 | AC
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1591 | 1600 | -9 | 99 | 1136 | AC
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1494 | 1600 | -106 | 93 | 1066 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1405 | 1600 | -195 | 88 | 992 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1404 | 1600 | -196 | 88 | 992 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1394 | 1600 | -206 | 87 | 993 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1322 | 1600 | -278 | 83 | 944 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1313 | 1600 | -287 | 82 | 938 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1308 | 1600 | -292 | 82 | 934 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1303 | 1600 | -297 | 81 | 932 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1600 | -335 | 79 | 904 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1263 | 1600 | -337 | 79 | 903 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1600 | -363 | 77 | 884 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 867 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 865 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 861 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 861 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 856 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 854 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 854 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 854 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 854 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 854 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 852 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 852 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 850 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 847 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 845 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1600 | -427 | 73 | 839 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1171 | 1600 | -429 | 73 | 813 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1171 | 1600 | -429 | 73 | 813 | AC
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11 GKARDI13 1 | 1157 | 1600 | -443 | 72 | 803 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1600 | -467 | 71 | 808 | AC