## 0030
Detailed results
Generated at: | 13/04/2026 22:13:44
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3700
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1914 | 2000 | -86 | 96 | 1345 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1908 | 2000 | -92 | 95 | 1340 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1892 | 2000 | -108 | 95 | 1323 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1890 | 2000 | -110 | 94 | 1327 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1881 | 2000 | -119 | 94 | 1321 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1880 | 2000 | -120 | 94 | 1328 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1876 | 2000 | -124 | 94 | 1318 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1872 | 2000 | -128 | 94 | 1315 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1872 | 2000 | -128 | 94 | 1311 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1871 | 2000 | -129 | 94 | 1314 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1868 | 2000 | -132 | 93 | 1312 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1857 | 2000 | -143 | 93 | 1307 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1829 | 2000 | -171 | 91 | 1284 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1787 | 2000 | -213 | 89 | 1258 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1784 | 2000 | -216 | 89 | 1243 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1784 | 2000 | -216 | 89 | -1219 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1771 | 2000 | -229 | 89 | 1236 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1771 | 2000 | -229 | 89 | -1208 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1051 | 1248 | -197 | 84 | 429 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1051 | 1248 | -197 | 84 | 429 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1683 | 2000 | -317 | 84 | 1164 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1049 | 1248 | -200 | 84 | 428 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1049 | 1248 | -200 | 84 | 428 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1674 | 2000 | -326 | 84 | 1159 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1045 | 1248 | -204 | 84 | 427 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1045 | 1248 | -204 | 84 | 427 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1430 | 1836 | -406 | 78 | 1021 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1420 | 1836 | -416 | 77 | 1013 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1420 | 1836 | -416 | 77 | 1013 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1405 | 1836 | -431 | 77 | 1003 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1405 | 1836 | -431 | 77 | 1003 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1374 | 1836 | -462 | 75 | 980 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 926 | 1248 | -323 | 74 | 378 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 926 | 1248 | -323 | 74 | 378 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1836 | -475 | 74 | 970 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1360 | 1836 | -476 | 74 | 970 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1358 | 1836 | -478 | 74 | 969 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1354 | 1836 | -482 | 74 | 966 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 920 | 1248 | -329 | 74 | 375 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1836 | -484 | 74 | 965 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1836 | -484 | 74 | 965 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1347 | 1836 | -489 | 73 | 961 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1334 | 1836 | -502 | 73 | 951 | AC

## 0130
Detailed results
Generated at: | 13/04/2026 22:13:45
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3750
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Medgidia Sud - Rahman/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1919 | 2000 | -81 | 96 | 1347 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1915 | 2000 | -85 | 96 | 1339 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1914 | 2000 | -86 | 96 | 1343 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1904 | 2000 | -96 | 95 | 1344 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1898 | 2000 | -102 | 95 | 1329 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1898 | 2000 | -102 | 95 | 1332 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1893 | 2000 | -107 | 95 | 1328 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1884 | 2000 | -116 | 94 | 1323 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1884 | 2000 | -116 | 94 | 1325 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1882 | 2000 | -118 | 94 | 1321 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1880 | 2000 | -120 | 94 | 1319 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1875 | 2000 | -125 | 94 | 1316 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1850 | 2000 | -150 | 93 | 1298 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1846 | 2000 | -154 | 92 | -1260 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1846 | 2000 | -154 | 92 | 1285 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1832 | 2000 | -168 | 92 | 1277 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1832 | 2000 | -168 | 92 | -1248 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1823 | 2000 | -177 | 91 | 1283 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1075 | 1248 | -173 | 86 | 439 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1075 | 1248 | -173 | 86 | 439 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1072 | 1248 | -176 | 86 | 438 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1072 | 1248 | -176 | 86 | 438 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1068 | 1248 | -180 | 86 | 436 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1068 | 1248 | -180 | 86 | 436 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1689 | 2000 | -311 | 84 | 1166 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1679 | 2000 | -321 | 84 | 1160 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1836 | -432 | 76 | 1001 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1836 | -432 | 76 | 1001 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1370 | 1836 | -466 | 75 | 977 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1370 | 1836 | -466 | 75 | 977 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 926 | 1248 | -322 | 74 | 378 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 926 | 1248 | -322 | 74 | 378 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 920 | 1248 | -328 | 74 | 376 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1333 | 1836 | -503 | 73 | 949 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1333 | 1836 | -503 | 73 | 949 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1331 | 1836 | -505 | 72 | 948 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1326 | 1836 | -510 | 72 | 945 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1322 | 1836 | -514 | 72 | 942 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1320 | 1836 | -516 | 72 | 940 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1317 | 1836 | -519 | 72 | 939 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1312 | 1836 | -524 | 71 | 935 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1310 | 1836 | -526 | 71 | 933 | AC

## 0230
Detailed results
Generated at: | 13/04/2026 22:13:45
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3734
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Medgidia Sud - Rahman/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1912 | 2000 | -88 | 96 | 1337 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1911 | 2000 | -89 | 96 | 1342 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1910 | 2000 | -90 | 96 | 1341 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1901 | 2000 | -99 | 95 | 1341 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1897 | 2000 | -103 | 95 | 1328 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1894 | 2000 | -106 | 95 | 1329 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1889 | 2000 | -111 | 94 | 1326 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1883 | 2000 | -117 | 94 | 1324 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1879 | 2000 | -121 | 94 | 1319 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1878 | 2000 | -122 | 94 | 1318 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1874 | 2000 | -126 | 94 | 1315 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1869 | 2000 | -131 | 93 | 1311 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1853 | 2000 | -147 | 93 | 1300 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1842 | 2000 | -158 | 92 | -1257 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1842 | 2000 | -158 | 92 | 1283 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1829 | 2000 | -171 | 91 | 1275 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1829 | 2000 | -171 | 91 | -1245 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1824 | 2000 | -176 | 91 | 1283 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1079 | 1248 | -169 | 86 | 440 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1079 | 1248 | -169 | 86 | 440 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1076 | 1248 | -172 | 86 | 439 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1076 | 1248 | -172 | 86 | 439 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1072 | 1248 | -176 | 86 | 437 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1072 | 1248 | -176 | 86 | 437 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1686 | 2000 | -314 | 84 | 1163 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1676 | 2000 | -324 | 84 | 1158 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1836 | -448 | 76 | 994 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1836 | -448 | 76 | 994 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1380 | 1836 | -456 | 75 | 988 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 927 | 1248 | -321 | 74 | 378 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 927 | 1248 | -321 | 74 | 378 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 921 | 1248 | -327 | 74 | 375 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1353 | 1836 | -483 | 74 | 968 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1353 | 1836 | -483 | 74 | 968 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1315 | 1836 | -521 | 72 | 941 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1315 | 1836 | -521 | 72 | 941 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1308 | 1836 | -528 | 71 | 936 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1306 | 1836 | -530 | 71 | 934 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1305 | 1836 | -531 | 71 | 934 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1302 | 1836 | -534 | 71 | 932 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1299 | 1836 | -537 | 71 | 930 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1295 | 1836 | -541 | 71 | 927 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1294 | 1836 | -542 | 70 | 926 | AC

## 0330
Detailed results
Generated at: | 13/04/2026 22:13:45
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3721
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Medgidia Sud - Rahman/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1896 | 2000 | -104 | 95 | 1324 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1891 | 2000 | -109 | 95 | 1326 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1889 | 2000 | -111 | 94 | 1325 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1884 | 2000 | -116 | 94 | 1329 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1882 | 2000 | -118 | 94 | 1316 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1874 | 2000 | -126 | 94 | 1314 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1870 | 2000 | -130 | 93 | 1311 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1867 | 2000 | -133 | 93 | 1312 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1859 | 2000 | -141 | 93 | 1304 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1859 | 2000 | -141 | 93 | 1303 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1853 | 2000 | -147 | 93 | 1300 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1848 | 2000 | -152 | 92 | 1296 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1839 | 2000 | -161 | 92 | 1289 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1835 | 2000 | -165 | 92 | 1276 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1835 | 2000 | -165 | 92 | -1251 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1821 | 2000 | -179 | 91 | -1240 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1821 | 2000 | -179 | 91 | 1269 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1814 | 2000 | -186 | 91 | 1276 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1090 | 1248 | -159 | 87 | 444 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1090 | 1248 | -159 | 87 | 444 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1087 | 1248 | -162 | 87 | 443 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1087 | 1248 | -162 | 87 | 443 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1083 | 1248 | -166 | 87 | 441 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1083 | 1248 | -166 | 87 | 441 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1667 | 2000 | -333 | 83 | 1149 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1657 | 2000 | -343 | 83 | 1143 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1387 | 1836 | -449 | 76 | 994 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1387 | 1836 | -449 | 76 | 994 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1373 | 1836 | -463 | 75 | 984 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 929 | 1248 | -320 | 74 | 377 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 929 | 1248 | -320 | 74 | 377 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 533 | 721 | -188 | 74 | 375 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1347 | 1836 | -489 | 73 | 964 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1347 | 1836 | -489 | 73 | 964 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1309 | 1836 | -527 | 71 | 938 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1308 | 1836 | -528 | 71 | 938 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1301 | 1836 | -535 | 71 | 933 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1299 | 1836 | -537 | 71 | 931 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1298 | 1836 | -538 | 71 | 931 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1296 | 1836 | -540 | 71 | 929 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1292 | 1836 | -544 | 70 | 926 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1290 | 1836 | -546 | 70 | 924 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1289 | 1836 | -547 | 70 | 924 | AC

## 0430
Detailed results
Generated at: | 13/04/2026 22:13:45
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3712
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Medgidia Sud - Rahman/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1881 | 2000 | -119 | 94 | 1316 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1873 | 2000 | -127 | 94 | 1315 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1870 | 2000 | -130 | 93 | 1320 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1869 | 2000 | -131 | 93 | 1309 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1869 | 2000 | -131 | 93 | 1312 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1855 | 2000 | -145 | 93 | 1302 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1854 | 2000 | -146 | 93 | 1305 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1852 | 2000 | -148 | 93 | 1300 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1842 | 2000 | -158 | 92 | 1294 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1841 | 2000 | -159 | 92 | 1293 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1836 | 2000 | -164 | 92 | 1289 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1831 | 2000 | -169 | 92 | 1285 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1828 | 2000 | -172 | 91 | -1249 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1828 | 2000 | -172 | 91 | 1275 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1828 | 2000 | -172 | 91 | 1283 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1815 | 2000 | -185 | 91 | 1267 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1815 | 2000 | -185 | 91 | -1238 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1805 | 2000 | -195 | 90 | 1272 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1091 | 1248 | -158 | 87 | 444 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1091 | 1248 | -158 | 87 | 444 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1088 | 1248 | -161 | 87 | 443 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1088 | 1248 | -161 | 87 | 443 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1084 | 1248 | -165 | 87 | 442 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1084 | 1248 | -165 | 87 | 442 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1650 | 2000 | -350 | 83 | 1139 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1640 | 2000 | -360 | 82 | 1134 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1385 | 1836 | -451 | 75 | 993 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1385 | 1836 | -451 | 75 | 993 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1371 | 1836 | -465 | 75 | 983 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 929 | 1248 | -320 | 74 | 377 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 929 | 1248 | -320 | 74 | 377 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 533 | 721 | -188 | 74 | 375 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1344 | 1836 | -492 | 73 | 962 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1344 | 1836 | -492 | 73 | 962 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1306 | 1836 | -530 | 71 | 937 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1306 | 1836 | -530 | 71 | 937 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1296 | 1836 | -540 | 71 | 929 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1295 | 1836 | -541 | 71 | 929 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1293 | 1836 | -543 | 70 | 927 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1290 | 1836 | -546 | 70 | 925 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1288 | 1836 | -548 | 70 | 923 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1288 | 1836 | -548 | 70 | 923 | AC

## 0530
Detailed results
Generated at: | 13/04/2026 22:13:45
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3711
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Medgidia Sud - Rahman/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1937 | 2000 | -63 | 97 | 1350 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1927 | 2000 | -73 | 96 | 1345 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1925 | 2000 | -75 | 96 | 1355 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1923 | 2000 | -77 | 96 | 1345 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1917 | 2000 | -83 | 96 | 1341 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1912 | 2000 | -88 | 96 | 1341 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1907 | 2000 | -93 | 95 | 1334 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1906 | 2000 | -94 | 95 | 1333 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1894 | 2000 | -106 | 95 | 1325 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1887 | 2000 | -113 | 94 | 1320 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1887 | 2000 | -113 | 94 | -1284 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1887 | 2000 | -113 | 94 | 1311 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1885 | 2000 | -115 | 94 | 1319 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1877 | 2000 | -123 | 94 | 1313 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1873 | 2000 | -127 | 94 | -1273 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1873 | 2000 | -127 | 94 | 1304 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1870 | 2000 | -130 | 94 | 1309 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1861 | 2000 | -139 | 93 | 1308 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1096 | 1248 | -153 | 88 | 446 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1096 | 1248 | -153 | 88 | 446 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1093 | 1248 | -156 | 88 | 445 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1093 | 1248 | -156 | 88 | 445 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1089 | 1248 | -160 | 87 | 444 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1089 | 1248 | -160 | 87 | 444 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1694 | 2000 | -306 | 85 | 1166 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1685 | 2000 | -315 | 84 | 1161 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 927 | 1248 | -322 | 74 | 377 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 927 | 1248 | -322 | 74 | 377 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1356 | 1836 | -480 | 74 | 972 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1356 | 1836 | -480 | 74 | 972 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 532 | 721 | -189 | 74 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1340 | 1836 | -496 | 73 | 960 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1313 | 1836 | -523 | 72 | 940 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1313 | 1836 | -523 | 72 | 940 | AC

## 0630
Detailed results
Generated at: | 13/04/2026 22:13:45
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3993
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1995 | 2000 | -5 | 100 | 1378 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1993 | 2000 | -7 | 100 | 1377 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1990 | 2000 | -10 | 100 | 1377 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1990 | 2000 | -10 | 100 | 1377 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1990 | 2000 | -10 | 100 | 1374 | AC
Base case | Base case | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1988 | 2000 | -12 | 99 | 1375 | AC
Base case | Base case | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1988 | 2000 | -12 | 99 | -1341 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1987 | 2000 | -13 | 99 | 1371 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1986 | 2000 | -14 | 99 | 1372 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1968 | 2000 | -32 | 98 | 1359 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1965 | 2000 | -35 | 98 | 1357 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1952 | 2000 | -48 | 98 | 1349 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1952 | 2000 | -48 | 98 | 1348 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1950 | 2000 | -50 | 97 | 1349 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1950 | 2000 | -50 | 97 | 1349 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1950 | 2000 | -50 | 97 | 1349 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1948 | 2000 | -52 | 97 | 1335 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1948 | 2000 | -52 | 97 | 1346 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1943 | 2000 | -57 | 97 | 1343 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1931 | 2000 | -69 | 97 | 1328 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1929 | 2000 | -71 | 96 | 1339 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1922 | 2000 | -78 | 96 | 1328 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1919 | 2000 | -81 | 96 | 1328 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1805 | 2000 | -195 | 90 | 1241 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1557 | 1836 | -279 | 85 | 1112 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1557 | 1836 | -279 | 85 | 1112 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1534 | 1836 | -302 | 84 | 1095 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1534 | 1836 | -302 | 84 | 1095 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1521 | 1836 | -315 | 83 | 1087 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1502 | 1836 | -334 | 82 | 1073 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1497 | 1836 | -339 | 82 | 1069 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1486 | 1836 | -350 | 81 | 1063 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1472 | 1836 | -364 | 80 | 1052 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 801 | 999 | -199 | 80 | 298 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1462 | 1836 | -374 | 80 | 1045 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1462 | 1836 | -374 | 80 | 1045 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1457 | 1836 | -379 | 79 | 1041 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1442 | 1836 | -394 | 79 | 1031 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 747 | 999 | -252 | 75 | 291 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1395 | 1890 | -495 | 74 | -968 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1395 | 1890 | -495 | 74 | -968 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1395 | 1920 | -525 | 73 | 990 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1395 | 1920 | -525 | 73 | 990 | AC

## 0730
Detailed results
Generated at: | 13/04/2026 22:13:45
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2646.65
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT3 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1251 | 1248 | 3 | 100 | 511 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1248 | 1248 | 0 | 100 | 510 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1220 | 1248 | -28 | 98 | 499 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 977 | 1248 | -272 | 78 | 399 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 970 | 1248 | -278 | 78 | 396 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1544 | 2000 | -456 | 77 | 1080 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1399 | 1836 | -437 | 76 | 997 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 935 | 1248 | -313 | 75 | 382 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 929 | 1248 | -319 | 74 | 379 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1478 | 2000 | -522 | 74 | 1034 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1470 | 2000 | -530 | 73 | 1027 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1466 | 2000 | -534 | 73 | 1024 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 912 | 1248 | -336 | 73 | 372 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1457 | 2000 | -543 | 73 | 1019 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1449 | 2000 | -551 | 72 | 1013 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1325 | 1836 | -511 | 72 | 943 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1442 | 2000 | -558 | 72 | 1008 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1438 | 2000 | -562 | 72 | 1002 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 895 | 1248 | -354 | 72 | 365 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1432 | 2000 | -568 | 72 | 1001 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 889 | 1248 | -360 | 71 | 363 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1303 | 1836 | -533 | 71 | 928 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1303 | 1836 | -533 | 71 | 928 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1295 | 1836 | -541 | 71 | 922 | AC

## 0830
Detailed results
Generated at: | 13/04/2026 22:13:45
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2643.08
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT3 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1254 | 1248 | 5 | 100 | 511 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1251 | 1248 | 2 | 100 | 510 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1238 | 1248 | -10 | 99 | 506 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1577 | 1836 | -259 | 86 | 1118 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1568 | 1836 | -268 | 85 | 1115 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 835 | 999 | -164 | 84 | 331 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1008 | 1248 | -240 | 81 | 410 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 579 | 721 | -142 | 80 | 407 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1459 | 1836 | -377 | 79 | 1036 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1459 | 1836 | -377 | 79 | 1036 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1457 | 1836 | -379 | 79 | 1032 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1574 | 2000 | -426 | 79 | 1102 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1427 | 1836 | -409 | 78 | 1014 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1422 | 1836 | -414 | 77 | 1009 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 963 | 1248 | -285 | 77 | 392 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1412 | 1836 | -424 | 77 | 1003 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1403 | 1836 | -433 | 76 | 996 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 954 | 1248 | -295 | 76 | 387 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1399 | 1836 | -437 | 76 | 992 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1399 | 1836 | -437 | 76 | 992 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1398 | 1836 | -438 | 76 | 992 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 547 | 721 | -174 | 76 | 384 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1497 | 2000 | -503 | 75 | 1048 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1372 | 1836 | -464 | 75 | 974 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1492 | 2000 | -508 | 75 | 1042 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1487 | 2000 | -513 | 74 | 1039 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 916 | 1248 | -333 | 73 | 371 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1462 | 2000 | -538 | 73 | 1023 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1458 | 2000 | -542 | 73 | 1020 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 526 | 721 | -195 | 73 | 369 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1455 | 2000 | -545 | 73 | 1018 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1453 | 2000 | -547 | 73 | 1013 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1451 | 2000 | -549 | 73 | 1013 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 RRESI22 1 | 691 | 970 | -279 | 71 | 282 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 RRESI12 1 | 691 | 970 | -279 | 71 | 282 | AC

## 0930
Detailed results
Generated at: | 13/04/2026 22:13:45
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2352.98
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT3 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1253 | 1248 | 5 | 100 | 511 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1250 | 1248 | 2 | 100 | 510 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1202 | 1248 | -46 | 96 | 491 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1560 | 1836 | -276 | 85 | 1107 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1516 | 1836 | -320 | 83 | 1078 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1000 | 1248 | -248 | 80 | 406 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 574 | 721 | -147 | 80 | 404 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1414 | 1836 | -422 | 77 | 1004 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1414 | 1836 | -422 | 77 | 1004 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 951 | 1248 | -297 | 76 | 387 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1836 | -444 | 76 | 987 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 938 | 1248 | -311 | 75 | 380 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1375 | 1836 | -461 | 75 | 977 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 538 | 721 | -183 | 75 | 378 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1836 | -468 | 74 | 971 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1836 | -474 | 74 | 967 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1354 | 1836 | -482 | 74 | 962 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1836 | -484 | 74 | 960 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 912 | 1248 | -336 | 73 | 370 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1339 | 1836 | -497 | 73 | 950 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1339 | 1836 | -497 | 73 | 950 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 726 | 999 | -273 | 73 | 289 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 524 | 721 | -197 | 73 | 367 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1327 | 1836 | -509 | 72 | 942 | AC

## 1030
Detailed results
Generated at: | 13/04/2026 22:13:45
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2494.74
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT3 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1255 | 1248 | 6 | 101 | 512 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1252 | 1248 | 3 | 100 | 510 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1223 | 1248 | -26 | 98 | 500 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1670 | 1836 | -166 | 91 | 1183 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1607 | 1836 | -229 | 88 | 1143 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1836 | -331 | 82 | 1068 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1836 | -331 | 82 | 1068 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1012 | 1248 | -237 | 81 | 411 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1479 | 1836 | -357 | 81 | 1048 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 581 | 721 | -140 | 81 | 408 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1003 | 1248 | -245 | 80 | 409 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 797 | 999 | -202 | 80 | 316 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1457 | 1836 | -379 | 79 | 1035 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1455 | 1836 | -381 | 79 | 1032 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1447 | 1836 | -389 | 79 | 1027 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1836 | -397 | 78 | 1021 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1836 | -397 | 78 | 1021 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 967 | 1248 | -281 | 77 | 392 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1422 | 1836 | -414 | 77 | 1008 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1422 | 1836 | -414 | 77 | 1008 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 555 | 721 | -166 | 77 | 390 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1409 | 1836 | -427 | 77 | 1000 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 RRESI12 1 | 704 | 970 | -266 | 73 | 287 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 RRESI22 1 | 704 | 970 | -266 | 73 | 287 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 903 | 1248 | -345 | 72 | 366 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 518 | 721 | -203 | 72 | 363 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1422 | 2000 | -578 | 71 | 995 | AC

## 1130
Detailed results
Generated at: | 13/04/2026 22:13:45
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2547.37
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Portile de Fier-Djerdap/[RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1245 | 1248 | -4 | 100 | 508 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1241 | 1248 | -7 | 99 | 506 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1238 | 1248 | -10 | 99 | 505 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1696 | 1836 | -140 | 92 | 1200 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 902 | 999 | -97 | 90 | 357 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1644 | 1836 | -192 | 90 | 1168 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1534 | 1836 | -302 | 84 | 1088 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1534 | 1836 | -302 | 84 | 1088 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1043 | 1248 | -206 | 84 | 425 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1516 | 1836 | -320 | 83 | 1072 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1015 | 1248 | -233 | 81 | 412 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1488 | 1836 | -348 | 81 | 1056 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1836 | -351 | 81 | 1053 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 583 | 721 | -138 | 81 | 410 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1479 | 1836 | -357 | 81 | 1049 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1468 | 1836 | -368 | 80 | 1041 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1468 | 1836 | -368 | 80 | 1041 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1836 | -388 | 79 | 1026 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1836 | -388 | 79 | 1026 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1435 | 1836 | -401 | 78 | 1018 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 971 | 1248 | -278 | 78 | 394 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 557 | 721 | -164 | 77 | 391 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 RRESI22 1 | 731 | 970 | -239 | 75 | 298 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 RRESI12 1 | 731 | 970 | -239 | 75 | 298 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1487 | 2000 | -513 | 74 | 1041 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [DIR] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1152 | 1600 | -448 | 72 | 791 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 897 | 1248 | -352 | 72 | 363 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 515 | 721 | -206 | 71 | 361 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1408 | 2000 | -592 | 70 | 985 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1400 | 2000 | -600 | 70 | 980 | AC

## 1230
Detailed results
Generated at: | 13/04/2026 22:13:46
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2695.61
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT3 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1256 | 1248 | 7 | 101 | 513 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1253 | 1248 | 4 | 100 | 511 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1235 | 1248 | -14 | 99 | 504 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1653 | 1836 | -183 | 90 | 1172 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1612 | 1836 | -224 | 88 | 1146 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 833 | 999 | -167 | 83 | 330 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1512 | 1836 | -324 | 82 | 1074 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1512 | 1836 | -324 | 82 | 1074 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1489 | 1836 | -347 | 81 | 1056 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1007 | 1248 | -241 | 81 | 410 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1005 | 1248 | -244 | 80 | 410 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1001 | 1248 | -248 | 80 | 407 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1463 | 1836 | -373 | 80 | 1040 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1461 | 1836 | -375 | 80 | 1037 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1456 | 1836 | -380 | 79 | 1034 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1447 | 1836 | -389 | 79 | 1028 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1446 | 1836 | -390 | 79 | 1027 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1436 | 1836 | -400 | 78 | 1020 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1436 | 1836 | -400 | 78 | 1020 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 968 | 1248 | -280 | 78 | 394 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1416 | 1836 | -420 | 77 | 1006 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 556 | 721 | -165 | 77 | 391 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1512 | 2000 | -488 | 76 | 1059 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 904 | 1248 | -344 | 72 | 367 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1442 | 2000 | -558 | 72 | 1009 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 RRESI22 1 | 699 | 970 | -271 | 72 | 285 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 RRESI12 1 | 699 | 970 | -271 | 72 | 285 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 519 | 721 | -202 | 72 | 365 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1432 | 2000 | -568 | 72 | 1001 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1429 | 2000 | -571 | 71 | 1000 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1427 | 2000 | -573 | 71 | 999 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1424 | 2000 | -576 | 71 | 996 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1420 | 2000 | -580 | 71 | 993 | AC

## 1330
Detailed results
Generated at: | 13/04/2026 22:13:46
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2555.86
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT3 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1255 | 1248 | 7 | 101 | 513 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1252 | 1248 | 4 | 100 | 512 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1228 | 1248 | -20 | 98 | 502 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1561 | 1836 | -275 | 85 | 1109 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1538 | 1836 | -298 | 84 | 1095 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1004 | 1248 | -245 | 80 | 409 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 997 | 1248 | -251 | 80 | 407 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1433 | 1836 | -403 | 78 | 1019 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1433 | 1836 | -403 | 78 | 1019 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 970 | 1248 | -278 | 78 | 396 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1410 | 1836 | -426 | 77 | 1002 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1391 | 1836 | -445 | 76 | 990 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 942 | 1248 | -307 | 75 | 384 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1384 | 1836 | -452 | 75 | 984 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1379 | 1836 | -457 | 75 | 981 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 936 | 1248 | -313 | 75 | 381 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1372 | 1836 | -464 | 75 | 976 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1371 | 1836 | -465 | 75 | 975 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 430 | 577 | -147 | 75 | 295 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1363 | 1836 | -473 | 74 | 969 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1363 | 1836 | -473 | 74 | 969 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 915 | 1248 | -333 | 73 | 373 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1344 | 1836 | -492 | 73 | 956 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1461 | 2000 | -539 | 73 | 1024 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 909 | 1248 | -339 | 73 | 370 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c1 | RPDF212 RRESI12 1 | 681 | 970 | -289 | 70 | 278 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [DIR] OHL 220 kV Portile de Fier-Resita c2 | RPDF222 RRESI22 1 | 681 | 970 | -289 | 70 | 278 | AC

## 1430
Detailed results
Generated at: | 13/04/2026 22:13:46
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2279.53
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT3 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1253 | 1248 | 4 | 100 | 512 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1250 | 1248 | 1 | 100 | 511 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1205 | 1248 | -43 | 97 | 493 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 986 | 1248 | -262 | 79 | 402 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 980 | 1248 | -269 | 78 | 399 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1434 | 1836 | -402 | 78 | 1021 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1836 | -418 | 77 | 1010 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 928 | 1248 | -320 | 74 | 378 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 923 | 1248 | -326 | 74 | 376 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 908 | 1248 | -340 | 73 | 370 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 903 | 1248 | -345 | 72 | 368 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 897 | 1248 | -351 | 72 | 366 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1318 | 1836 | -518 | 72 | 939 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1318 | 1836 | -518 | 72 | 939 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1301 | 1836 | -535 | 71 | 926 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1289 | 1836 | -547 | 70 | 919 | AC

## 1530
Detailed results
Generated at: | 13/04/2026 22:13:46
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2089.43
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT3 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1252 | 1248 | 4 | 100 | 512 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1249 | 1248 | 1 | 100 | 510 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1172 | 1248 | -77 | 94 | 478 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 968 | 1248 | -281 | 78 | 395 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 962 | 1248 | -287 | 77 | 392 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 946 | 1248 | -302 | 76 | 386 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 940 | 1248 | -308 | 75 | 383 | AC

## 1630
Detailed results
Generated at: | 13/04/2026 22:13:46
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3864
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1995 | 2000 | -5 | 100 | 1381 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1990 | 2000 | -10 | 100 | 1378 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1966 | 2000 | -34 | 98 | 1360 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1961 | 2000 | -39 | 98 | 1357 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1959 | 2000 | -41 | 98 | 1357 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1951 | 2000 | -49 | 98 | 1351 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1946 | 2000 | -54 | 97 | 1346 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1941 | 2000 | -59 | 97 | 1344 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1941 | 2000 | -59 | 97 | 1345 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1938 | 2000 | -62 | 97 | 1341 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1932 | 2000 | -68 | 97 | 1341 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1932 | 2000 | -68 | 97 | 1341 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1932 | 2000 | -68 | 97 | 1336 | AC
Base case | Base case | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1929 | 2000 | -71 | 96 | 1339 | AC
Base case | Base case | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1929 | 2000 | -71 | 96 | -1306 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1928 | 2000 | -72 | 96 | 1325 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1909 | 2000 | -91 | 95 | 1329 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1904 | 2000 | -96 | 95 | 1312 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1900 | 2000 | -100 | 95 | 1318 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1900 | 2000 | -100 | 95 | 1318 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1900 | 2000 | -100 | 95 | 1318 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1891 | 2000 | -109 | 95 | 1311 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1889 | 2000 | -111 | 94 | 1306 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1764 | 2000 | -236 | 88 | 1213 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 832 | 999 | -167 | 83 | 318 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1836 | -331 | 82 | 1074 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1836 | -331 | 82 | 1074 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1503 | 1836 | -333 | 82 | 1072 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1503 | 1836 | -333 | 82 | 1072 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1836 | -342 | 81 | 1067 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1475 | 1836 | -361 | 80 | 1052 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1471 | 1836 | -365 | 80 | 1051 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1449 | 1836 | -387 | 79 | 1036 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1836 | -397 | 78 | 1028 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1836 | -410 | 78 | 1019 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1424 | 1836 | -412 | 78 | 1017 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1419 | 1836 | -417 | 77 | 1014 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1836 | -432 | 76 | 1003 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 748 | 999 | -251 | 75 | 292 | AC

## 1730
Detailed results
Generated at: | 13/04/2026 22:13:46
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3194
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1987 | 2000 | -13 | 99 | 1397 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1965 | 2000 | -35 | 98 | 1381 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1944 | 2000 | -56 | 97 | 1366 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1935 | 2000 | -65 | 97 | 1359 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1917 | 2000 | -83 | 96 | 1347 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1906 | 2000 | -94 | 95 | 1339 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1895 | 2000 | -105 | 95 | 1326 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1892 | 2000 | -108 | 95 | 1329 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1885 | 2000 | -115 | 94 | 1325 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1881 | 2000 | -119 | 94 | 1329 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1881 | 2000 | -119 | 94 | 1321 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1872 | 2000 | -128 | 94 | 1312 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1861 | 2000 | -139 | 93 | 1310 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1661 | 1836 | -175 | 90 | 1177 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1656 | 1836 | -180 | 90 | 1173 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1767 | 2000 | -233 | 88 | 1244 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1758 | 2000 | -242 | 88 | 1221 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1751 | 2000 | -249 | 88 | 1217 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1068 | 1248 | -181 | 86 | 436 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1068 | 1248 | -181 | 86 | 436 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1065 | 1248 | -184 | 85 | 435 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1065 | 1248 | -184 | 85 | 435 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1061 | 1248 | -187 | 85 | 434 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1061 | 1248 | -187 | 85 | 434 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1606 | 2000 | -394 | 80 | -1101 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1606 | 2000 | -394 | 80 | 1121 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1595 | 2000 | -405 | 80 | -1093 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1595 | 2000 | -405 | 80 | 1115 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1423 | 1836 | -413 | 77 | 1003 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1406 | 1836 | -430 | 77 | 991 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1384 | 1836 | -452 | 75 | 974 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1836 | -454 | 75 | 972 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1359 | 1836 | -477 | 74 | 956 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1357 | 1836 | -479 | 74 | 954 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1350 | 1836 | -486 | 74 | 949 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1345 | 1836 | -491 | 73 | 945 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 914 | 1248 | -334 | 73 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 914 | 1248 | -334 | 73 | 374 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1339 | 1836 | -497 | 73 | 941 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 908 | 1248 | -340 | 73 | 371 | AC

## 1830
Detailed results
Generated at: | 13/04/2026 22:13:46
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2798
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1987 | 2000 | -13 | 99 | 1396 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1963 | 2000 | -37 | 98 | 1379 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1932 | 2000 | -68 | 97 | 1356 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1910 | 2000 | -90 | 96 | 1341 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1896 | 2000 | -104 | 95 | 1331 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1878 | 2000 | -122 | 94 | 1319 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1873 | 2000 | -127 | 94 | 1315 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1869 | 2000 | -131 | 93 | 1312 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1861 | 2000 | -139 | 93 | 1306 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1838 | 2000 | -162 | 92 | 1285 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1820 | 2000 | -180 | 91 | 1286 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1806 | 2000 | -194 | 90 | 1264 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1796 | 2000 | -204 | 90 | 1263 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1755 | 2000 | -245 | 88 | 1218 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1749 | 2000 | -251 | 87 | 1215 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1668 | 2000 | -332 | 83 | 1174 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1028 | 1248 | -221 | 82 | 419 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1028 | 1248 | -221 | 82 | 419 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1025 | 1248 | -223 | 82 | 418 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1025 | 1248 | -223 | 82 | 418 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1021 | 1248 | -227 | 82 | 417 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1021 | 1248 | -227 | 82 | 417 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1468 | 1836 | -368 | 80 | 1049 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1437 | 1836 | -399 | 78 | 1027 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 921 | 1248 | -328 | 74 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 921 | 1248 | -328 | 74 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 915 | 1248 | -334 | 73 | 373 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1434 | 2000 | -566 | 72 | 1001 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1434 | 2000 | -566 | 72 | -985 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1425 | 2000 | -575 | 71 | 996 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1425 | 2000 | -575 | 71 | -978 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1288 | 1836 | -548 | 70 | 921 | AC

## 1930
Detailed results
Generated at: | 13/04/2026 22:13:46
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2993
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1982 | 2000 | -18 | 99 | 1393 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1975 | 2000 | -25 | 99 | 1389 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1937 | 2000 | -63 | 97 | 1361 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1921 | 2000 | -79 | 96 | 1350 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1902 | 2000 | -98 | 95 | 1337 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1897 | 2000 | -103 | 95 | 1333 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1893 | 2000 | -107 | 95 | 1330 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1890 | 2000 | -110 | 95 | 1328 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1843 | 2000 | -157 | 92 | 1294 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1837 | 2000 | -163 | 92 | 1286 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1820 | 2000 | -180 | 91 | 1288 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1661 | 1836 | -175 | 90 | 1186 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1801 | 2000 | -199 | 90 | 1263 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1792 | 2000 | -208 | 90 | 1261 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1763 | 2000 | -237 | 88 | 1224 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1757 | 2000 | -243 | 88 | 1221 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1595 | 1836 | -241 | 87 | 1138 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1644 | 2000 | -356 | 82 | 1159 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1016 | 1248 | -233 | 81 | 415 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1016 | 1248 | -233 | 81 | 415 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1013 | 1248 | -235 | 81 | 414 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1013 | 1248 | -235 | 81 | 414 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1009 | 1248 | -239 | 81 | 412 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1009 | 1248 | -239 | 81 | 412 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1431 | 1836 | -405 | 78 | 1022 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1429 | 1836 | -407 | 78 | 1020 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1397 | 1836 | -439 | 76 | 997 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1836 | -454 | 75 | 986 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1377 | 1836 | -459 | 75 | 983 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1366 | 1836 | -470 | 74 | 975 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1354 | 1836 | -482 | 74 | 966 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 918 | 1248 | -330 | 74 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 918 | 1248 | -330 | 74 | 375 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1346 | 1836 | -490 | 73 | 961 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1345 | 1836 | -491 | 73 | 960 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 913 | 1248 | -336 | 73 | 372 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1330 | 1836 | -506 | 72 | 949 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1424 | 2000 | -576 | 71 | 997 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1424 | 2000 | -576 | 71 | -982 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1415 | 2000 | -585 | 71 | -975 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1415 | 2000 | -585 | 71 | 992 | AC

## 2030
Detailed results
Generated at: | 13/04/2026 22:13:46
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3061
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1988 | 2000 | -12 | 99 | 1399 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1983 | 2000 | -17 | 99 | 1396 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1943 | 2000 | -57 | 97 | 1367 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1928 | 2000 | -72 | 96 | 1357 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1909 | 2000 | -91 | 95 | 1344 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1904 | 2000 | -96 | 95 | 1339 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1747 | 1836 | -89 | 95 | 1247 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1901 | 2000 | -99 | 95 | 1337 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1899 | 2000 | -101 | 95 | 1336 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1850 | 2000 | -150 | 93 | 1301 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1843 | 2000 | -157 | 92 | 1293 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1827 | 2000 | -173 | 91 | 1294 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1808 | 2000 | -192 | 90 | 1270 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1800 | 2000 | -200 | 90 | 1268 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1651 | 1836 | -185 | 90 | 1178 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1770 | 2000 | -230 | 89 | 1231 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1764 | 2000 | -236 | 88 | 1227 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1649 | 2000 | -351 | 82 | 1165 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1491 | 1836 | -345 | 81 | 1064 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1014 | 1248 | -234 | 81 | 414 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1014 | 1248 | -234 | 81 | 414 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1488 | 1836 | -348 | 81 | 1062 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1011 | 1248 | -237 | 81 | 413 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1011 | 1248 | -237 | 81 | 413 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1008 | 1248 | -241 | 81 | 411 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1008 | 1248 | -241 | 81 | 411 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1457 | 1836 | -379 | 79 | 1040 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1444 | 1836 | -392 | 79 | 1031 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1434 | 1836 | -402 | 78 | 1024 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1428 | 1836 | -408 | 78 | 1020 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1420 | 1836 | -416 | 77 | 1014 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1417 | 1836 | -419 | 77 | 1011 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1405 | 1836 | -431 | 77 | 1003 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1836 | -448 | 76 | 991 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 920 | 1248 | -329 | 74 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 920 | 1248 | -329 | 74 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 914 | 1248 | -334 | 73 | 373 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1423 | 2000 | -577 | 71 | -983 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1423 | 2000 | -577 | 71 | 998 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1415 | 2000 | -585 | 71 | 993 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1415 | 2000 | -585 | 71 | -976 | AC

## 2130
Detailed results
Generated at: | 13/04/2026 22:13:46
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 2951
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1977 | 2000 | -23 | 99 | 1393 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1966 | 2000 | -34 | 98 | 1386 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1930 | 2000 | -70 | 96 | 1360 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1915 | 2000 | -85 | 96 | 1349 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1896 | 2000 | -104 | 95 | 1336 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1888 | 2000 | -112 | 94 | 1330 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1884 | 2000 | -116 | 94 | 1328 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1882 | 2000 | -118 | 94 | 1326 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1847 | 2000 | -153 | 92 | 1300 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1831 | 2000 | -169 | 92 | 1286 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1816 | 2000 | -184 | 91 | 1287 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1798 | 2000 | -202 | 90 | 1264 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1790 | 2000 | -210 | 90 | 1263 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1634 | 1836 | -202 | 89 | 1163 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1759 | 2000 | -241 | 88 | 1224 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1753 | 2000 | -247 | 88 | 1221 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1572 | 1836 | -264 | 86 | 1119 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1644 | 2000 | -356 | 82 | 1162 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1022 | 1248 | -227 | 82 | 417 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1022 | 1248 | -227 | 82 | 417 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1019 | 1248 | -230 | 82 | 416 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1019 | 1248 | -230 | 82 | 416 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1015 | 1248 | -233 | 81 | 415 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1015 | 1248 | -233 | 81 | 415 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1413 | 1836 | -423 | 77 | 1005 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1411 | 1836 | -425 | 77 | 1004 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1375 | 1836 | -461 | 75 | 977 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1364 | 1836 | -472 | 74 | 969 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1364 | 1836 | -472 | 74 | 970 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 921 | 1248 | -328 | 74 | 376 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 921 | 1248 | -328 | 74 | 376 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1351 | 1836 | -485 | 74 | 959 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 915 | 1248 | -333 | 73 | 374 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1339 | 1836 | -497 | 73 | 951 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1332 | 1836 | -504 | 73 | 946 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1328 | 1836 | -508 | 72 | 943 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1316 | 1836 | -520 | 72 | 935 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1413 | 2000 | -587 | 71 | -977 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1413 | 2000 | -587 | 71 | 992 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1405 | 2000 | -595 | 70 | -970 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1405 | 2000 | -595 | 70 | 987 | AC

## 2230
Detailed results
Generated at: | 13/04/2026 22:13:47
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3457
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1976 | 2000 | -24 | 99 | 1389 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1968 | 2000 | -32 | 98 | 1383 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1947 | 2000 | -53 | 97 | 1368 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1940 | 2000 | -60 | 97 | 1363 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1925 | 2000 | -75 | 96 | 1347 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1924 | 2000 | -76 | 96 | 1352 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1924 | 2000 | -76 | 96 | 1352 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1765 | 1836 | -71 | 96 | 1257 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1918 | 2000 | -82 | 96 | 1348 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1914 | 2000 | -86 | 96 | 1345 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1912 | 2000 | -88 | 96 | 1351 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1899 | 2000 | -101 | 95 | 1330 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1885 | 2000 | -115 | 94 | 1327 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1728 | 1836 | -108 | 94 | 1231 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1875 | 2000 | -125 | 94 | 1316 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1782 | 2000 | -218 | 89 | 1254 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1751 | 2000 | -249 | 88 | 1212 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1742 | 2000 | -258 | 87 | 1216 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1742 | 2000 | -258 | 87 | -1193 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1742 | 2000 | -258 | 87 | 1207 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1729 | 2000 | -271 | 86 | -1182 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1729 | 2000 | -271 | 86 | 1208 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1061 | 1248 | -188 | 85 | 434 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1061 | 1248 | -188 | 85 | 434 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1058 | 1248 | -190 | 85 | 432 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1058 | 1248 | -190 | 85 | 432 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1054 | 1248 | -194 | 84 | 431 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1054 | 1248 | -194 | 84 | 431 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1504 | 1836 | -332 | 82 | 1070 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1470 | 1836 | -366 | 80 | 1046 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1458 | 1836 | -378 | 79 | 1038 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1453 | 1836 | -383 | 79 | 1033 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1447 | 1836 | -389 | 79 | 1029 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1446 | 1836 | -390 | 79 | 1028 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1836 | -393 | 79 | 1026 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1427 | 1836 | -409 | 78 | 1015 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1421 | 1836 | -415 | 77 | 1010 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1419 | 1836 | -417 | 77 | 1009 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 921 | 1248 | -327 | 74 | 376 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 921 | 1248 | -327 | 74 | 376 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 915 | 1248 | -333 | 73 | 374 | AC

## 2330
Detailed results
Generated at: | 13/04/2026 22:13:47
Business day: | 2026-04-15
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3555
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Isaccea - Tulcea Vest/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1829 | 1836 | -7 | 100 | 1303 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1978 | 2000 | -22 | 99 | 1392 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1974 | 2000 | -26 | 99 | 1389 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1954 | 2000 | -46 | 98 | 1375 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1953 | 2000 | -47 | 98 | 1375 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1944 | 2000 | -56 | 97 | 1363 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1935 | 2000 | -65 | 97 | 1362 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1933 | 2000 | -67 | 97 | 1367 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1928 | 2000 | -72 | 96 | 1357 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1923 | 2000 | -77 | 96 | 1350 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1922 | 2000 | -78 | 96 | 1353 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1918 | 2000 | -82 | 96 | 1350 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1754 | 1836 | -82 | 96 | 1249 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1910 | 2000 | -90 | 95 | 1346 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1900 | 2000 | -100 | 95 | 1336 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1821 | 2000 | -179 | 91 | 1283 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1791 | 2000 | -209 | 90 | 1250 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1791 | 2000 | -209 | 90 | -1226 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1779 | 2000 | -221 | 89 | 1243 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1779 | 2000 | -221 | 89 | -1215 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1761 | 2000 | -239 | 88 | 1220 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1752 | 2000 | -248 | 88 | 1215 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1078 | 1248 | -171 | 86 | 440 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1078 | 1248 | -171 | 86 | 440 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1075 | 1248 | -174 | 86 | 439 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1075 | 1248 | -174 | 86 | 439 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1071 | 1248 | -178 | 86 | 438 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1071 | 1248 | -178 | 86 | 438 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1533 | 1836 | -303 | 84 | 1091 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1497 | 1836 | -339 | 82 | 1065 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1489 | 1836 | -347 | 81 | 1059 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1482 | 1836 | -354 | 81 | 1054 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1479 | 1836 | -357 | 81 | 1052 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1477 | 1836 | -359 | 80 | 1050 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1472 | 1836 | -364 | 80 | 1047 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1460 | 1836 | -376 | 80 | 1038 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1458 | 1836 | -378 | 79 | 1037 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1455 | 1836 | -381 | 79 | 1035 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1403 | 1890 | -487 | 74 | -979 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 920 | 1248 | -328 | 74 | 376 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 920 | 1248 | -328 | 74 | 376 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 915 | 1248 | -334 | 73 | 374 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1403 | 1920 | -517 | 73 | 1002 | AC