## SRO borders-exports
SUBMISSION DATE: | 20.04.2026
BUSINESS DATE: | 22.04.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC RO-BG
00:00 | 01:00 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3908 | 3708 | 2596
01:00 | 02:00 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3936 | 3736 | 2615
02:00 | 03:00 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 90 | 3775 | 3575 | 2502
03:00 | 04:00 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 100 | 3887 | 3687 | 2581
04:00 | 05:00 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 100 | 3896 | 3696 | 2587
05:00 | 06:00 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3663 | 3463 | 2424
06:00 | 07:00 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | 84 | 3516 | 3316 | 2321
07:00 | 08:00 | Fallback - Initial CC | Fallback - Initial CC | Fallback - Initial CC | Fallback - Initial CC | Fallback - Initial CC | 1500
08:00 | 09:00 | Fallback - Initial CC | Fallback - Initial CC | Fallback - Initial CC | Fallback - Initial CC | Fallback - Initial CC | 1500
09:00 | 10:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | 70 | 523 | 323 | 226
10:00 | 11:00 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | 100 | 738 | 538 | 377
11:00 | 12:00 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | 100 | 806 | 606 | 424
12:00 | 13:00 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | 100 | 1020 | 820 | 574
13:00 | 14:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | 81 | 1551 | 1351 | 946
14:00 | 15:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | 83 | 1762 | 1562 | 1093
15:00 | 16:00 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | 100 | 2024 | 1824 | 1277
16:00 | 17:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 91 | 3582 | 3382 | 2367
17:00 | 18:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 98 | 3500 | 3300 | 2310
18:00 | 19:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 97 | 3242 | 3042 | 2129
19:00 | 20:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 96 | 3190 | 2990 | 2093
20:00 | 21:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 96 | 3226 | 3026 | 2118
21:00 | 22:00 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 99 | 3064 | 2864 | 2005
22:00 | 23:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 3507 | 3307 | 2315
23:00 | 00:00 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | 100 | 3659 | 3459 | 2421

## SRO borders-imports
SUBMISSION DATE: | 20.04.2026
BUSINESS DATE: | 22.04.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC BG-RO
00:00 | 01:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3591 | 3391 | 2374
01:00 | 02:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 97 | 3765 | 3565 | 2496
02:00 | 03:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3676 | 3476 | 2433
03:00 | 04:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 99 | 3803 | 3603 | 2522
04:00 | 05:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 95 | 3824 | 3624 | 2537
05:00 | 06:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 96 | 3844 | 3644 | 2551
06:00 | 07:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3670 | 3470 | 2429
07:00 | 08:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 96 | 3193 | 2993 | 2095
08:00 | 09:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 99 | 2881 | 2681 | 1877
09:00 | 10:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 98 | 2869 | 2669 | 1868
10:00 | 11:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 97 | 2993 | 2793 | 1955
11:00 | 12:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 96 | 3052 | 2852 | 1996
12:00 | 13:00 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] TRA 400/220 kV AT1 Portile de Fier | 99 | 3353 | 3153 | 2207
13:00 | 14:00 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] TRA 400/220 kV AT1 Portile de Fier | 100 | 3311 | 3111 | 2178
14:00 | 15:00 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] TRA 400/220 kV AT1 Portile de Fier | 99 | 3267 | 3067 | 2147
15:00 | 16:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 96 | 3205 | 3005 | 2104
16:00 | 17:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 97 | 3438 | 3238 | 2267
17:00 | 18:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3719 | 3519 | 2463
18:00 | 19:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3694 | 3494 | 2446
19:00 | 20:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3856 | 3656 | 2559
20:00 | 21:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3731 | 3531 | 2472
21:00 | 22:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3753 | 3553 | 2487
22:00 | 23:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3468 | 3268 | 2288
23:00 | 00:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3411 | 3211 | 2248

## SRO borders-exports RAs
SUBMISSION DATE: | 20.04.2026
BUSINESS DATE: | 22.04.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  | helpful
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  | helpful
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | helpful | helpful | helpful | helpful | helpful | helpful | notApplied |  |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | helpful | helpful | helpful | helpful |  |  | helpful
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst_ra |  | applied | [7 empty] | applied |  |  | applied | applied | applied
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst_ra |  | applied | [7 empty] | applied |  |  | applied | applied | applied
PST_ARAD 400/220_3 | RO_RA_00101 | pst_ra |  | applied | [7 empty] | applied |  |  | applied | applied | applied
PST_URECHESTI 400/220_1 | RO_RA_00102 | pst_ra |  | applied | [7 empty] | applied |  |  | applied | applied | applied
PRA 110 kV Resita | RO_RA_00007 | topological_ra | [9 empty] | applied |  |  | applied | applied | applied
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst_ra |  |  |  | applied
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst_ra |  |  |  | applied
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
RVMAR_5 _generator | RO_RA_00116 | costly_ra | 33 | 40 |  | 50 | 0 | 0 | [6 empty] | 50 | 50 |  | 50 | [7 empty] | 0
RGODI_5 _generator | RO_RA_00117 | costly_ra | 114 | 114 |  | 114 | 0 | 0 | [6 empty] | 114 |  |  | 114 | [7 empty] | 0
RTOPV_5 _generator | RO_RA_00120 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 10 |  |  | 0 | 10 | 10 | 0 | [7 empty] | 0
RFMEP_5 _generator | RO_RA_00121 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 14 |  |  |  | 14 | 14 | 0 | [7 empty] | 0
RVLCE15 _generator | RO_RA_00122 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 55 |  |  | 0 | 55 | 55 | 0 | [7 empty] | 0
RVALD_5 _generator | RO_RA_00123 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 15 |  |  |  | 15 | 15 | 0 | [7 empty] | 0
RELAR_5 _generator | RO_RA_00124 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 10 |  |  |  | 10 | 10 | 0 | [7 empty] | 0
RAREF_5 _generator | RO_RA_00125 | costly_ra | 0 | 0 |  | 0 | 0 | 10 |  |  |  | 10 |  |  |  | 10 | 10 | 10 | [7 empty] | 0
RARGS_5 _generator | RO_RA_00126 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 31 |  |  | 0 | 31 | 31 | 31 | [7 empty] | 0
RALBE_5 _generator | RO_RA_00127 | costly_ra | 0 | 0 |  | 0 | 0 | 30 |  |  |  | 30 |  |  | 0 | 30 | 30 | 0 | [7 empty] | 0
RCERB_5 _generator | RO_RA_00128 | costly_ra | 0 | 0 |  | 0 | 0 | 15 |  |  |  | 15 |  |  |  | 15 | 15 | 15 | [7 empty] | 0
RVLCE25 _generator | RO_RA_00129 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 12 |  |  |  | 12 | 12 | 0 | [7 empty] | 0
RCLNG_5 _generator | RO_RA_00130 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 90 |  |  | 0 | 90 | 90 | 0 | [7 empty] | 0
RSTUP_5 _generator | RO_RA_00134 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 45 |  |  | 0 | 45 | 45 | 0 | [7 empty] | 0
RDAIES5 _generator | RO_RA_00135 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 37 |  |  | 0 | 37 | 37 | 37 | [7 empty] | 0
RVILN_5 _generator | RO_RA_00136 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 46 |  |  | 0 | 46 | 46 | 0 | [7 empty] | 0
RRIUR15 _generator | RO_RA_00137 | costly_ra | 0 | 0 |  | 0 | 0 | 27 |  |  |  | 48 |  |  | 0 | 48 | 48 | 0 | [7 empty] | 0
RMARC_5 _generator | RO_RA_00138 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 39 |  |  | 0 | 39 | 39 | 0 | [7 empty] | 0
RIONE_5 _generator | RO_RA_00139 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 38 | 38 | 0 | [7 empty] | 0
RJIBL_5 _generator | RO_RA_00140 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 38 |  |  | 0 | 38 | 38 | 38 | [7 empty] | 0
RZAVI_5 _generator | RO_RA_00141 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 38 |  |  | 0 | 38 | 38 | 0 | [7 empty] | 0
RCHTU_5 _generator | RO_RA_00142 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 74 |  |  | 0 | 74 | 74 | 74 | [7 empty] | 0
RTRAI_5 _generator | RO_RA_00143 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 45 | 45 | 45 | [7 empty] | 0
RHGLOT5 _generator | RO_RA_00144 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 25 |  |  | 0 | 25 | 25 | 0 | [7 empty] | 0
RCHESJ5 _generator | RO_RA_00145 | costly_ra | 0 | 0 |  | 50 | 0 | 0 |  |  |  | 0 |  |  | 0 | 50 | 50 | 0 | [7 empty] | 0
RCHEAC5 _generator | RO_RA_00146 | costly_ra | 0 | 0 |  | 38 | 0 | 0 |  |  |  | 0 |  |  | 0 | 38 | 38 | 38 | [7 empty] | 0
RCHEST5 _generator | RO_RA_00147 | costly_ra | 0 | 0 |  | 26 | 0 | 0 |  |  |  | 0 |  |  | 0 | 26 | 26 | 26 | [7 empty] | 0
RCHEIO5 _generator | RO_RA_00148 | costly_ra | 0 | 0 |  | 53 | 0 | 0 |  |  |  | 0 |  |  | 0 | 53 | 53 | 53 | [7 empty] | 0
RCHDO_5 _generator | RO_RA_00149 | costly_ra | 0 | 0 |  | 53 | 0 | 53 |  |  |  | 0 |  |  | 0 | 53 | 53 | 53 | [7 empty] | 0
RFRUN_5 _generator | RO_RA_00150 | costly_ra | 0 | 0 |  | 53 | 0 | 49 |  |  |  | 0 |  |  | 0 | 53 | 53 | 53 | [7 empty] | 0
RCIZBI5 _generator | RO_RA_00151 | costly_ra | 0 | 0 |  | 53 | 0 | 0 |  |  |  | 0 |  |  | 0 | 53 | 53 | 0 | [7 empty] | 0
RRUSA_5 _generator | RO_RA_00152 | costly_ra | 0 | 0 |  | 53 | 0 | 0 |  |  |  | 0 |  |  | 0 | 53 | 53 | 38 | [7 empty] | 0
RHCORN5 _generator | RO_RA_00153 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 59 |  |  | 0 | 59 | 59 | 0 | [7 empty] | 0
RFAGA_5 _generator | RO_RA_00154 | costly_ra | 0 | 0 |  | 0 | 0 | 20 |  |  |  | 20 |  |  | 0 | 20 | 20 | 0 | [7 empty] | 0
RUCEA25 _generator | RO_RA_00155 | costly_ra | 0 | 0 |  | 0 | 0 | 32 |  |  |  | 32 |  |  | 0 | 32 | 32 | 32 | [7 empty] | 0
RUCEA15 _generator | RO_RA_00156 | costly_ra | 0 | 0 |  | 0 | 0 | 49 |  |  |  | 0 |  |  | 0 | 49 | 49 | 0 | [7 empty] | 0
RCIRT_5 _generator | RO_RA_00157 | costly_ra | 0 | 0 |  | 0 | 0 | 54 |  |  |  | 54 |  |  | 0 | 54 | 54 | 54 | [7 empty] | 7
RSTEJ_5 _generator | RO_RA_00158 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 137 |  |  |  | 79 | 137 | [8 empty] | 137
RRACO_5 _generator | RO_RA_00165 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 23 |  |  | 0 | 23 | 23 | 0 | [7 empty] | 0
RGARL_5 _generator | RO_RA_00166 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 23 |  |  | 0 | 23 | 23 | 23 | [7 empty] | 0
RLILI_5 _generator | RO_RA_00167 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 23 |  |  | 0 | 23 | 23 | 0 | [7 empty] | 0
RBACS_5 _generator | RO_RA_00168 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 98 |  |  | 0 | 98 | 98 | 0 | [7 empty] | 0
RFARA_5 _generator | RO_RA_00169 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 30 |  |  | 0 | 30 | 30 | 30 | [7 empty] | 0
RSISC_5 _generator | RO_RA_00170 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 44 |  |  | 0 | 44 | 44 | 0 | [7 empty] | 0
RMARA_5 _generator | RO_RA_00171 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 46 | 0 | [7 empty] | 0
RTECU_5 _generator | RO_RA_00172 | costly_ra | 0 | 0 |  | 0 | 0 | 0 |  |  |  | 0 |  |  | 0 | 34 | 34 | 0 | [7 empty] | 0
RMARI22 _generator | RO_RA_00173 | costly_ra | 217 | 217 |  | 217 | 217 | 217 |  |  |  | 217 |  |  | 217 | [10 empty] | 217
RSEBE_5 _generator | RO_RA_00176 | costly_ra | 55 | 55 |  | 55 | 55 | 55 |  |  |  | 55 |  |  | 55 | 0 | 0 | 55 | [7 empty] | 55
RIAZUA5 _generator | RO_RA_00177 | costly_ra | 71 | 71 |  | 71 | 71 | 71 | [6 empty] | 71 |  |  | 71 | [7 empty] | 71
RRETE22 _generator | RO_RA_00180 | costly_ra | 222 | 222 |  | 222 | 222 | [7 empty] | 222 | 0 | 0
RRETE_5 _generator | RO_RA_00181 | costly_ra | 20 | 20 |  | 20 | 20 | 20 |  |  |  | 20 |  |  | 20 | 20 | 20 | 0 | [7 empty] | 20
RCIRNA5 _generator | RO_RA_00182 | costly_ra | 29 | 29 |  | 29 | 29 | 29 |  |  |  | 0 |  |  | 0 | 0 | 0 | 0 | [7 empty] | 29
RCIRNB5 _generator | RO_RA_00183 | costly_ra | 27 | 27 |  | 27 | 27 | 27 |  |  |  | 0 |  |  | 0 | 0 | 0 | 0 | [7 empty] | 27
RHATE_5 _generator | RO_RA_00184 | costly_ra | 52 | 52 |  | 52 | 52 | 52 |  |  |  | 0 |  |  | 0 | 0 | 0 | 0 | [7 empty] | 52
RPDF212 _generator | RO_RA_00115 | costly_ra |  |  |  | 262 | [5 empty] | 0 |  |  | 106 | 0 | 0 | 336
RLOTR22 _generator | RO_RA_00131 | costly_ra |  |  |  | 0 | [5 empty] | 0 |  |  | 131 | 0 | 0
RLOT212 _generator | RO_RA_00132 | costly_ra |  |  |  | 91 | 235 | [7 empty] | 340 | 0 | 114
RGILC22 _generator | RO_RA_00175 | costly_ra |  |  |  | 150 | 150 | [7 empty] | 150 |  | 0 | 0
RBRDS25 _generator | RO_RA_00133 | costly_ra |  |  |  |  | 118 |  |  |  |  | 47 |  |  | 118
RROVI31 _generator | RO_RA_00105 | costly_ra | [9 empty] | 1
RTURC51 _generator | RO_RA_00108 | costly_ra | [9 empty] | 1 |  |  | 1
RSTEJ25 _generator | RO_RA_00159 | costly_ra | [9 empty] | 32 |  |  |  | 32 | 32 | [8 empty] | 32
RVADU_5 _generator | RO_RA_00160 | costly_ra | [9 empty] | 67 |  |  |  | 67 | 67 | [8 empty] | 24
RIZVO_5 _generator | RO_RA_00161 | costly_ra | [9 empty] | 9 |  |  |  | 9 | 9
RDUMB_5 _generator | RO_RA_00162 | costly_ra | [9 empty] | 23 |  |  |  | 23 | 23
RCOST_5 _generator | RO_RA_00163 | costly_ra | [9 empty] | 24 |  |  |  | 24 | 24
RBUHU_5 _generator | RO_RA_00164 | costly_ra | [9 empty] | 13 |  |  |  | 13 | 13
RSUGA22 _generator | RO_RA_00174 | costly_ra | [12 empty] | 150 | 0 | 0 | 0
RREME_5 _generator | RO_RA_00178 | costly_ra | [12 empty] | 0 | 0 | 0 | 0
RMUNT_5 _generator | RO_RA_00179 | costly_ra | [12 empty] | 0 | 0 | 0

## SRO borders-imports RAs
SUBMISSION DATE: | 20.04.2026
BUSINESS DATE: | 22.04.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400 kV TINTARENI-KOZLODUI 1 | BG_RA_00001 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  | notApplied | [9 empty] | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400/220kV AT3 Arad | RO_RA_00001 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  |  |  | helpful | helpful | helpful |  |  | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  |  |  | helpful | helpful | helpful |  |  | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | helpful | helpful | helpful | helpful | helpful | helpful | notApplied | notApplied |  |  |  |  | notApplied | notApplied | notApplied |  |  | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  |  |  | notApplied | notApplied | notApplied |  |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful |  |  |  |  | helpful | helpful | helpful |  |  | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied |  |  |  |  | notApplied | notApplied | notApplied |  |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV TINTARENI-KOZLODUI 2 | BG_RA_00002 | topological | [7 empty] | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
RROVI31 _generator | RO_RA_00105 | costly_ra | [19 empty] | 310 | 310
RTURC51 _generator | RO_RA_00108 | costly_ra | [19 empty] | 288 | 252
RPDF222 _generator | RO_RA_00114 | costly_ra | [19 empty] | 32 | 16 | 263
RPDF212 _generator | RO_RA_00115 | costly_ra | [19 empty] | 0 | 0
RVMAR_5 _generator | RO_RA_00116 | costly_ra | [19 empty] | 0 | 0 | 0
RGODI_5 _generator | RO_RA_00117 | costly_ra | [19 empty] | 0 | 0 | 0
RTOPV_5 _generator | RO_RA_00120 | costly_ra | [19 empty] | 0 | 0 | 0
RFMEP_5 _generator | RO_RA_00121 | costly_ra | [19 empty] | 0 | 0 | 0
RVLCE15 _generator | RO_RA_00122 | costly_ra | [19 empty] | 0 | 0 | 0
RVALD_5 _generator | RO_RA_00123 | costly_ra | [19 empty] | 0 | 0 | 0
RELAR_5 _generator | RO_RA_00124 | costly_ra | [19 empty] | 0 | 0 | 0
RAREF_5 _generator | RO_RA_00125 | costly_ra | [19 empty] | 0 | 0 | 0
RARGS_5 _generator | RO_RA_00126 | costly_ra | [19 empty] | 0 | 0 | 0
RALBE_5 _generator | RO_RA_00127 | costly_ra | [19 empty] | 0 | 0 | 0
RCERB_5 _generator | RO_RA_00128 | costly_ra | [19 empty] | 0 | 0 | 0
RVLCE25 _generator | RO_RA_00129 | costly_ra | [19 empty] | 0 | 0 | 0
RCLNG_5 _generator | RO_RA_00130 | costly_ra | [19 empty] | 0 | 0 | 0
RLOTR22 _generator | RO_RA_00131 | costly_ra | [19 empty] | 0 | 0
RLOT212 _generator | RO_RA_00132 | costly_ra | [19 empty] | 0 | 0
RBRDS25 _generator | RO_RA_00133 | costly_ra | [19 empty] | 0 | 0
RSTUP_5 _generator | RO_RA_00134 | costly_ra | [19 empty] | 0 | 0 | 0
RDAIES5 _generator | RO_RA_00135 | costly_ra | [19 empty] | 0 | 0 | 0
RVILN_5 _generator | RO_RA_00136 | costly_ra | [19 empty] | 0 | 0 | 0
RRIUR15 _generator | RO_RA_00137 | costly_ra | [19 empty] | 0 | 0 | 0
RMARC_5 _generator | RO_RA_00138 | costly_ra | [19 empty] | 0 | 0 | 0
RIONE_5 _generator | RO_RA_00139 | costly_ra | [19 empty] | 0 | 0 | 0
RJIBL_5 _generator | RO_RA_00140 | costly_ra | [19 empty] | 0 | 0 | 0
RZAVI_5 _generator | RO_RA_00141 | costly_ra | [19 empty] | 0 | 0 | 0
RCHTU_5 _generator | RO_RA_00142 | costly_ra | [19 empty] | 0 | 0 | 0
RTRAI_5 _generator | RO_RA_00143 | costly_ra | [19 empty] | 0 | 0 | 0
RHGLOT5 _generator | RO_RA_00144 | costly_ra | [19 empty] | 0 | 0 | 0
RCHESJ5 _generator | RO_RA_00145 | costly_ra | [19 empty] | 50 | 50 | 0
RCHEAC5 _generator | RO_RA_00146 | costly_ra | [19 empty] | 38 | 38 | 0
RCHEST5 _generator | RO_RA_00147 | costly_ra | [19 empty] | 26 | 0 | 0
RCHEIO5 _generator | RO_RA_00148 | costly_ra | [19 empty] | 53 | 53 | 0
RCHDO_5 _generator | RO_RA_00149 | costly_ra | [19 empty] | 53 | 53 | 0
RFRUN_5 _generator | RO_RA_00150 | costly_ra | [19 empty] | 0 | 53 | 0
RCIZBI5 _generator | RO_RA_00151 | costly_ra | [19 empty] | 0 | 53 | 0
RRUSA_5 _generator | RO_RA_00152 | costly_ra | [19 empty] | 53 | 53 | 0
RHCORN5 _generator | RO_RA_00153 | costly_ra | [19 empty] | 0 | 0 | 0
RFAGA_5 _generator | RO_RA_00154 | costly_ra | [19 empty] | 0 | 0 | 0
RUCEA25 _generator | RO_RA_00155 | costly_ra | [19 empty] | 0 | 0 | 0
RUCEA15 _generator | RO_RA_00156 | costly_ra | [19 empty] | 0 | 0 | 0
RCIRT_5 _generator | RO_RA_00157 | costly_ra | [19 empty] | 0 | 0 | 0
RSTEJ_5 _generator | RO_RA_00158 | costly_ra | [19 empty] | 0 | 0
RRACO_5 _generator | RO_RA_00165 | costly_ra | [19 empty] | 0 | 0 | 0
RGARL_5 _generator | RO_RA_00166 | costly_ra | [19 empty] | 0 | 0 | 0
RLILI_5 _generator | RO_RA_00167 | costly_ra | [19 empty] | 0 | 0 | 0
RBACS_5 _generator | RO_RA_00168 | costly_ra | [19 empty] | 0 | 0 | 0
RFARA_5 _generator | RO_RA_00169 | costly_ra | [19 empty] | 0 | 0 | 0
RSISC_5 _generator | RO_RA_00170 | costly_ra | [19 empty] | 0 | 0 | 0
RMARA_5 _generator | RO_RA_00171 | costly_ra | [19 empty] | 0 | 0 | 0
RTECU_5 _generator | RO_RA_00172 | costly_ra | [19 empty] | 0 | 0 | 0
RMARI22 _generator | RO_RA_00173 | costly_ra | [19 empty] | 0 | 0
RSUGA22 _generator | RO_RA_00174 | costly_ra | [19 empty] | 0 | 0 | 150
RGILC22 _generator | RO_RA_00175 | costly_ra | [19 empty] | 0 | 0 | 69
RSEBE_5 _generator | RO_RA_00176 | costly_ra | [19 empty] | 0 | 0 | 0
RREME_5 _generator | RO_RA_00178 | costly_ra | [19 empty] | 0 | 0
RMUNT_5 _generator | RO_RA_00179 | costly_ra | [19 empty] | 0 | 0
RRETE22 _generator | RO_RA_00180 | costly_ra | [19 empty] | 0 | 0 | 222
RRETE_5 _generator | RO_RA_00181 | costly_ra | [19 empty] | 0 | 0 | 20
RCIRNA5 _generator | RO_RA_00182 | costly_ra | [19 empty] | 0 | 0 | 29
RCIRNB5 _generator | RO_RA_00183 | costly_ra | [19 empty] | 0 | 0 | 27
RHATE_5 _generator | RO_RA_00184 | costly_ra | [19 empty] | 0 | 0 | 52