## 0030
Detailed results
Generated at: | 20/04/2026 21:48:40
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2519.42
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1590 | 1600 | -10 | 99 | 1137 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1456 | 1600 | -144 | 91 | 1031 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1455 | 1600 | -145 | 91 | 1031 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1406 | 1600 | -194 | 88 | 1003 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1312 | 1600 | -288 | 82 | 939 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1306 | 1600 | -294 | 82 | 935 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1275 | 1600 | -325 | 80 | 912 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1271 | 1600 | -329 | 79 | 911 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1600 | -350 | 78 | 895 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | 878 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 875 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 852 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 845 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 843 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 842 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 838 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 838 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 838 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 836 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 836 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 835 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 835 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 833 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1600 | -439 | 73 | 831 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1600 | -439 | 73 | 831 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1600 | -440 | 73 | 831 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1600 | -440 | 72 | 831 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 830 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 829 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1156 | 1600 | -444 | 72 | 828 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 824 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 824 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 824 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1600 | -454 | 72 | 821 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 820 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1600 | -457 | 71 | 819 | AC

## 0130
Detailed results
Generated at: | 20/04/2026 21:48:40
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2614.68
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1594 | 1600 | -6 | 100 | 1140 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1464 | 1600 | -136 | 91 | 1038 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1463 | 1600 | -137 | 91 | 1037 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1389 | 1600 | -211 | 87 | 991 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1310 | 1600 | -290 | 82 | 938 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1286 | 1600 | -314 | 80 | 920 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1259 | 1600 | -341 | 79 | 901 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1256 | 1600 | -344 | 78 | 900 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1600 | -356 | 78 | 891 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1600 | -366 | 77 | 884 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 879 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 855 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 845 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 844 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 843 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 838 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 838 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 836 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 835 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 834 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 834 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1600 | -437 | 73 | 834 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1600 | -440 | 72 | 831 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1600 | -440 | 72 | 831 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 831 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 830 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 830 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 830 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 829 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 827 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 826 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 826 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 824 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 823 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 823 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1600 | -454 | 72 | 821 | AC

## 0230
Detailed results
Generated at: | 20/04/2026 21:48:40
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2618.25
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1595 | 1600 | -5 | 100 | 1140 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1468 | 1600 | -132 | 92 | 1040 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1467 | 1600 | -133 | 92 | 1039 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1380 | 1600 | -220 | 86 | 985 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1308 | 1600 | -292 | 82 | 937 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1276 | 1600 | -324 | 80 | 913 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1600 | -346 | 78 | 897 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1250 | 1600 | -350 | 78 | 896 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1600 | -356 | 78 | 891 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1600 | -361 | 77 | 887 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1233 | 1600 | -367 | 77 | 883 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 879 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 853 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 844 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 74 | 843 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 841 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1168 | 1600 | -432 | 73 | 837 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 835 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 835 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 833 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 833 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 833 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 832 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1600 | -439 | 73 | 832 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 830 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 830 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 830 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 830 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 829 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1156 | 1600 | -444 | 72 | 828 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 828 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 827 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 827 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 824 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 822 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 822 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 822 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1600 | -454 | 72 | 821 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1125 | 1600 | -475 | 70 | 806 | AC

## 0330
Detailed results
Generated at: | 20/04/2026 21:48:40
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2692.88
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1596 | 1600 | -4 | 100 | 1141 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1481 | 1600 | -119 | 93 | 1050 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1481 | 1600 | -119 | 93 | 1049 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1350 | 1600 | -250 | 84 | 964 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1307 | 1600 | -293 | 82 | 936 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1253 | 1600 | -347 | 78 | 897 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1600 | -354 | 78 | 892 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1600 | -361 | 77 | 887 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 886 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1236 | 1600 | -364 | 77 | 885 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1600 | -377 | 76 | 876 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 874 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 847 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 840 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1600 | -437 | 73 | 834 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1600 | -440 | 73 | 831 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 831 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1156 | 1600 | -444 | 72 | 828 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 828 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 826 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 826 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 826 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 825 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 824 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 823 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1600 | -452 | 72 | 823 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1600 | -452 | 72 | 823 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1600 | -452 | 72 | 823 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 822 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 822 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 821 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 72 | 820 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 72 | 820 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1600 | -460 | 71 | 817 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1139 | 1600 | -461 | 71 | 816 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1138 | 1600 | -462 | 71 | 815 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1138 | 1600 | -462 | 71 | 815 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 811 | AC

## 0430
Detailed results
Generated at: | 20/04/2026 21:48:40
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2679.52
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1595 | 1600 | -5 | 100 | 1140 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1487 | 1600 | -113 | 93 | 1054 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1487 | 1600 | -113 | 93 | 1054 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1328 | 1600 | -272 | 83 | 948 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1297 | 1600 | -303 | 81 | 929 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1242 | 1600 | -358 | 78 | 890 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 882 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1600 | -375 | 77 | 877 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1600 | -377 | 76 | 876 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 876 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1600 | -384 | 76 | 871 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 870 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1600 | -426 | 73 | 841 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 835 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1156 | 1600 | -444 | 72 | 829 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 826 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 823 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 823 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 823 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1600 | -452 | 72 | 823 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 822 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 822 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1600 | -454 | 72 | 822 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1600 | -457 | 71 | 819 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1600 | -458 | 71 | 819 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1600 | -458 | 71 | 818 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1141 | 1600 | -459 | 71 | 818 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1141 | 1600 | -459 | 71 | 818 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1600 | -460 | 71 | 817 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1139 | 1600 | -461 | 71 | 817 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1138 | 1600 | -462 | 71 | 816 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1137 | 1600 | -463 | 71 | 815 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1136 | 1600 | -464 | 71 | 814 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 811 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 811 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 811 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1129 | 1600 | -471 | 71 | 809 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1128 | 1600 | -472 | 70 | 808 | AC

## 0530
Detailed results
Generated at: | 20/04/2026 21:48:40
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2677.82
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1592 | 1600 | -8 | 99 | 1138 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1480 | 1600 | -120 | 93 | 1048 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1480 | 1600 | -120 | 92 | 1047 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1348 | 1600 | -252 | 84 | 962 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1312 | 1600 | -288 | 82 | 939 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1247 | 1600 | -353 | 78 | 893 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1600 | -354 | 78 | 892 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1240 | 1600 | -360 | 78 | 887 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1600 | -363 | 77 | 886 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 873 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 869 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 839 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 836 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 830 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 829 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 827 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 826 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 824 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 824 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 824 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 823 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 823 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1600 | -452 | 72 | 823 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 71 | 819 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1600 | -457 | 71 | 819 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1600 | -457 | 71 | 819 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1600 | -458 | 71 | 819 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1600 | -458 | 71 | 818 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1600 | -460 | 71 | 817 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1600 | -460 | 71 | 817 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1139 | 1600 | -461 | 71 | 816 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1136 | 1600 | -464 | 71 | 814 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1134 | 1600 | -466 | 71 | 812 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1134 | 1600 | -466 | 71 | 812 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1130 | 1600 | -470 | 71 | 809 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1120 | 1600 | -480 | 70 | 803 | AC

## 0630
Detailed results
Generated at: | 20/04/2026 21:48:40
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2643.28
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1598 | 1600 | -2 | 100 | 1142 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1485 | 1600 | -115 | 93 | 1051 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1485 | 1600 | -115 | 93 | 1051 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1354 | 1600 | -246 | 85 | 967 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1320 | 1600 | -280 | 82 | 944 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1600 | -338 | 79 | 903 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1260 | 1600 | -340 | 79 | 902 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1242 | 1600 | -358 | 78 | 888 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 887 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 874 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 873 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 840 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 839 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 838 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1600 | -437 | 73 | 833 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 832 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1600 | -439 | 73 | 831 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 830 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 829 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 828 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 828 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1600 | -446 | 72 | 827 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 826 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1148 | 1600 | -452 | 72 | 823 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 822 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1147 | 1600 | -453 | 72 | 822 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1600 | -454 | 72 | 821 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 821 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 820 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1142 | 1600 | -458 | 71 | 819 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1600 | -460 | 71 | 817 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1600 | -460 | 71 | 817 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1137 | 1600 | -463 | 71 | 814 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 813 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1129 | 1600 | -471 | 71 | 809 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1600 | -474 | 70 | 807 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1123 | 1600 | -477 | 70 | 805 | AC

## 0730
Detailed results
Generated at: | 20/04/2026 21:48:41
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2439.23
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1592 | 1600 | -8 | 100 | 1139 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1488 | 1600 | -112 | 93 | 1056 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1487 | 1600 | -113 | 93 | 1056 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1303 | 1600 | -297 | 81 | 931 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1288 | 1600 | -312 | 80 | 923 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1600 | -354 | 78 | 893 | AC
GR_IT_CO_00001 | N-1 TIE 400 kV Arachthos - Galatina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1243 | 1600 | -357 | 78 | 890 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 868 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 865 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 860 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 859 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 857 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 853 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1600 | -429 | 73 | 840 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1161 | 1600 | -439 | 73 | 832 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 826 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 826 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 824 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 824 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 821 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 821 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 821 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1600 | -457 | 71 | 819 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1600 | -457 | 71 | 819 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1600 | -460 | 71 | 818 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1136 | 1600 | -464 | 71 | 815 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1136 | 1600 | -464 | 71 | 814 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1136 | 1600 | -464 | 71 | 814 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 814 | AC
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 814 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 813 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1130 | 1600 | -470 | 71 | 810 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1128 | 1600 | -472 | 70 | 809 | AC

## 0830
Detailed results
Generated at: | 20/04/2026 21:48:41
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2382.67
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1595 | 1600 | -5 | 100 | 1140 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1466 | 1600 | -134 | 92 | 1039 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1465 | 1600 | -135 | 92 | 1039 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1307 | 1600 | -293 | 82 | 935 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1301 | 1600 | -299 | 81 | 930 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1279 | 1600 | -321 | 80 | 915 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 879 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 878 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1224 | 1600 | -376 | 77 | 877 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 875 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 873 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 870 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 857 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 849 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 844 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 843 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 74 | 843 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 838 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1168 | 1600 | -432 | 73 | 837 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1168 | 1600 | -432 | 73 | 837 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 835 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 836 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 834 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1600 | -437 | 73 | 834 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 831 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 831 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 830 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 830 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 830 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1600 | -454 | 72 | 821 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1600 | -454 | 72 | 821 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1140 | 1600 | -460 | 71 | 817 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1137 | 1600 | -463 | 71 | 815 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1128 | 1600 | -472 | 70 | 808 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1126 | 1600 | -474 | 70 | 806 | AC

## 0930
Detailed results
Generated at: | 20/04/2026 21:48:41
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2382.22
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1598 | 1600 | -2 | 100 | 1138 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1433 | 1600 | -167 | 90 | 1010 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1433 | 1600 | -167 | 90 | 1011 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1352 | 1600 | -248 | 85 | 964 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1330 | 1600 | -270 | 83 | 949 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1305 | 1600 | -295 | 82 | 931 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1272 | 1600 | -328 | 79 | 908 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1271 | 1600 | -329 | 79 | 906 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1268 | 1600 | -332 | 79 | 905 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1600 | -336 | 79 | 902 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1252 | 1600 | -348 | 78 | 894 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1245 | 1600 | -355 | 78 | 889 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 870 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1600 | -384 | 76 | 869 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 868 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 867 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 861 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 857 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 856 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 856 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 856 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 855 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 855 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 853 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 74 | 851 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 851 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 850 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 849 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 849 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 842 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 839 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 836 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 833 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 826 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1600 | -454 | 72 | 818 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 807 | AC

## 1030
Detailed results
Generated at: | 20/04/2026 21:48:41
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2351.58
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1594 | 1600 | -6 | 100 | 1137 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1433 | 1600 | -167 | 90 | 1013 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1432 | 1600 | -168 | 90 | 1012 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1357 | 1600 | -243 | 85 | 968 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1324 | 1600 | -276 | 83 | 946 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1290 | 1600 | -310 | 81 | 922 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1287 | 1600 | -313 | 80 | 920 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1270 | 1600 | -330 | 79 | 907 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1267 | 1600 | -333 | 79 | 906 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1252 | 1600 | -348 | 78 | 895 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1237 | 1600 | -363 | 77 | 884 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1236 | 1600 | -364 | 77 | 884 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 865 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 864 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 75 | 864 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 860 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 856 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 74 | 853 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 851 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 851 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 851 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 851 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 850 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 846 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 845 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 844 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1600 | -426 | 73 | 839 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1600 | -427 | 73 | 840 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 836 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 833 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 828 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1600 | -446 | 72 | 824 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1139 | 1600 | -461 | 71 | 814 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1600 | -478 | 70 | 801 | AC

## 1130
Detailed results
Generated at: | 20/04/2026 21:48:41
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2395.07
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1599 | 1600 | -1 | 100 | 1137 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1405 | 1600 | -195 | 88 | 991 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1405 | 1600 | -195 | 88 | 992 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1393 | 1600 | -207 | 87 | 992 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1354 | 1600 | -246 | 85 | 965 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1332 | 1600 | -268 | 83 | 949 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1324 | 1600 | -276 | 83 | 943 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1311 | 1600 | -289 | 82 | 934 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1308 | 1600 | -292 | 82 | 933 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1273 | 1600 | -327 | 80 | 907 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1269 | 1600 | -331 | 79 | 905 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1263 | 1600 | -337 | 79 | 901 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1600 | -356 | 78 | 888 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1242 | 1600 | -358 | 78 | 885 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1240 | 1600 | -360 | 78 | 885 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1600 | -370 | 77 | 877 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 875 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1600 | -377 | 76 | 872 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 872 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 871 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 871 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 870 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 870 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 869 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 867 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 867 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 866 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 866 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 860 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 859 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 858 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 854 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 853 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 854 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 846 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 845 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1162 | 1600 | -438 | 73 | 827 | AC
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1128 | 1600 | -472 | 70 | 805 | AC

## 1230
Detailed results
Generated at: | 20/04/2026 21:48:41
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2639.46
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1598 | 1600 | -2 | 100 | 1139 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1438 | 1600 | -162 | 90 | 1025 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1393 | 1600 | -207 | 87 | 986 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1393 | 1600 | -207 | 87 | 986 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1390 | 1600 | -210 | 87 | 992 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1388 | 1600 | -212 | 87 | 991 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1367 | 1600 | -233 | 85 | 975 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1363 | 1600 | -237 | 85 | 973 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1342 | 1600 | -258 | 84 | 958 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1288 | 1600 | -312 | 81 | 920 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1265 | 1600 | -335 | 79 | 904 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1600 | -336 | 79 | 903 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1247 | 1600 | -353 | 78 | 891 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1600 | -354 | 78 | 891 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1243 | 1600 | -357 | 78 | 888 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1600 | -365 | 77 | 883 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 880 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1600 | -371 | 77 | 878 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 878 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | 876 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | 876 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | 876 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1600 | -375 | 77 | 876 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1225 | 1600 | -375 | 77 | 875 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 873 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 873 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 872 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 872 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 871 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 869 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 866 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 863 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 856 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 856 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 851 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 842 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 827 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1152 | 1600 | -448 | 72 | 822 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1137 | 1600 | -463 | 71 | 813 | AC

## 1330
Detailed results
Generated at: | 20/04/2026 21:48:42
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2730.31
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1598 | 1600 | -2 | 100 | 1141 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1453 | 1600 | -147 | 91 | 1036 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1405 | 1600 | -195 | 88 | 1004 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1402 | 1600 | -198 | 88 | 994 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1402 | 1600 | -198 | 88 | 994 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1393 | 1600 | -207 | 87 | 996 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1376 | 1600 | -224 | 86 | 983 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1373 | 1600 | -227 | 86 | 982 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1330 | 1600 | -270 | 83 | 951 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1283 | 1600 | -317 | 80 | 918 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1600 | -338 | 79 | 903 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1258 | 1600 | -342 | 79 | 901 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1600 | -361 | 77 | 886 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1236 | 1600 | -364 | 77 | 884 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 881 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1600 | -377 | 76 | 876 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 875 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 875 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 873 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 872 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 872 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1600 | -383 | 76 | 872 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1600 | -384 | 76 | 871 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1215 | 1600 | -385 | 76 | 870 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 869 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1214 | 1600 | -386 | 76 | 869 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 868 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 867 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 867 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 866 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 860 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 860 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 853 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 850 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 835 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 820 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 812 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1124 | 1600 | -476 | 70 | 805 | AC

## 1430
Detailed results
Generated at: | 20/04/2026 21:48:42
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2742.98
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1599 | 1600 | -1 | 100 | 1142 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1461 | 1600 | -139 | 91 | 1042 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1411 | 1600 | -189 | 88 | 1009 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1405 | 1600 | -195 | 88 | 996 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1404 | 1600 | -196 | 88 | 996 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1392 | 1600 | -208 | 87 | 995 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1379 | 1600 | -221 | 86 | 986 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1376 | 1600 | -224 | 86 | 984 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1326 | 1600 | -274 | 83 | 948 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1282 | 1600 | -318 | 80 | 918 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1262 | 1600 | -338 | 79 | 903 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1259 | 1600 | -341 | 79 | 902 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1239 | 1600 | -361 | 77 | 887 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 881 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 880 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1221 | 1600 | -379 | 76 | 875 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 874 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 874 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 872 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1600 | -383 | 76 | 871 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1600 | -384 | 76 | 871 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1216 | 1600 | -384 | 76 | 871 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 869 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 869 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 869 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 868 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1211 | 1600 | -389 | 76 | 867 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1210 | 1600 | -390 | 76 | 867 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 866 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 866 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 860 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 860 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 75 | 854 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1186 | 1600 | -414 | 74 | 850 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 842 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 835 | AC
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 71 | 819 | AC
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1133 | 1600 | -467 | 71 | 811 | AC
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1600 | -478 | 70 | 804 | AC

## 1530
Detailed results
Generated at: | 20/04/2026 21:48:42
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2688.31
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1600 | 1600 | 0 | 100 | 1143 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1449 | 1600 | -151 | 91 | 1033 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1433 | 1600 | -167 | 90 | 1011 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1432 | 1600 | -168 | 90 | 1010 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1388 | 1600 | -212 | 87 | 993 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1377 | 1600 | -223 | 86 | 985 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1348 | 1600 | -252 | 84 | 963 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1344 | 1600 | -256 | 84 | 961 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1314 | 1600 | -286 | 82 | 940 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1261 | 1600 | -339 | 79 | 902 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1248 | 1600 | -352 | 78 | 893 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1236 | 1600 | -364 | 77 | 885 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | 878 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1220 | 1600 | -380 | 76 | 873 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1213 | 1600 | -387 | 76 | 869 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1212 | 1600 | -388 | 76 | 868 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 862 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 861 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 860 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 860 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 860 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 860 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 859 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 856 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 856 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 855 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 855 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 853 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1600 | -413 | 74 | 850 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 849 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 844 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 844 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1168 | 1600 | -432 | 73 | 836 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 829 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1155 | 1600 | -445 | 72 | 827 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 824 | AC

## 1630
Detailed results
Generated at: | 20/04/2026 21:48:42
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2638.39
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1591 | 1600 | -9 | 99 | 1137 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1440 | 1600 | -160 | 90 | 1026 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1422 | 1600 | -178 | 89 | 1005 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1422 | 1600 | -178 | 89 | 1004 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1373 | 1600 | -227 | 86 | 982 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1366 | 1600 | -234 | 85 | 977 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1346 | 1600 | -254 | 84 | 962 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1342 | 1600 | -258 | 84 | 960 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1313 | 1600 | -287 | 82 | 939 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1255 | 1600 | -345 | 78 | 898 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1246 | 1600 | -354 | 78 | 892 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1231 | 1600 | -369 | 77 | 881 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1222 | 1600 | -378 | 76 | 875 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1219 | 1600 | -381 | 76 | 872 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1217 | 1600 | -383 | 76 | 871 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 863 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1202 | 1600 | -398 | 75 | 860 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 858 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 858 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 858 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 857 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 856 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 854 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 853 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 853 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 853 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1190 | 1600 | -410 | 74 | 852 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1187 | 1600 | -413 | 74 | 850 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 846 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 846 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 846 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1600 | -427 | 73 | 840 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 833 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1156 | 1600 | -444 | 72 | 828 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 824 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1600 | -457 | 71 | 818 | AC

## 1730
Detailed results
Generated at: | 20/04/2026 21:48:42
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2704.55
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1592 | 1600 | -8 | 100 | 1137 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1493 | 1600 | -107 | 93 | 1062 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1427 | 1600 | -173 | 89 | 1003 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1426 | 1600 | -174 | 89 | 1002 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1419 | 1600 | -181 | 89 | 1014 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1384 | 1600 | -216 | 86 | 989 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1369 | 1600 | -231 | 86 | 977 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1363 | 1600 | -237 | 85 | 975 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1325 | 1600 | -275 | 83 | 947 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1264 | 1600 | -336 | 79 | 904 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1254 | 1600 | -346 | 78 | 897 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1600 | -371 | 77 | 879 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 877 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1226 | 1600 | -374 | 77 | 877 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1208 | 1600 | -392 | 76 | 864 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 863 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1203 | 1600 | -397 | 75 | 860 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 860 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1201 | 1600 | -399 | 75 | 860 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 858 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 857 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1197 | 1600 | -403 | 75 | 857 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1193 | 1600 | -407 | 75 | 854 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 74 | 853 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 852 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 852 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 852 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 846 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 845 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 844 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 844 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1600 | -426 | 73 | 840 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 834 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 829 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1138 | 1600 | -462 | 71 | 814 | AC
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1130 | 1600 | -470 | 71 | 807 | AC

## 1830
Detailed results
Generated at: | 20/04/2026 21:48:42
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2567.97
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1593 | 1600 | -7 | 100 | 1137 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1458 | 1600 | -142 | 91 | 1038 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1453 | 1600 | -147 | 91 | 1023 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1452 | 1600 | -148 | 91 | 1022 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1380 | 1600 | -220 | 86 | 986 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1355 | 1600 | -245 | 85 | 968 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1327 | 1600 | -273 | 83 | 948 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1322 | 1600 | -278 | 83 | 945 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1299 | 1600 | -301 | 81 | 929 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1236 | 1600 | -364 | 77 | 884 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 878 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1227 | 1600 | -373 | 77 | 878 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 863 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1205 | 1600 | -395 | 75 | 861 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 856 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 74 | 853 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1182 | 1600 | -418 | 74 | 846 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 841 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 839 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1600 | -429 | 73 | 838 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1600 | -429 | 73 | 838 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 838 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 837 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 837 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 837 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 829 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 828 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 823 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 822 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1139 | 1600 | -461 | 71 | 815 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 810 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1131 | 1600 | -469 | 71 | 809 | AC

## 1930
Detailed results
Generated at: | 20/04/2026 21:48:42
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2523.95
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1591 | 1600 | -9 | 99 | 1136 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1454 | 1600 | -146 | 91 | 1023 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1453 | 1600 | -147 | 91 | 1034 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1453 | 1600 | -147 | 91 | 1022 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1369 | 1600 | -231 | 86 | 978 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1347 | 1600 | -253 | 84 | 963 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1311 | 1600 | -289 | 82 | 936 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1306 | 1600 | -294 | 82 | 934 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1292 | 1600 | -308 | 81 | 923 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1232 | 1600 | -368 | 77 | 881 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 879 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1228 | 1600 | -372 | 77 | 878 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 861 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1199 | 1600 | -401 | 75 | 856 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1189 | 1600 | -411 | 74 | 851 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 850 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 845 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 845 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1178 | 1600 | -422 | 74 | 843 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 840 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1600 | -427 | 73 | 839 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1600 | -429 | 73 | 838 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 836 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 835 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 835 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 834 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 834 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 834 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1156 | 1600 | -444 | 72 | 827 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1154 | 1600 | -446 | 72 | 826 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1146 | 1600 | -454 | 72 | 820 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1141 | 1600 | -459 | 71 | 817 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 812 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1134 | 1600 | -466 | 71 | 811 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1132 | 1600 | -468 | 71 | 810 | AC

## 2030
Detailed results
Generated at: | 20/04/2026 21:48:42
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2550.47
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1595 | 1600 | -5 | 100 | 1138 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1465 | 1600 | -135 | 92 | 1042 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1457 | 1600 | -143 | 91 | 1025 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1456 | 1600 | -144 | 91 | 1024 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1377 | 1600 | -223 | 86 | 984 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1352 | 1600 | -248 | 84 | 966 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1317 | 1600 | -283 | 82 | 940 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1311 | 1600 | -289 | 82 | 937 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1297 | 1600 | -303 | 81 | 927 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1244 | 1600 | -356 | 78 | 890 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1232 | 1600 | -368 | 77 | 881 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1600 | -370 | 77 | 880 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 865 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1204 | 1600 | -396 | 75 | 860 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1194 | 1600 | -406 | 75 | 854 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1192 | 1600 | -408 | 75 | 853 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 848 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1184 | 1600 | -416 | 74 | 847 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 846 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 843 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 842 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 841 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1173 | 1600 | -427 | 73 | 839 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1600 | -429 | 73 | 838 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1171 | 1600 | -429 | 73 | 838 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 837 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 837 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 837 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1160 | 1600 | -440 | 72 | 830 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 829 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 823 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1145 | 1600 | -455 | 72 | 820 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1138 | 1600 | -462 | 71 | 814 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 812 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 812 | AC

## 2130
Detailed results
Generated at: | 20/04/2026 21:48:43
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2621.92
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1591 | 1600 | -9 | 99 | 1136 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1461 | 1600 | -139 | 91 | 1039 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1459 | 1600 | -141 | 91 | 1026 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1458 | 1600 | -142 | 91 | 1025 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1374 | 1600 | -226 | 86 | 982 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1354 | 1600 | -246 | 85 | 967 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1324 | 1600 | -276 | 83 | 945 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1319 | 1600 | -281 | 82 | 943 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1296 | 1600 | -304 | 81 | 926 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1230 | 1600 | -370 | 77 | 880 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1229 | 1600 | -371 | 77 | 879 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1218 | 1600 | -382 | 76 | 871 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 857 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1198 | 1600 | -402 | 75 | 856 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1191 | 1600 | -409 | 74 | 852 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 848 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1177 | 1600 | -423 | 74 | 842 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 74 | 842 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 73 | 841 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1172 | 1600 | -428 | 73 | 838 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 836 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 835 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 834 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 833 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1600 | -437 | 73 | 832 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1600 | -437 | 73 | 832 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1600 | -437 | 73 | 832 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1600 | -437 | 73 | 832 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1153 | 1600 | -447 | 72 | 825 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1150 | 1600 | -450 | 72 | 823 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1143 | 1600 | -457 | 71 | 818 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 812 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1131 | 1600 | -469 | 71 | 809 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1129 | 1600 | -471 | 71 | 808 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1122 | 1600 | -478 | 70 | 803 | AC

## 2230
Detailed results
Generated at: | 20/04/2026 21:48:43
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2618.57
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1597 | 1600 | -3 | 100 | 1140 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1470 | 1600 | -130 | 92 | 1034 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1469 | 1600 | -131 | 92 | 1033 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1465 | 1600 | -135 | 92 | 1042 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1371 | 1600 | -229 | 86 | 980 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1359 | 1600 | -241 | 85 | 971 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1326 | 1600 | -274 | 83 | 947 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1321 | 1600 | -279 | 83 | 944 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1296 | 1600 | -304 | 81 | 926 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1235 | 1600 | -365 | 77 | 884 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1223 | 1600 | -377 | 76 | 875 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 858 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1200 | 1600 | -400 | 75 | 858 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 855 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 855 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 845 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 844 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1179 | 1600 | -421 | 74 | 844 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 74 | 841 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1176 | 1600 | -424 | 73 | 841 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 841 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1170 | 1600 | -430 | 73 | 837 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 835 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1167 | 1600 | -433 | 73 | 835 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 834 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1166 | 1600 | -434 | 73 | 834 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1165 | 1600 | -435 | 73 | 834 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1158 | 1600 | -442 | 72 | 829 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 828 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1157 | 1600 | -443 | 72 | 828 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1151 | 1600 | -449 | 72 | 823 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 822 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1139 | 1600 | -461 | 71 | 814 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1129 | 1600 | -471 | 71 | 808 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1125 | 1600 | -475 | 70 | 805 | AC

## 2330
Detailed results
Generated at: | 20/04/2026 21:48:43
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | North-Greece Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2618.61
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Thessaloniki - Dubrovo/[GR-MK] [OPP] TIE 400 kV Meliti - Bitola
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1596 | 1600 | -4 | 100 | 1139 | AC
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1474 | 1600 | -126 | 92 | 1049 | AC
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1454 | 1600 | -146 | 91 | 1023 | AC
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11 GTHESS11 1 | 1453 | 1600 | -147 | 91 | 1022 | AC
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1380 | 1600 | -220 | 86 | 986 | AC
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1358 | 1600 | -242 | 85 | 970 | AC
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1334 | 1600 | -266 | 83 | 952 | AC
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1328 | 1600 | -272 | 83 | 950 | AC
BG-CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1292 | 1600 | -308 | 81 | 924 | AC
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1238 | 1600 | -362 | 77 | 886 | AC
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1234 | 1600 | -366 | 77 | 882 | AC
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1209 | 1600 | -391 | 76 | 864 | AC
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1206 | 1600 | -394 | 75 | 863 | AC
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1196 | 1600 | -404 | 75 | 855 | AC
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1195 | 1600 | -405 | 75 | 855 | AC
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1188 | 1600 | -412 | 74 | 850 | AC
BG-CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1185 | 1600 | -415 | 74 | 848 | AC
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1183 | 1600 | -417 | 74 | 847 | AC
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 845 | AC
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1181 | 1600 | -419 | 74 | 845 | AC
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 845 | AC
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1180 | 1600 | -420 | 74 | 844 | AC
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 841 | AC
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1175 | 1600 | -425 | 73 | 840 | AC
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1600 | -426 | 73 | 840 | AC
Base case | Base case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1600 | -426 | 73 | 840 | AC
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1174 | 1600 | -426 | 73 | 840 | AC
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1169 | 1600 | -431 | 73 | 836 | AC
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1164 | 1600 | -436 | 73 | 833 | AC
BG-CO_00005 | N-1 OHL 400 kV Vetren - Chervena Mogila | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1600 | -437 | 73 | 832 | AC
BG-CO_00006 | N-1 OHL 400 kV Plovdiv - Vetren | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1163 | 1600 | -437 | 73 | 832 | AC
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1159 | 1600 | -441 | 72 | 829 | AC
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1149 | 1600 | -451 | 72 | 822 | AC
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1144 | 1600 | -456 | 72 | 819 | AC
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11 GMELIT11 1 | 1135 | 1600 | -465 | 71 | 812 | AC