## 0030
Detailed results
Generated at: | 20/04/2026 22:41:18
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3908
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Medgidia Sud - Rahman/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 26 | 33 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 59 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 4 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 14 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 18 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 29 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 38 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 15 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 27 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 31 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 10 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 17 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 13 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 9 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 12 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 18 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 10 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 44 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 14 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 20 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 15 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 25 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1995 | 2000 | -5 | 100 | 1392 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1987 | 2000 | -13 | 99 | 1389 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1983 | 2000 | -17 | 99 | 1397 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1974 | 2000 | -26 | 99 | 1387 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1969 | 2000 | -31 | 98 | 1380 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1963 | 2000 | -37 | 98 | 1375 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1962 | 2000 | -38 | 98 | 1374 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1956 | 2000 | -44 | 98 | 1371 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1952 | 2000 | -48 | 98 | 1352 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1952 | 2000 | -48 | 98 | -1324 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1950 | 2000 | -50 | 98 | 1367 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1947 | 2000 | -53 | 97 | 1364 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1946 | 2000 | -54 | 97 | 1364 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1944 | 2000 | -56 | 97 | 1362 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1937 | 2000 | -63 | 97 | 1344 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1937 | 2000 | -63 | 97 | -1311 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1927 | 2000 | -73 | 96 | 1350 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1912 | 2000 | -88 | 96 | 1344 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 922 | 999 | -77 | 92 | 358 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1744 | 2000 | -256 | 87 | 1202 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1735 | 2000 | -265 | 87 | 1196 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1412 | 1836 | -424 | 77 | 1010 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1412 | 1836 | -424 | 77 | 1010 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1836 | -444 | 76 | 995 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1836 | -444 | 76 | 995 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1359 | 1836 | -477 | 74 | 972 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1836 | -484 | 74 | 967 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1341 | 1836 | -495 | 73 | 959 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1331 | 1836 | -505 | 72 | 952 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1326 | 1836 | -510 | 72 | 949 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1319 | 1836 | -517 | 72 | 944 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1311 | 1836 | -525 | 71 | 938 | AC

## 0130
Detailed results
Generated at: | 20/04/2026 22:41:18
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3936
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Medgidia Sud - Rahman/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 26 | 40 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 59 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 14 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 18 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 29 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 38 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 15 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 28 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 32 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 10 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 17 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 13 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 9 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 12 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 18 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 10 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 44 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 14 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 20 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 15 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 25 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1391 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1987 | 2000 | -13 | 99 | 1389 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1982 | 2000 | -18 | 99 | 1396 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1976 | 2000 | -24 | 99 | -1339 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1976 | 2000 | -24 | 99 | 1369 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1973 | 2000 | -27 | 99 | 1385 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1962 | 2000 | -38 | 98 | 1374 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1961 | 2000 | -39 | 98 | -1327 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1961 | 2000 | -39 | 98 | 1361 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1955 | 2000 | -45 | 98 | 1369 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1955 | 2000 | -45 | 98 | 1368 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1950 | 2000 | -50 | 97 | 1365 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1944 | 2000 | -56 | 97 | 1362 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1943 | 2000 | -57 | 97 | 1361 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1943 | 2000 | -57 | 97 | 1361 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1942 | 2000 | -58 | 97 | 1360 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1920 | 2000 | -80 | 96 | 1344 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1918 | 2000 | -82 | 96 | 1348 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 930 | 999 | -69 | 93 | 362 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1735 | 2000 | -265 | 87 | 1194 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1725 | 2000 | -275 | 86 | 1188 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1385 | 1836 | -451 | 75 | 992 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1385 | 1836 | -451 | 75 | 992 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1364 | 1836 | -472 | 74 | 977 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1364 | 1836 | -472 | 74 | 977 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1317 | 1836 | -519 | 72 | 944 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1307 | 1836 | -529 | 71 | 936 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1300 | 1836 | -536 | 71 | 931 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1296 | 1836 | -540 | 71 | 929 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1296 | 1836 | -540 | 71 | 928 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1290 | 1836 | -546 | 70 | 924 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1288 | 1836 | -548 | 70 | 923 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1287 | 1836 | -549 | 70 | 922 | AC

## 0230
Detailed results
Generated at: | 20/04/2026 22:41:18
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3775
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA/[BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1794 | 2000 | -206 | 90 | 1255 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1792 | 2000 | -208 | 90 | -1226 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1792 | 2000 | -208 | 90 | 1251 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1789 | 2000 | -211 | 89 | 1253 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1784 | 2000 | -216 | 89 | 1260 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1778 | 2000 | -222 | 89 | 1243 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1778 | 2000 | -222 | 89 | -1215 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1774 | 2000 | -226 | 89 | 1249 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1754 | 2000 | -246 | 88 | 1231 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1094 | 1248 | -155 | 88 | 446 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1094 | 1248 | -155 | 88 | 446 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1751 | 2000 | -249 | 88 | 1230 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1751 | 2000 | -249 | 88 | 1228 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1748 | 2000 | -252 | 87 | 1227 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1091 | 1248 | -158 | 87 | 444 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1091 | 1248 | -158 | 87 | 444 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1745 | 2000 | -255 | 87 | 1225 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1743 | 2000 | -257 | 87 | 1223 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1087 | 1248 | -162 | 87 | 443 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1087 | 1248 | -162 | 87 | 443 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1741 | 2000 | -259 | 87 | 1222 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1738 | 2000 | -262 | 87 | 1220 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1735 | 2000 | -265 | 87 | 1218 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1734 | 2000 | -266 | 87 | 1223 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1428 | 1836 | -408 | 78 | 1023 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1428 | 1836 | -408 | 78 | 1023 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1552 | 2000 | -448 | 78 | 1071 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1543 | 2000 | -457 | 77 | 1066 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1403 | 1836 | -433 | 76 | 1005 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1391 | 1836 | -445 | 76 | 996 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1391 | 1836 | -445 | 76 | 996 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1346 | 1836 | -490 | 73 | 965 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1340 | 1836 | -496 | 73 | 960 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1336 | 1836 | -500 | 73 | 957 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 908 | 1248 | -340 | 73 | 369 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 908 | 1248 | -340 | 73 | 369 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1334 | 1836 | -502 | 73 | 956 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1333 | 1836 | -503 | 73 | 956 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1333 | 1836 | -503 | 73 | 955 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1330 | 1836 | -506 | 72 | 953 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1329 | 1836 | -507 | 72 | 952 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 521 | 721 | -200 | 72 | 366 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1322 | 1836 | -514 | 72 | 947 | AC

## 0330
Detailed results
Generated at: | 20/04/2026 22:41:18
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3887
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA/[BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 389 | 262 |  | 389 | 0 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 26 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 59 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 4 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 14 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 170 | 0 |  | 170 | 0 | FALSE | TRUE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 340 | 91 |  | 340 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 18 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 29 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 38 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 15 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 27 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 31 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 10 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 17 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 13 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 9 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 18 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 12 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 18 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 10 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 44 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 14 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 20 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 15 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 25 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-10) HigherStep(12.0)
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1994 | 2000 | -6 | 100 | 1383 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1994 | 2000 | -6 | 100 | -1353 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1988 | 2000 | -12 | 99 | 1388 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1980 | 2000 | -20 | 99 | 1386 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1978 | 2000 | -22 | 99 | 1374 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1978 | 2000 | -22 | 99 | -1340 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1977 | 2000 | -23 | 99 | 1394 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1966 | 2000 | -34 | 98 | 1382 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1952 | 2000 | -48 | 98 | 1369 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1946 | 2000 | -54 | 97 | 1364 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1941 | 2000 | -59 | 97 | 1360 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1940 | 2000 | -60 | 97 | 1359 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1935 | 2000 | -65 | 97 | 1356 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1934 | 2000 | -66 | 97 | 1356 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1933 | 2000 | -67 | 97 | 1355 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1932 | 2000 | -68 | 97 | 1354 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1922 | 2000 | -78 | 96 | 1353 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 959 | 999 | -40 | 96 | 375 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1907 | 2000 | -93 | 95 | 1337 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1722 | 2000 | -278 | 86 | 1186 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1711 | 2000 | -289 | 86 | 1180 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1319 | 1836 | -517 | 72 | 942 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1319 | 1836 | -517 | 72 | 942 | AC

## 0430
Detailed results
Generated at: | 20/04/2026 22:41:18
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3896
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Medgidia Sud - Rahman/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 59 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 8 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 2 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 14 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 340 | 235 |  | 340 | 0 | FALSE | FALSE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 0 | 118 |  | 118 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 18 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 29 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 38 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 15 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 28 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 32 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 10 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 17 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 13 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 9 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 12 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 18 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 10 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 44 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 14 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 20 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 15 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 25 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 0 | 222 |  | 222 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 0 | 20 |  | 20 | 0 | TRUE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 0 | 29 |  | 29 | 0 | TRUE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 0 | 27 |  | 27 | 0 | TRUE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 0 | 52 |  | 52 | 0 | TRUE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1994 | 2000 | -6 | 100 | 1383 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1994 | 2000 | -6 | 100 | -1353 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1989 | 2000 | -11 | 99 | 1389 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1980 | 2000 | -20 | 99 | 1386 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1979 | 2000 | -21 | 99 | 1395 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1979 | 2000 | -21 | 99 | 1374 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1979 | 2000 | -21 | 99 | -1340 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1966 | 2000 | -34 | 98 | 1382 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1954 | 2000 | -46 | 98 | 1370 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1946 | 2000 | -54 | 97 | 1364 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1942 | 2000 | -58 | 97 | 1361 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1941 | 2000 | -59 | 97 | 1360 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1940 | 2000 | -60 | 97 | 1360 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1940 | 2000 | -60 | 97 | 1360 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1939 | 2000 | -61 | 97 | 1359 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1935 | 2000 | -65 | 97 | 1356 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1913 | 2000 | -87 | 96 | 1346 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1904 | 2000 | -96 | 95 | 1334 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1723 | 2000 | -277 | 86 | 1188 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1713 | 2000 | -287 | 86 | 1182 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 794 | 999 | -205 | 79 | 309 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1836 | -475 | 74 | 974 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1361 | 1836 | -475 | 74 | 974 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1320 | 1836 | -516 | 72 | 942 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1320 | 1836 | -516 | 72 | 942 | AC

## 0530
Detailed results
Generated at: | 20/04/2026 22:41:18
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3663
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Medgidia Sud - Rahman/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 63 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 7 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 2 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 14 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 28 | 27 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 17 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 13 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 9 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 17 | 49 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 18 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 12 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 6 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 6 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 18 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 137 | 0 |  | 137 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 10 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 5 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 44 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 14 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 20 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 15 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 25 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 4 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 6 | 29 |  | 29 | 0 | FALSE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 5 | 27 |  | 27 | 0 | FALSE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 9 | 52 |  | 52 | 0 | FALSE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1993 | 2000 | -7 | 100 | 1391 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1984 | 2000 | -16 | 99 | 1388 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1983 | 2000 | -17 | 99 | 1397 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1971 | 2000 | -29 | 99 | 1385 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1969 | 2000 | -31 | 98 | 1379 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1961 | 2000 | -39 | 98 | 1374 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1960 | 2000 | -40 | 98 | -1332 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1960 | 2000 | -40 | 98 | 1361 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1959 | 2000 | -41 | 98 | 1372 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1955 | 2000 | -45 | 98 | 1369 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1951 | 2000 | -49 | 98 | 1367 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1950 | 2000 | -50 | 98 | 1367 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1949 | 2000 | -51 | 97 | 1365 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1948 | 2000 | -52 | 97 | 1365 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1946 | 2000 | -54 | 97 | 1353 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1946 | 2000 | -54 | 97 | -1319 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1920 | 2000 | -80 | 96 | 1345 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1910 | 2000 | -90 | 96 | 1342 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1741 | 2000 | -259 | 87 | 1201 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1730 | 2000 | -270 | 87 | 1195 | AC
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 843 | 999 | -156 | 84 | 328 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 837 | 999 | -162 | 84 | 326 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 812 | 999 | -187 | 81 | 316 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 793 | 999 | -207 | 79 | 309 | AC

## 0630
Detailed results
Generated at: | 20/04/2026 22:41:19
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3515.51
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00042 | N-1 OHL 400 kV Arefu-Tantareni | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 841 | 999 | -158 | 84 | 328 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1047 | 1248 | -201 | 84 | 426 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1047 | 1248 | -201 | 84 | 426 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 836 | 999 | -163 | 84 | 326 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1044 | 1248 | -204 | 84 | 425 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1044 | 1248 | -204 | 84 | 425 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1667 | 2000 | -333 | 83 | 1169 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1040 | 1248 | -208 | 83 | 424 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1040 | 1248 | -208 | 83 | 424 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1653 | 2000 | -347 | 83 | 1160 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1626 | 2000 | -374 | 81 | 1141 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1620 | 2000 | -380 | 81 | 1132 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1620 | 2000 | -380 | 81 | 1136 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1479 | 1836 | -357 | 81 | 1057 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1479 | 1836 | -357 | 81 | 1057 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1607 | 2000 | -393 | 80 | 1127 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1604 | 2000 | -396 | 80 | 1126 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1603 | 2000 | -397 | 80 | 1124 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1601 | 2000 | -399 | 80 | 1117 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1598 | 2000 | -402 | 80 | 1121 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1463 | 1836 | -373 | 80 | 1046 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1591 | 2000 | -409 | 80 | 1112 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1585 | 2000 | -415 | 79 | 1120 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1580 | 2000 | -420 | 79 | 1111 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1450 | 1836 | -386 | 79 | 1035 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1450 | 1836 | -386 | 79 | 1035 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1578 | 2000 | -422 | 79 | 1106 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1576 | 2000 | -424 | 79 | 1104 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1576 | 2000 | -424 | 79 | 1104 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1575 | 2000 | -425 | 79 | 1104 | AC
Base case | Base case | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1574 | 2000 | -426 | 79 | -1084 | AC
Base case | Base case | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1574 | 2000 | -426 | 79 | 1103 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 779 | 999 | -220 | 78 | 303 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1535 | 2000 | -465 | 77 | 1080 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1836 | -432 | 76 | 1004 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1399 | 1836 | -437 | 76 | 1000 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1836 | -448 | 76 | 992 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1836 | -448 | 76 | 992 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1386 | 1836 | -450 | 75 | 991 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1384 | 1836 | -452 | 75 | 990 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1836 | -454 | 75 | 989 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1372 | 1836 | -464 | 75 | 981 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 906 | 1248 | -342 | 73 | 368 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 906 | 1248 | -342 | 73 | 368 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 520 | 721 | -201 | 72 | 366 | AC

## 0730
Detailed results
Generated at: | 20/04/2026 22:41:19
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Fallback
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type

## 0830
Detailed results
Generated at: | 20/04/2026 22:41:19
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Fallback
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type

## 0930
Detailed results
Generated at: | 20/04/2026 22:41:19
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 523
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00105 | RO | RROVI31 _generator | 0 | 310 |  |  | 310 | 1 |  | 310 | 1 | FALSE | FALSE
RO_RA_00108 | RO | RTURC51 _generator | 0 | 300 |  |  | 300 | 1 |  | 300 | 1 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 389 | 0 |  | 389 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 6 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 0 | 14 |  | 14 | 0 | TRUE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 0 | 15 |  | 15 | 0 | TRUE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 0 | 10 |  | 10 | 0 | TRUE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 0 | 10 |  | 10 | 0 | TRUE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 0 | 15 |  | 15 | 0 | TRUE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 0 | 12 |  | 12 | 0 | TRUE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 14 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 170 | 0 |  | 170 | 0 | FALSE | TRUE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 67 | 47 |  | 118 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 27 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 21 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 21 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 7 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 16 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 12 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 8 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 7 | 59 |  | 59 | 0 | FALSE | FALSE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 3 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 11 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 18 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 11 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 0 | 137 |  | 137 | 0 | TRUE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 0 | 32 |  | 32 | 0 | TRUE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 0 | 67 |  | 67 | 0 | TRUE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 0 | 9 |  | 9 | 0 | TRUE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 0 | 23 |  | 23 | 0 | TRUE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 0 | 24 |  | 24 | 0 | TRUE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 0 | 13 |  | 13 | 0 | TRUE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 2 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 1 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 1 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 21 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 4 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 6 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 8 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 4 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 29 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 10 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 9 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 15 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 876 | 1248 | -373 | 70 | 358 | AC

## 1030
Detailed results
Generated at: | 20/04/2026 22:41:19
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 738.47
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1244 | 1248 | -4 | 100 | 509 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1212 | 1248 | -37 | 97 | 493 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1200 | 1248 | -48 | 96 | 491 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1103 | 1248 | -145 | 88 | 448 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 541 | 721 | -180 | 75 | 379 | AC

## 1130
Detailed results
Generated at: | 20/04/2026 22:41:19
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 806.39
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1242 | 1248 | -6 | 100 | 506 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1195 | 1248 | -53 | 96 | 487 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1173 | 1248 | -76 | 94 | 478 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1042 | 1248 | -206 | 84 | 424 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 904 | 1248 | -344 | 72 | 367 | AC

## 1230
Detailed results
Generated at: | 20/04/2026 22:41:19
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 1020
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00108 | RO | RTURC51 _generator | 0 | 300 |  |  | 300 | 1 |  | 300 | 1 | FALSE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 181 | 106 |  | 389 | 0 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 0 | 50 |  | 50 | 0 | TRUE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 0 | 114 |  | 114 | 0 | TRUE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 8 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 1 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 1 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 1 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 14 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 170 | 131 |  | 170 | 0 | FALSE | FALSE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 222 | 340 |  | 340 | 0 | FALSE | FALSE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 0 | 118 |  | 118 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 27 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 21 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 21 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 7 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 16 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 12 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 8 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 17 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 7 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 3 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 14 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 23 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 11 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 20 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 4 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 6 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 9 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 4 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 111 | 150 |  | 150 | 0 | FALSE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 30 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 64 | 0 |  | 96 | 0 | FALSE | TRUE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 41 | 0 |  | 58 | 0 | FALSE | TRUE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 147 | 222 |  | 222 | 0 | FALSE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 7 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 10 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 9 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 15 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1248 | 1248 | -1 | 100 | 509 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1146 | 1248 | -103 | 92 | 466 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1133 | 1248 | -115 | 91 | 461 | AC
Base case | Base case | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 925 | 1248 | -323 | 74 | 375 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 894 | 1248 | -355 | 72 | 362 | AC

## 1330
Detailed results
Generated at: | 20/04/2026 22:41:19
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 1551
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 369 | 0 |  | 389 | 0 | FALSE | TRUE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 0 | 50 |  | 50 | 0 | TRUE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 9 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 14 |  | 14 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 14 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 170 | 0 |  | 170 | 0 | FALSE | TRUE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 340 | 0 |  | 340 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 27 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 21 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 21 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 7 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 16 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 12 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 8 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 8 | 59 |  | 59 | 0 | FALSE | FALSE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 4 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 15 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 24 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 13 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 0 | 79 |  | 137 | 0 | TRUE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 0 | 32 |  | 32 | 0 | TRUE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 0 | 67 |  | 67 | 0 | TRUE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 0 | 9 |  | 9 | 0 | TRUE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 0 | 23 |  | 23 | 0 | TRUE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 0 | 24 |  | 24 | 0 | TRUE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 0 | 13 |  | 13 | 0 | TRUE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 2 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 1 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 1 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 23 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 6 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 8 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 11 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 6 | 34 |  | 34 | 0 | FALSE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 150 | 0 |  | 150 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 30 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 96 | 0 |  | 96 | 0 | FALSE | TRUE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 58 | 0 |  | 58 | 0 | FALSE | TRUE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 222 | 0 |  | 222 | 0 | FALSE | TRUE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 10 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 9 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 15 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1015 | 1248 | -234 | 81 | 413 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 984 | 1248 | -264 | 79 | 399 | AC

## 1430
Detailed results
Generated at: | 20/04/2026 22:41:19
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 1762
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 389 | 0 |  | 389 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 8 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 14 |  | 14 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 14 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 170 | 0 |  | 170 | 0 | FALSE | TRUE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 340 | 114 |  | 340 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 13 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 21 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 13 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 27 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 11 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 21 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 11 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 21 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 20 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 23 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 7 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 16 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 12 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 8 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 17 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 8 | 59 |  | 59 | 0 | FALSE | FALSE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 4 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 14 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 23 | 49 |  | 49 | 0 | FALSE | FALSE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 13 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 0 | 137 |  | 137 | 0 | TRUE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 0 | 32 |  | 32 | 0 | TRUE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 0 | 67 |  | 67 | 0 | TRUE | FALSE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 0 | 9 |  | 9 | 0 | TRUE | FALSE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 0 | 23 |  | 23 | 0 | TRUE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 0 | 24 |  | 24 | 0 | TRUE | FALSE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 0 | 13 |  | 13 | 0 | TRUE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 2 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 1 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 1 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 23 | 98 |  | 98 | 0 | FALSE | FALSE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 6 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 8 | 44 |  | 44 | 0 | FALSE | FALSE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 11 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 6 | 34 |  | 34 | 0 | FALSE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 150 | 0 |  | 150 | 0 | FALSE | TRUE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 150 | 0 |  | 150 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 30 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 96 | 0 |  | 96 | 0 | FALSE | TRUE
RO_RA_00179 | RO | RMUNT_5 _generator | 0 | 58 |  |  | 58 | 0 |  | 58 | 0 | FALSE | TRUE
RO_RA_00180 | RO | RRETE22 _generator | 0 | 222 |  |  | 222 | 0 |  | 222 | 0 | FALSE | TRUE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 7 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 10 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 9 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 15 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1032 | 1248 | -216 | 83 | 421 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 987 | 1248 | -261 | 79 | 402 | AC

## 1530
Detailed results
Generated at: | 20/04/2026 22:41:19
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 2024
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT3 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 389 | 336 |  | 389 | 0 | FALSE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 0 | 50 |  | 50 | 0 | TRUE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 0 | 114 |  | 114 | 0 | TRUE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 6 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 12 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 11 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 19 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 24 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 10 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 19 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 10 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 19 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 18 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 20 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 7 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 15 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 11 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 8 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 15 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 15 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 15 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 15 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 16 | 38 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 11 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 13 | 32 |  | 32 | 0 | FALSE | FALSE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 19 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 54 |  | 54 | 0 | FALSE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 1 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 20 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 5 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 7 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 9 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 6 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 150 | 0 |  | 150 | 0 | FALSE | TRUE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 150 | 0 |  | 150 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 26 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00178 | RO | RREME_5 _generator | 0 | 96 |  |  | 96 | 0 |  | 96 | 0 | FALSE | TRUE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 9 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 8 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 13 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1248 | 1248 | -1 | 100 | 510 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1245 | 1248 | -4 | 100 | 508 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1134 | 1248 | -115 | 91 | 462 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 955 | 1248 | -293 | 77 | 389 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 949 | 1248 | -299 | 76 | 387 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 919 | 1248 | -329 | 74 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 913 | 1248 | -335 | 73 | 372 | AC

## 1630
Detailed results
Generated at: | 20/04/2026 22:41:20
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3582
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1828 | 2000 | -172 | 91 | 1289 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 903 | 999 | -96 | 90 | 352 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1793 | 2000 | -207 | 90 | 1264 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1780 | 2000 | -220 | 89 | 1254 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1773 | 2000 | -227 | 89 | 1250 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1759 | 2000 | -241 | 88 | 1239 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1752 | 2000 | -248 | 88 | 1235 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1738 | 2000 | -262 | 87 | 1224 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 868 | 999 | -131 | 87 | 339 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1594 | 1836 | -242 | 87 | 1137 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1594 | 1836 | -242 | 87 | 1137 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1732 | 2000 | -268 | 87 | 1220 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1725 | 2000 | -275 | 86 | 1215 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1583 | 1836 | -253 | 86 | 1130 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1582 | 1836 | -254 | 86 | 1130 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1582 | 1836 | -254 | 86 | 1130 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1070 | 1248 | -179 | 86 | 436 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1070 | 1248 | -179 | 86 | 436 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1067 | 1248 | -182 | 85 | 435 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1067 | 1248 | -182 | 85 | 435 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1569 | 1836 | -267 | 85 | 1119 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1063 | 1248 | -186 | 85 | 433 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1063 | 1248 | -186 | 85 | 433 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1696 | 2000 | -304 | 85 | 1190 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1683 | 2000 | -317 | 84 | 1182 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1678 | 2000 | -322 | 84 | 1190 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1677 | 2000 | -323 | 84 | 1184 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1532 | 1836 | -304 | 83 | 1094 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1517 | 1836 | -319 | 83 | 1084 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1516 | 1836 | -320 | 83 | 1084 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1498 | 1836 | -338 | 82 | 1070 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1836 | -342 | 81 | 1068 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1490 | 1836 | -346 | 81 | 1065 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1486 | 1836 | -350 | 81 | 1062 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1538 | 2000 | -462 | 77 | 1086 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 934 | 1248 | -314 | 75 | 380 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 934 | 1248 | -314 | 75 | 380 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 536 | 721 | -185 | 74 | 377 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1428 | 2000 | -572 | 71 | 1006 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1426 | 2000 | -574 | 71 | 1005 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1416 | 2000 | -584 | 71 | 997 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1416 | 2000 | -584 | 71 | 997 | AC
Base case | Base case | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1413 | 2000 | -587 | 71 | 995 | AC
Base case | Base case | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1413 | 2000 | -587 | 71 | -980 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1407 | 2000 | -593 | 70 | 988 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1402 | 2000 | -598 | 70 | 985 | AC

## 1730
Detailed results
Generated at: | 20/04/2026 22:41:20
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3500
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1957 | 2000 | -43 | 98 | 1380 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1920 | 2000 | -80 | 96 | 1354 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1917 | 2000 | -83 | 96 | 1352 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1914 | 2000 | -86 | 96 | 1348 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1913 | 2000 | -87 | 96 | 1348 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1894 | 2000 | -106 | 95 | 1335 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1858 | 2000 | -142 | 93 | 1305 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1857 | 2000 | -143 | 93 | 1307 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1850 | 2000 | -150 | 93 | 1304 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1847 | 2000 | -153 | 92 | 1298 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1842 | 2000 | -158 | 92 | 1305 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1842 | 2000 | -158 | 92 | 1298 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1840 | 2000 | -160 | 92 | 1299 | AC
RO_CO_00004 | N-1 OHL 400 kV Arefu-Sibiu Sud | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 879 | 999 | -120 | 88 | 343 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1739 | 2000 | -261 | 87 | 1212 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1733 | 2000 | -267 | 87 | 1209 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1726 | 2000 | -274 | 86 | 1219 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1060 | 1248 | -189 | 85 | 432 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1060 | 1248 | -189 | 85 | 432 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1057 | 1248 | -191 | 85 | 430 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1057 | 1248 | -191 | 85 | 430 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1053 | 1248 | -195 | 84 | 429 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1053 | 1248 | -195 | 84 | 429 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 843 | 999 | -156 | 84 | 329 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1372 | 1836 | -464 | 75 | 980 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1372 | 1836 | -464 | 75 | 980 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1372 | 1836 | -464 | 75 | 981 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1369 | 1836 | -467 | 75 | 979 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1369 | 1836 | -467 | 75 | 979 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1481 | 2000 | -519 | 74 | -1021 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1481 | 2000 | -519 | 74 | 1038 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1354 | 1836 | -482 | 74 | 968 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1472 | 2000 | -528 | 74 | -1014 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1472 | 2000 | -528 | 74 | 1033 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 913 | 1248 | -335 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 913 | 1248 | -335 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 524 | 721 | -197 | 73 | 369 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1317 | 1836 | -519 | 72 | 942 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1312 | 1836 | -524 | 71 | 939 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1292 | 1836 | -544 | 70 | 925 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1291 | 1836 | -545 | 70 | 923 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1290 | 1836 | -546 | 70 | 923 | AC

## 1830
Detailed results
Generated at: | 20/04/2026 22:41:20
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3242
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1940 | 2000 | -60 | 97 | 1366 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1899 | 2000 | -101 | 95 | 1337 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1897 | 2000 | -103 | 95 | 1336 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1894 | 2000 | -106 | 95 | 1333 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1885 | 2000 | -115 | 94 | 1327 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1872 | 2000 | -128 | 94 | 1318 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1844 | 2000 | -156 | 92 | 1298 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1840 | 2000 | -160 | 92 | 1295 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1835 | 2000 | -165 | 92 | 1291 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1812 | 2000 | -188 | 91 | 1271 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1797 | 2000 | -203 | 90 | 1262 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1794 | 2000 | -206 | 90 | 1270 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1792 | 2000 | -208 | 90 | 1264 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1731 | 2000 | -269 | 87 | 1205 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1725 | 2000 | -275 | 86 | 1203 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1644 | 2000 | -356 | 82 | 1161 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1017 | 1248 | -231 | 81 | 415 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1017 | 1248 | -231 | 81 | 415 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1015 | 1248 | -234 | 81 | 414 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1015 | 1248 | -234 | 81 | 414 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1011 | 1248 | -238 | 81 | 412 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1011 | 1248 | -238 | 81 | 412 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1389 | 1836 | -447 | 76 | 992 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1371 | 1836 | -465 | 75 | 980 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1370 | 1836 | -466 | 75 | 979 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1370 | 1836 | -466 | 75 | 979 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 745 | 999 | -254 | 75 | 290 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1353 | 1836 | -483 | 74 | 968 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1353 | 1836 | -483 | 74 | 968 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 733 | 999 | -266 | 73 | 272 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 915 | 1248 | -333 | 73 | 373 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 915 | 1248 | -333 | 73 | 373 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 909 | 1248 | -339 | 73 | 370 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1333 | 1836 | -503 | 73 | 953 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1322 | 1836 | -514 | 72 | 945 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1321 | 1836 | -515 | 72 | 944 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1317 | 1836 | -519 | 72 | 942 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1313 | 1836 | -523 | 72 | 939 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1312 | 1836 | -524 | 71 | 938 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1309 | 1836 | -527 | 71 | 936 | AC

## 1930
Detailed results
Generated at: | 20/04/2026 22:41:20
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3190
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1925 | 2000 | -75 | 96 | 1353 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1883 | 2000 | -117 | 94 | 1323 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1878 | 2000 | -122 | 94 | 1320 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1877 | 2000 | -123 | 94 | 1319 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1866 | 2000 | -134 | 93 | 1311 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1853 | 2000 | -147 | 93 | 1302 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1829 | 2000 | -171 | 91 | 1284 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1824 | 2000 | -176 | 91 | 1281 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1818 | 2000 | -182 | 91 | 1277 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1787 | 2000 | -213 | 89 | 1251 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1770 | 2000 | -230 | 89 | 1241 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1767 | 2000 | -233 | 88 | 1250 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1766 | 2000 | -234 | 88 | 1243 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1719 | 2000 | -281 | 86 | 1194 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1714 | 2000 | -286 | 86 | 1191 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1013 | 1248 | -235 | 81 | 414 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1013 | 1248 | -235 | 81 | 414 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1011 | 1248 | -238 | 81 | 413 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1011 | 1248 | -238 | 81 | 413 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1007 | 1248 | -242 | 81 | 411 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1007 | 1248 | -242 | 81 | 411 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1613 | 2000 | -387 | 81 | 1138 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 767 | 999 | -232 | 77 | 299 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1406 | 1836 | -430 | 77 | 995 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1391 | 1836 | -445 | 76 | 986 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1836 | -454 | 75 | 980 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1836 | -454 | 75 | 980 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 752 | 999 | -247 | 75 | 272 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1367 | 1836 | -469 | 74 | 967 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1367 | 1836 | -469 | 74 | 967 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1351 | 1836 | -485 | 74 | 957 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 915 | 1248 | -333 | 73 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 915 | 1248 | -333 | 73 | 374 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1341 | 1836 | -495 | 73 | 949 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1339 | 1836 | -497 | 73 | 948 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 909 | 1248 | -339 | 73 | 371 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1332 | 1836 | -504 | 73 | 943 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1329 | 1836 | -507 | 72 | 941 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1329 | 1836 | -507 | 72 | 941 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1324 | 1836 | -512 | 72 | 937 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1298 | 1836 | -538 | 71 | 919 | AC

## 2030
Detailed results
Generated at: | 20/04/2026 22:41:20
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3226
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1922 | 2000 | -78 | 96 | 1350 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1888 | 2000 | -112 | 94 | 1326 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1881 | 2000 | -119 | 94 | 1322 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1880 | 2000 | -120 | 94 | 1320 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1871 | 2000 | -129 | 94 | 1315 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1859 | 2000 | -141 | 93 | 1305 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1835 | 2000 | -165 | 92 | 1288 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1829 | 2000 | -171 | 91 | 1284 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1823 | 2000 | -177 | 91 | 1280 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1797 | 2000 | -203 | 90 | 1257 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1780 | 2000 | -220 | 89 | 1248 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1777 | 2000 | -223 | 89 | 1256 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1775 | 2000 | -225 | 89 | 1249 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1721 | 2000 | -279 | 86 | 1195 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1716 | 2000 | -284 | 86 | 1192 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1631 | 2000 | -369 | 82 | 1150 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1001 | 1248 | -248 | 80 | 409 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1001 | 1248 | -248 | 80 | 409 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 998 | 1248 | -251 | 80 | 408 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 998 | 1248 | -251 | 80 | 408 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 994 | 1248 | -254 | 80 | 406 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 994 | 1248 | -254 | 80 | 406 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1405 | 1836 | -431 | 77 | 995 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 763 | 999 | -236 | 76 | 277 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 760 | 999 | -240 | 76 | 296 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1386 | 1836 | -450 | 75 | 983 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1836 | -454 | 75 | 980 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1836 | -454 | 75 | 980 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1836 | -468 | 74 | 968 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1836 | -468 | 74 | 968 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1836 | -484 | 74 | 956 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1341 | 1836 | -495 | 73 | 948 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1340 | 1836 | -496 | 73 | 948 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1334 | 1836 | -502 | 73 | 944 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 906 | 1248 | -343 | 73 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 906 | 1248 | -343 | 73 | 370 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1330 | 1836 | -506 | 72 | 941 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1330 | 1836 | -506 | 72 | 940 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1326 | 1836 | -510 | 72 | 938 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 900 | 1248 | -349 | 72 | 368 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1299 | 1836 | -537 | 71 | 918 | AC

## 2130
Detailed results
Generated at: | 20/04/2026 22:41:20
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3064
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1982 | 2000 | -18 | 99 | 1395 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1945 | 2000 | -55 | 97 | 1369 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1940 | 2000 | -60 | 97 | 1366 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1936 | 2000 | -64 | 97 | 1363 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1928 | 2000 | -72 | 96 | 1358 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1914 | 2000 | -86 | 96 | 1348 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1756 | 1836 | -80 | 96 | 1255 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1879 | 2000 | -121 | 94 | 1323 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1875 | 2000 | -125 | 94 | 1320 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1869 | 2000 | -131 | 93 | 1316 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1844 | 2000 | -156 | 92 | 1294 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1688 | 1836 | -148 | 92 | 1204 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1826 | 2000 | -174 | 91 | 1284 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1825 | 2000 | -175 | 91 | 1292 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1822 | 2000 | -178 | 91 | 1285 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1783 | 2000 | -217 | 89 | 1241 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1778 | 2000 | -222 | 89 | 1238 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1049 | 1248 | -200 | 84 | 427 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1049 | 1248 | -200 | 84 | 427 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1046 | 1248 | -202 | 84 | 426 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1046 | 1248 | -202 | 84 | 426 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1042 | 1248 | -206 | 83 | 424 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1042 | 1248 | -206 | 83 | 424 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1666 | 2000 | -334 | 83 | 1178 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1502 | 1836 | -334 | 82 | 1071 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1482 | 1836 | -354 | 81 | 1058 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1461 | 1836 | -375 | 80 | 1043 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1454 | 1836 | -382 | 79 | 1038 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1433 | 1836 | -403 | 78 | 1023 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1428 | 1836 | -408 | 78 | 1021 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1425 | 1836 | -411 | 78 | 1018 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1416 | 1836 | -420 | 77 | 1012 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1415 | 1836 | -421 | 77 | 1011 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1397 | 1836 | -439 | 76 | 998 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 912 | 1248 | -337 | 73 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 912 | 1248 | -337 | 73 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 523 | 721 | -198 | 73 | 368 | AC

## 2230
Detailed results
Generated at: | 20/04/2026 22:41:21
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3507.37
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1829 | 1836 | -7 | 100 | 1304 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1816 | 1836 | -20 | 99 | 1297 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1945 | 2000 | -55 | 97 | 1365 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1927 | 2000 | -73 | 96 | 1352 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1921 | 2000 | -79 | 96 | 1349 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1918 | 2000 | -82 | 96 | 1346 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1909 | 2000 | -91 | 95 | 1340 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1906 | 2000 | -94 | 95 | 1331 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1904 | 2000 | -96 | 95 | 1336 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1893 | 2000 | -107 | 95 | 1325 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1890 | 2000 | -110 | 94 | 1333 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1883 | 2000 | -117 | 94 | 1321 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1882 | 2000 | -118 | 94 | 1323 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1877 | 2000 | -123 | 94 | 1317 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1871 | 2000 | -129 | 94 | 1313 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1788 | 2000 | -212 | 89 | 1256 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1736 | 2000 | -264 | 87 | 1202 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1080 | 1248 | -168 | 87 | 440 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1080 | 1248 | -168 | 87 | 440 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1728 | 2000 | -272 | 86 | 1197 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1077 | 1248 | -171 | 86 | 439 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1077 | 1248 | -171 | 86 | 439 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1073 | 1248 | -175 | 86 | 437 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1073 | 1248 | -175 | 86 | 437 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1684 | 2000 | -316 | 84 | -1150 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1684 | 2000 | -316 | 84 | 1172 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1537 | 1836 | -299 | 84 | 1098 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1672 | 2000 | -328 | 84 | 1165 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1672 | 2000 | -328 | 84 | -1140 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1512 | 1836 | -324 | 82 | 1079 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1511 | 1836 | -325 | 82 | 1079 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1495 | 1836 | -341 | 81 | 1068 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1495 | 1836 | -341 | 81 | 1068 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1836 | -342 | 81 | 1068 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1836 | -360 | 80 | 1055 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1475 | 1836 | -361 | 80 | 1054 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1836 | -370 | 80 | 1047 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1836 | -370 | 80 | 1047 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 906 | 1248 | -342 | 73 | 368 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 906 | 1248 | -342 | 73 | 368 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 520 | 721 | -201 | 72 | 366 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1355 | 1890 | -535 | 72 | -947 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1355 | 1920 | -565 | 71 | 968 | AC

## 2330
Detailed results
Generated at: | 20/04/2026 22:41:21
Business day: | 2026-04-22
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | South-Romania Exporting
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3659
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei/[RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 22 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 50 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 8 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 2 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 12 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 15 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 25 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 16 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 32 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 12 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 26 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 13 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 26 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 24 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 27 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 9 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 14 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 7 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 15 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 15 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 15 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 15 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 15 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 10 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 5 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 5 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 5 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 16 | 7 |  | 54 | 0 | FALSE | FALSE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 0 | 137 |  | 137 | 0 | TRUE | FALSE
RO_RA_00159 | RO | RSTEJ25 _generator | 0 | 32 |  |  | 0 | 32 |  | 32 | 0 | TRUE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 0 | 24 |  | 67 | 0 | TRUE | FALSE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 40 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 18 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 25 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 23 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 20 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 21 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00177 | RO | RIAZUA5 _generator | 0 | 71 |  |  | 0 | 71 |  | 71 | 0 | TRUE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 20 |  | 20 | 0 | FALSE | FALSE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 9 | 29 |  | 29 | 0 | FALSE | FALSE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 8 | 27 |  | 27 | 0 | FALSE | FALSE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 13 | 52 |  | 52 | 0 | FALSE | FALSE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1997 | 2000 | -3 | 100 | 1398 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1994 | 2000 | -6 | 100 | 1390 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1986 | 2000 | -14 | 99 | 1390 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1986 | 2000 | -14 | 99 | 1391 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1982 | 2000 | -18 | 99 | 1385 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1982 | 2000 | -18 | 99 | 1396 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1980 | 2000 | -20 | 99 | 1385 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1971 | 2000 | -29 | 99 | 1380 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1970 | 2000 | -30 | 98 | 1383 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1968 | 2000 | -32 | 98 | 1378 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1968 | 2000 | -32 | 98 | 1378 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1965 | 2000 | -35 | 98 | 1376 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1935 | 2000 | -65 | 97 | 1354 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1885 | 2000 | -115 | 94 | 1322 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1879 | 2000 | -121 | 94 | -1275 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1879 | 2000 | -121 | 94 | 1302 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1772 | 2000 | -228 | 89 | 1222 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1763 | 2000 | -237 | 88 | 1216 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [OPP] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 783 | 999 | -216 | 78 | 305 | AC