## 1230Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 12:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3284
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1883 | 1890 | 1890 | -7 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1883 | 1890 | 1890 | -7 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1611 | 1836 | 1836 | -225 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1611 | 1836 | 1836 | -225 | 88 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1513 | 1836 | 1836 | -323 | 82 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1476 | 1836 | 1836 | -360 | 80 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 | 1836 | 1836 | -361 | 80 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 | 1836 | 1836 | -361 | 80 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 | 1836 | 1836 | -367 | 80 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1447 | 1836 | 1836 | -389 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1447 | 1836 | 1836 | -389 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 | 1836 | 1836 | -427 | 77 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1448 | 1890 | 1890 | -442 | 77 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1448 | 1890 | 1890 | -442 | 77 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1392 | 1836 | 1836 | -444 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1441 | 1920 | 1920 | -479 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1441 | 1920 | 1920 | -479 | 75 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1371 | 1836 | 1836 | -465 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1399 | 1890 | 1890 | -491 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1399 | 1890 | 1890 | -491 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1392 | 1920 | 1920 | -528 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1392 | 1920 | 1920 | -528 | 72 | []

## 1230Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 12:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3284
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1883 |  | 1890 | -7 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1883 |  | 1890 | -7 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 |  | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 |  | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1611 |  | 1836 | -225 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1611 |  | 1836 | -225 | 88 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1513 |  | 1836 | -323 | 82 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1476 |  | 1836 | -360 | 80 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 |  | 1836 | -361 | 80 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 |  | 1836 | -361 | 80 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 |  | 1836 | -367 | 80 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1447 |  | 1836 | -389 | 79 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1447 |  | 1836 | -389 | 79 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 |  | 1836 | -427 | 77 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1448 |  | 1890 | -442 | 77 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1448 |  | 1890 | -442 | 77 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1392 |  | 1836 | -444 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1441 |  | 1920 | -479 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1441 |  | 1920 | -479 | 75 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1371 |  | 1836 | -465 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1399 |  | 1890 | -491 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1399 |  | 1890 | -491 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1392 |  | 1920 | -528 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1392 |  | 1920 | -528 | 72 | []

## 1330Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 13:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3566
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1825 | 1836 | 1836 | -11 | 99 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1825 | 1836 | 1836 | -11 | 99 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1870 | 1890 | 1890 | -20 | 99 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1870 | 1890 | 1890 | -20 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1859 | 1920 | 1920 | -61 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1859 | 1920 | 1920 | -61 | 97 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1712 | 1836 | 1836 | -124 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1703 | 1836 | 1836 | -133 | 93 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1697 | 1836 | 1836 | -139 | 92 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1697 | 1836 | 1836 | -139 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1684 | 1836 | 1836 | -152 | 92 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1683 | 1836 | 1836 | -153 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1662 | 1836 | 1836 | -174 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1662 | 1836 | 1836 | -174 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1633 | 1836 | 1836 | -203 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1615 | 1836 | 1836 | -221 | 88 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1612 | 1836 | 1836 | -224 | 88 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT3 Arad | RARA4D1 _RARAD22 _3:trf | -874 | -999 | -999 | -125 | 87 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1540 | 1836 | 1836 | -296 | 84 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1459 | 1890 | 1890 | -431 | 77 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1459 | 1890 | 1890 | -431 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1453 | 1920 | 1920 | -467 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1453 | 1920 | 1920 | -467 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1407 | 1890 | 1890 | -483 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1407 | 1890 | 1890 | -483 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1401 | 1920 | 1920 | -519 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1401 | 1920 | 1920 | -519 | 73 | []

## 1330Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 13:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3566
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1825 |  | 1836 | -11 | 99 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1825 |  | 1836 | -11 | 99 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1870 |  | 1890 | -20 | 99 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1870 |  | 1890 | -20 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1859 |  | 1920 | -61 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1859 |  | 1920 | -61 | 97 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1712 |  | 1836 | -124 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1703 |  | 1836 | -133 | 93 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1697 |  | 1836 | -139 | 92 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1697 |  | 1836 | -139 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1684 |  | 1836 | -152 | 92 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1683 |  | 1836 | -153 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1662 |  | 1836 | -174 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1662 |  | 1836 | -174 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1633 |  | 1836 | -203 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1615 |  | 1836 | -221 | 88 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1612 |  | 1836 | -224 | 88 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT3 Arad | RARA4D1 _RARAD22 _3:trf | -874 |  | -999 | -125 | 87 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1540 |  | 1836 | -296 | 84 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1459 |  | 1890 | -431 | 77 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1459 |  | 1890 | -431 | 77 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1453 |  | 1920 | -467 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1453 |  | 1920 | -467 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1407 |  | 1890 | -483 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1407 |  | 1890 | -483 | 74 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1401 |  | 1920 | -519 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1401 |  | 1920 | -519 | 73 | []

## 1430Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 14:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3349
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1884 | 1890 | 1890 | -6 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1884 | 1890 | 1890 | -6 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 | 1920 | 1920 | -48 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 | 1920 | 1920 | -48 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1678 | 1836 | 1836 | -158 | 91 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1678 | 1836 | 1836 | -158 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1603 | 1836 | 1836 | -233 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1547 | 1836 | 1836 | -289 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1547 | 1836 | 1836 | -289 | 84 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1546 | 1836 | 1836 | -290 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1538 | 1836 | 1836 | -298 | 84 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1515 | 1836 | 1836 | -321 | 83 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1515 | 1836 | 1836 | -321 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 | 1836 | 1836 | -364 | 80 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 | 1836 | 1836 | -375 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1438 | 1836 | 1836 | -398 | 78 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1448 | 1890 | 1890 | -442 | 77 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1448 | 1890 | 1890 | -442 | 77 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1381 | 1836 | 1836 | -455 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1441 | 1920 | 1920 | -479 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1441 | 1920 | 1920 | -479 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1410 | 1890 | 1890 | -480 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1410 | 1890 | 1890 | -480 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1403 | 1920 | 1920 | -517 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1403 | 1920 | 1920 | -517 | 73 | []

## 1430Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 14:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3349
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1884 |  | 1890 | -6 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1884 |  | 1890 | -6 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1872 |  | 1920 | -48 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1872 |  | 1920 | -48 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1678 |  | 1836 | -158 | 91 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1678 |  | 1836 | -158 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1603 |  | 1836 | -233 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1547 |  | 1836 | -289 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1547 |  | 1836 | -289 | 84 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1546 |  | 1836 | -290 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1538 |  | 1836 | -298 | 84 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1515 |  | 1836 | -321 | 83 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1515 |  | 1836 | -321 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 |  | 1836 | -364 | 80 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 |  | 1836 | -375 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1438 |  | 1836 | -398 | 78 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1448 |  | 1890 | -442 | 77 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1448 |  | 1890 | -442 | 77 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1381 |  | 1836 | -455 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1441 |  | 1920 | -479 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1441 |  | 1920 | -479 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1410 |  | 1890 | -480 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1410 |  | 1890 | -480 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1403 |  | 1920 | -517 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1403 |  | 1920 | -517 | 73 | []

## 1530Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 15:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2789
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1883 | 1890 | 1890 | -7 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1883 | 1890 | 1890 | -7 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1870 | 1920 | 1920 | -50 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1870 | 1920 | 1920 | -50 | 97 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1421 | 1890 | 1890 | -469 | 75 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1421 | 1890 | 1890 | -469 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1414 | 1920 | 1920 | -506 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1414 | 1920 | 1920 | -506 | 74 | []

## 1530Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 15:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2789
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1883 |  | 1890 | -7 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1883 |  | 1890 | -7 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1870 |  | 1920 | -50 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1870 |  | 1920 | -50 | 97 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1421 |  | 1890 | -469 | 75 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1421 |  | 1890 | -469 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1414 |  | 1920 | -506 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1414 |  | 1920 | -506 | 74 | []

## 1630Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 16:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2501
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1883 | 1890 | 1890 | -7 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1883 | 1890 | 1890 | -7 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 | 1920 | 1920 | -49 | 97 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1437 | 1890 | 1890 | -453 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1437 | 1890 | 1890 | -453 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1430 | 1920 | 1920 | -490 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1430 | 1920 | 1920 | -490 | 75 | []

## 1630Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 16:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2501
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1883 |  | 1890 | -7 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1883 |  | 1890 | -7 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1871 |  | 1920 | -49 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1871 |  | 1920 | -49 | 97 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1437 |  | 1890 | -453 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1437 |  | 1890 | -453 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1430 |  | 1920 | -490 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1430 |  | 1920 | -490 | 75 | []

## 1730Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 17:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3468
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1889 | 1890 | 1890 | -1 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1889 | 1890 | 1890 | -1 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1879 | 1920 | 1920 | -41 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1879 | 1920 | 1920 | -41 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 | 1836 | 1836 | -397 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 | 1836 | 1836 | -397 | 78 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1319 | 1836 | 1836 | -517 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1357 | 1890 | 1890 | -533 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1357 | 1890 | 1890 | -533 | 72 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1315 | 1836 | 1836 | -521 | 72 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1306 | 1836 | 1836 | -530 | 71 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1303 | 1836 | 1836 | -533 | 71 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1302 | 1836 | 1836 | -534 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1350 | 1920 | 1920 | -570 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1350 | 1920 | 1920 | -570 | 70 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1288 | 1836 | 1836 | -548 | 70 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1285 | 1836 | 1836 | -551 | 70 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1285 | 1836 | 1836 | -551 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 17:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3468
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1889 |  | 1890 | -1 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1889 |  | 1890 | -1 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1879 |  | 1920 | -41 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1879 |  | 1920 | -41 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 |  | 1836 | -397 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 |  | 1836 | -397 | 78 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1319 |  | 1836 | -517 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1357 |  | 1890 | -533 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1357 |  | 1890 | -533 | 72 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1315 |  | 1836 | -521 | 72 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1306 |  | 1836 | -530 | 71 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1303 |  | 1836 | -533 | 71 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1302 |  | 1836 | -534 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1350 |  | 1920 | -570 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1350 |  | 1920 | -570 | 70 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1288 |  | 1836 | -548 | 70 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1285 |  | 1836 | -551 | 70 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1285 |  | 1836 | -551 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 18:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3488
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1890 | 1890 | 1890 | 0 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1890 | 1890 | 1890 | 0 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1879 | 1920 | 1920 | -41 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1879 | 1920 | 1920 | -41 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1462 | -1836 | -1836 | -374 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1462 | -1836 | -1836 | -374 | 80 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1345 | -1836 | -1836 | -491 | 73 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1326 | 1836 | 1836 | -510 | 72 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1325 | 1836 | 1836 | -511 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1361 | 1890 | 1890 | -529 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1361 | 1890 | 1890 | -529 | 72 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1319 | -1836 | -1836 | -517 | 72 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1319 | -1836 | -1836 | -517 | 72 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1308 | -1836 | -1836 | -528 | 71 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1307 | -1836 | -1836 | -529 | 71 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1296 | -1836 | -1836 | -540 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1355 | 1920 | 1920 | -565 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1355 | 1920 | 1920 | -565 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 18:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3488
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1890 |  | 1890 | 0 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1890 |  | 1890 | 0 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1879 |  | 1920 | -41 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1879 |  | 1920 | -41 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1462 |  | -1836 | -374 | 80 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1462 |  | -1836 | -374 | 80 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1345 |  | -1836 | -491 | 73 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1326 |  | 1836 | -510 | 72 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1325 |  | 1836 | -511 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1361 |  | 1890 | -529 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1361 |  | 1890 | -529 | 72 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1319 |  | -1836 | -517 | 72 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1319 |  | -1836 | -517 | 72 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1308 |  | -1836 | -528 | 71 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1307 |  | -1836 | -529 | 71 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1296 |  | -1836 | -540 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1355 |  | 1920 | -565 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1355 |  | 1920 | -565 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 19:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3458
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 | 1890 | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1876 | 1920 | 1920 | -44 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1876 | 1920 | 1920 | -44 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1559 | -1836 | -1836 | -277 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1559 | -1836 | -1836 | -277 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1441 | -1836 | -1836 | -395 | 78 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1417 | -1836 | -1836 | -419 | 77 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1416 | -1836 | -1836 | -420 | 77 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1415 | -1836 | -1836 | -421 | 77 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1413 | -1836 | -1836 | -423 | 77 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1404 | -1836 | -1836 | -432 | 76 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1401 | -1836 | -1836 | -435 | 76 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1391 | -1836 | -1836 | -445 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1371 | 1890 | 1890 | -519 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1371 | 1890 | 1890 | -519 | 73 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1316 | -1836 | -1836 | -520 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1308 | -1836 | -1836 | -528 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1365 | 1920 | 1920 | -555 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1365 | 1920 | 1920 | -555 | 71 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1292 | -1836 | -1836 | -544 | 70 | []

## 1930Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 19:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3458
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1886 |  | 1890 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1876 |  | 1920 | -44 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1876 |  | 1920 | -44 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1559 |  | -1836 | -277 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1559 |  | -1836 | -277 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1441 |  | -1836 | -395 | 78 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1417 |  | -1836 | -419 | 77 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1416 |  | -1836 | -420 | 77 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1415 |  | -1836 | -421 | 77 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1413 |  | -1836 | -423 | 77 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1404 |  | -1836 | -432 | 76 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1401 |  | -1836 | -435 | 76 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1391 |  | -1836 | -445 | 76 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1371 |  | 1890 | -519 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1371 |  | 1890 | -519 | 73 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1316 |  | -1836 | -520 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1308 |  | -1836 | -528 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1365 |  | 1920 | -555 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1365 |  | 1920 | -555 | 71 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1292 |  | -1836 | -544 | 70 | []

## 2030Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 20:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3193
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1890 | 1890 | 1890 | 0 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1890 | 1890 | 1890 | 0 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1880 | 1920 | 1920 | -40 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1880 | 1920 | 1920 | -40 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1429 | -1836 | -1836 | -407 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1429 | -1836 | -1836 | -407 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1372 | 1890 | 1890 | -518 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1372 | 1890 | 1890 | -518 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1366 | 1920 | 1920 | -554 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1366 | 1920 | 1920 | -554 | 71 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1293 | -1836 | -1836 | -543 | 70 | []

## 2030Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 20:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3193
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1890 |  | 1890 | 0 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1890 |  | 1890 | 0 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1880 |  | 1920 | -40 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1880 |  | 1920 | -40 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1429 |  | -1836 | -407 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1429 |  | -1836 | -407 | 78 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1372 |  | 1890 | -518 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1372 |  | 1890 | -518 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1366 |  | 1920 | -554 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1366 |  | 1920 | -554 | 71 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1293 |  | -1836 | -543 | 70 | []

## 2130Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 21:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3384
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1877 | 1920 | 1920 | -43 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1877 | 1920 | 1920 | -43 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1645 | 1836 | 1836 | -191 | 90 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1645 | 1836 | 1836 | -191 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1520 | 1836 | 1836 | -316 | 83 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1496 | 1836 | 1836 | -340 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1496 | 1836 | 1836 | -340 | 82 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1495 | 1836 | 1836 | -341 | 81 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1491 | 1836 | 1836 | -345 | 81 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1491 | 1836 | 1836 | -345 | 81 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 | 1836 | 1836 | -357 | 81 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1471 | 1836 | 1836 | -365 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1398 | 1836 | 1836 | -438 | 76 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1383 | 1836 | 1836 | -453 | 75 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1369 | 1836 | 1836 | -467 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1387 | 1890 | 1890 | -503 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1387 | 1890 | 1890 | -503 | 73 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1338 | 1836 | 1836 | -498 | 73 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RIS1A41 _XVK_IS11_1:line | -1442 | -2000 | -2000 | -558 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1381 | 1920 | 1920 | -539 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1381 | 1920 | 1920 | -539 | 72 | []

## 2130Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 21:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3384
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1877 |  | 1920 | -43 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1877 |  | 1920 | -43 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1645 |  | 1836 | -191 | 90 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1645 |  | 1836 | -191 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1520 |  | 1836 | -316 | 83 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1496 |  | 1836 | -340 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1496 |  | 1836 | -340 | 82 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1495 |  | 1836 | -341 | 81 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1491 |  | 1836 | -345 | 81 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1491 |  | 1836 | -345 | 81 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 |  | 1836 | -357 | 81 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1471 |  | 1836 | -365 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1398 |  | 1836 | -438 | 76 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1383 |  | 1836 | -453 | 75 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1369 |  | 1836 | -467 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1387 |  | 1890 | -503 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1387 |  | 1890 | -503 | 73 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1338 |  | 1836 | -498 | 73 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-UA] [DIR] TIE 400 kV Isaccea-Vulcanesti | RIS1A41 _XVK_IS11_1:line | -1442 |  | -2000 | -558 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1381 |  | 1920 | -539 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1381 |  | 1920 | -539 | 72 | []

## 2230Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 22:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3515
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1815 | 1836 | 1836 | -21 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1815 | 1836 | 1836 | -21 | 99 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1875 | 1920 | 1920 | -45 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1875 | 1920 | 1920 | -45 | 98 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1695 | 1836 | 1836 | -141 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1679 | 1836 | 1836 | -157 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1678 | 1836 | 1836 | -158 | 91 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1674 | 1836 | 1836 | -162 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1671 | 1836 | 1836 | -165 | 91 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1667 | 1836 | 1836 | -169 | 91 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1662 | 1836 | 1836 | -174 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1658 | 1836 | 1836 | -178 | 90 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1594 | 1836 | 1836 | -242 | 87 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1551 | 1836 | 1836 | -285 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1547 | 1836 | 1836 | -289 | 84 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1496 | 1836 | 1836 | -340 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1418 | 1890 | 1890 | -472 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1418 | 1890 | 1890 | -472 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1411 | 1920 | 1920 | -509 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1411 | 1920 | 1920 | -509 | 73 | []

## 2230Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 22:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3515
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1815 |  | 1836 | -21 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1815 |  | 1836 | -21 | 99 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1875 |  | 1920 | -45 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1875 |  | 1920 | -45 | 98 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1695 |  | 1836 | -141 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1679 |  | 1836 | -157 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1678 |  | 1836 | -158 | 91 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1674 |  | 1836 | -162 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1671 |  | 1836 | -165 | 91 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1667 |  | 1836 | -169 | 91 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1662 |  | 1836 | -174 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1658 |  | 1836 | -178 | 90 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1594 |  | 1836 | -242 | 87 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1551 |  | 1836 | -285 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1547 |  | 1836 | -289 | 84 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1496 |  | 1836 | -340 | 81 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1418 |  | 1890 | -472 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1418 |  | 1890 | -472 | 75 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1411 |  | 1920 | -509 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1411 |  | 1920 | -509 | 73 | []

## 2330Preventive
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 23:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3429
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1834 | 1836 | 1836 | -2 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1834 | 1836 | 1836 | -2 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1732 | 1836 | 1836 | -104 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1719 | 1836 | 1836 | -117 | 94 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1717 | 1836 | 1836 | -119 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1709 | 1836 | 1836 | -127 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1709 | 1836 | 1836 | -127 | 93 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1707 | 1836 | 1836 | -129 | 93 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1698 | 1836 | 1836 | -138 | 92 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1746 | 1890 | 1890 | -144 | 92 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1746 | 1890 | 1890 | -144 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1691 | 1836 | 1836 | -145 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1734 | 1920 | 1920 | -186 | 90 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1734 | 1920 | 1920 | -186 | 90 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1634 | 1836 | 1836 | -202 | 89 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1589 | 1836 | 1836 | -247 | 87 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1582 | 1836 | 1836 | -254 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1559 | 1836 | 1836 | -277 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1331 | 1890 | 1890 | -559 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1331 | 1890 | 1890 | -559 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2026-04-27 08:25
Business day: | 27.04.2026
Timestamp: | 23:30
Border & direction: | South-Romania Import
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3429
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00001 | PRA 400/220kV AT3 Arad | preventive | pst |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1834 |  | 1836 | -2 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1834 |  | 1836 | -2 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1732 |  | 1836 | -104 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1719 |  | 1836 | -117 | 94 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1717 |  | 1836 | -119 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1709 |  | 1836 | -127 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1709 |  | 1836 | -127 | 93 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1707 |  | 1836 | -129 | 93 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1698 |  | 1836 | -138 | 92 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1746 |  | 1890 | -144 | 92 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1746 |  | 1890 | -144 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1691 |  | 1836 | -145 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1734 |  | 1920 | -186 | 90 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1734 |  | 1920 | -186 | 90 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1634 |  | 1836 | -202 | 89 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1589 |  | 1836 | -247 | 87 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1582 |  | 1836 | -254 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1559 |  | 1836 | -277 | 85 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1331 |  | 1890 | -559 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1331 |  | 1890 | -559 | 70 | []