## SRO borders-exports
SUBMISSION DATE: | 08.05.2026
BUSINESS DATE: | 10.05.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC RO-BG
00:00 | 01:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 80 | 3569 | 3369 | 2358
01:00 | 02:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 80 | 3550 | 3350 | 2345
02:00 | 03:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 82 | 3557 | 3357 | 2350
03:00 | 04:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 82 | 3590 | 3390 | 2373
04:00 | 05:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 81 | 3513 | 3313 | 2319
05:00 | 06:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 80 | 3501 | 3301 | 2311
06:00 | 07:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 86 | 3556 | 3356 | 2349
07:00 | 08:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 89 | 3518 | 3318 | 2323
08:00 | 09:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 96 | 3587 | 3387 | 2371
09:00 | 10:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 97 | 3672 | 3472 | 2430
10:00 | 11:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 92 | 3825 | 3625 | 2538
11:00 | 12:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 95 | 4101 | 3901 | 2731
12:00 | 13:00 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 100 | 4346 | 4146 | 2902
13:00 | 14:00 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 100 | 4316 | 4116 | 2881
14:00 | 15:00 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 97 | 4173 | 3973 | 2781
15:00 | 16:00 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | 97 | 4228 | 4028 | 2820
16:00 | 17:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 87 | 3679 | 3479 | 2435
17:00 | 18:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3555 | 3355 | 2348
18:00 | 19:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3491 | 3291 | 2304
19:00 | 20:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 3443 | 3243 | 2270
20:00 | 21:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 95 | 3468 | 3268 | 2288
21:00 | 22:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 96 | 3496 | 3296 | 2307
22:00 | 23:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 95 | 3567 | 3367 | 2357
23:00 | 00:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 83 | 3524 | 3324 | 2327

## SRO borders-imports
SUBMISSION DATE: | 08.05.2026
BUSINESS DATE: | 10.05.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC BG-RO
00:00 | 01:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 98 | 3870 | 3670 | 2569
01:00 | 02:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 96 | 3853 | 3653 | 2557
02:00 | 03:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 94 | 3845 | 3645 | 2552
03:00 | 04:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 98 | 3857 | 3657 | 2560
04:00 | 05:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 94 | 3863 | 3663 | 2564
05:00 | 06:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 94 | 3854 | 3654 | 2558
06:00 | 07:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3609 | 3409 | 2386
07:00 | 08:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3834 | 3634 | 2544
08:00 | 09:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 97 | 3802 | 3602 | 2521
09:00 | 10:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3598 | 3398 | 2379
10:00 | 11:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3252 | 3052 | 2136
11:00 | 12:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3296 | 3096 | 2167
12:00 | 13:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3146 | 2946 | 2062
13:00 | 14:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 98 | 2928 | 2728 | 1910
14:00 | 15:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 99 | 2920 | 2720 | 1904
15:00 | 16:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3200 | 3000 | 2100
16:00 | 17:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 99 | 3600 | 3400 | 2380
17:00 | 18:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3466 | 3266 | 2286
18:00 | 19:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3723 | 3523 | 2466
19:00 | 20:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 99 | 3595 | 3395 | 2376
20:00 | 21:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3367 | 3167 | 2217
21:00 | 22:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3304 | 3104 | 2173
22:00 | 23:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3176 | 2976 | 2083
23:00 | 00:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3209 | 3009 | 2106

## SRO borders-exports RAs
SUBMISSION DATE: | 08.05.2026
BUSINESS DATE: | 10.05.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | notApplied | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 110 kV Pelicanu | RO_RA_00005 | topological_ra | [13 empty] | applied
PRA 110 kV Resita | RO_RA_00007 | topological_ra | [13 empty] | applied
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst_ra | [13 empty] | applied
PST_ARAD 400/220_3 | RO_RA_00101 | pst_ra | [13 empty] | applied
PST_URECHESTI 400/220_1 | RO_RA_00102 | pst_ra | [13 empty] | applied
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
RBRAZ41 _generator | RO_RA_00111 | costly_ra | [12 empty] | 1
RBRZ241 _generator | RO_RA_00112 | costly_ra | [12 empty] | 1
RPDF212 _generator | RO_RA_00115 | costly_ra | [12 empty] | 0
RGODI_5 _generator | RO_RA_00117 | costly_ra | [12 empty] | 114
RTOPV_5 _generator | RO_RA_00120 | costly_ra | [12 empty] | 10
RFMEP_5 _generator | RO_RA_00121 | costly_ra | [12 empty] | 14
RVLCE15 _generator | RO_RA_00122 | costly_ra | [12 empty] | 55
RARGS_5 _generator | RO_RA_00126 | costly_ra | [12 empty] | 31
RALBE_5 _generator | RO_RA_00127 | costly_ra | [12 empty] | 30
RCERB_5 _generator | RO_RA_00128 | costly_ra | [12 empty] | 15
RVLCE25 _generator | RO_RA_00129 | costly_ra | [12 empty] | 12
RCLNG_5 _generator | RO_RA_00130 | costly_ra | [12 empty] | 0
RLOTR22 _generator | RO_RA_00131 | costly_ra | [12 empty] | 0
RLOT212 _generator | RO_RA_00132 | costly_ra | [12 empty] | 0
RVILN_5 _generator | RO_RA_00136 | costly_ra | [12 empty] | 46
RRIUR15 _generator | RO_RA_00137 | costly_ra | [12 empty] | 48
RMARC_5 _generator | RO_RA_00138 | costly_ra | [12 empty] | 0
RCHTU_5 _generator | RO_RA_00142 | costly_ra | [12 empty] | 74
RHGLOT5 _generator | RO_RA_00144 | costly_ra | [12 empty] | 25
RCHESJ5 _generator | RO_RA_00145 | costly_ra | [12 empty] | 0
RCHEAC5 _generator | RO_RA_00146 | costly_ra | [12 empty] | 38
RCHEST5 _generator | RO_RA_00147 | costly_ra | [12 empty] | 26
RCHEIO5 _generator | RO_RA_00148 | costly_ra | [12 empty] | 53
RCHDO_5 _generator | RO_RA_00149 | costly_ra | [12 empty] | 53
RFRUN_5 _generator | RO_RA_00150 | costly_ra | [12 empty] | 53
RCIZBI5 _generator | RO_RA_00151 | costly_ra | [12 empty] | 53
RRUSA_5 _generator | RO_RA_00152 | costly_ra | [12 empty] | 0
RHCORN5 _generator | RO_RA_00153 | costly_ra | [12 empty] | 59
RFAGA_5 _generator | RO_RA_00154 | costly_ra | [12 empty] | 20
RUCEA25 _generator | RO_RA_00155 | costly_ra | [12 empty] | 32
RUCEA15 _generator | RO_RA_00156 | costly_ra | [12 empty] | 49
RCIRT_5 _generator | RO_RA_00157 | costly_ra | [12 empty] | 0
RSTEJ25 _generator | RO_RA_00159 | costly_ra | [12 empty] | 32
RVADU_5 _generator | RO_RA_00160 | costly_ra | [12 empty] | 67
RIZVO_5 _generator | RO_RA_00161 | costly_ra | [12 empty] | 9
RDUMB_5 _generator | RO_RA_00162 | costly_ra | [12 empty] | 0
RCOST_5 _generator | RO_RA_00163 | costly_ra | [12 empty] | 0
RBUHU_5 _generator | RO_RA_00164 | costly_ra | [12 empty] | 12
RRACO_5 _generator | RO_RA_00165 | costly_ra | [12 empty] | 0
RGARL_5 _generator | RO_RA_00166 | costly_ra | [12 empty] | 23
RLILI_5 _generator | RO_RA_00167 | costly_ra | [12 empty] | 23
RBACS_5 _generator | RO_RA_00168 | costly_ra | [12 empty] | 98
RFARA_5 _generator | RO_RA_00169 | costly_ra | [12 empty] | 30
RSISC_5 _generator | RO_RA_00170 | costly_ra | [12 empty] | 44
RMARA_5 _generator | RO_RA_00171 | costly_ra | [12 empty] | 0
RTECU_5 _generator | RO_RA_00172 | costly_ra | [12 empty] | 0
RSEBE_5 _generator | RO_RA_00176 | costly_ra | [12 empty] | 55
RIAZUA5 _generator | RO_RA_00177 | costly_ra | [12 empty] | 33
RRETE22 _generator | RO_RA_00180 | costly_ra | [12 empty] | 222
RCIRNA5 _generator | RO_RA_00182 | costly_ra | [12 empty] | 29
RCIRNB5 _generator | RO_RA_00183 | costly_ra | [12 empty] | 27
RHATE_5 _generator | RO_RA_00184 | costly_ra | [12 empty] | 52

## SRO borders-imports RAs
SUBMISSION DATE: | 08.05.2026
BUSINESS DATE: | 10.05.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400 kV TINTARENI-KOZLODUI 1 | BG_RA_00001 | topological | helpful | helpful | helpful | helpful | helpful | helpful |  | helpful | helpful | helpful
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | helpful | notApplied | notApplied | notApplied | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 110 kV S5 | RO_RA_00004 | topological_ra | [20 empty] | applied | applied | applied
PRA 110 kV Pelicanu | RO_RA_00005 | topological_ra | [20 empty] | applied | applied | applied
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst_ra | [20 empty] | applied | applied | applied
PST_ARAD 400/220_3 | RO_RA_00101 | pst_ra | [20 empty] | applied | applied | applied
PST_URECHESTI 400/220_1 | RO_RA_00102 | pst_ra | [20 empty] | applied | applied | applied
PRA 110 kV Dobrogea | RO_RA_00006 | topological_ra | [21 empty] | applied
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
RPDF222 _generator | RO_RA_00114 | costly_ra | [20 empty] | 577 | 580 | 458
RGODI_5 _generator | RO_RA_00117 | costly_ra | [20 empty] | 0
RFMEP_5 _generator | RO_RA_00121 | costly_ra | [20 empty] | 0
RVLCE15 _generator | RO_RA_00122 | costly_ra | [20 empty] | 0 | 0 | 0
RVALD_5 _generator | RO_RA_00123 | costly_ra | [20 empty] | 0
RARGS_5 _generator | RO_RA_00126 | costly_ra | [20 empty] | 0 | 0 | 0
RALBE_5 _generator | RO_RA_00127 | costly_ra | [20 empty] | 0 | 0 | 0
RCERB_5 _generator | RO_RA_00128 | costly_ra | [20 empty] | 0
RVLCE25 _generator | RO_RA_00129 | costly_ra | [20 empty] | 0
RCLNG_5 _generator | RO_RA_00130 | costly_ra | [20 empty] | 0 | 0 | 0
RLOTR22 _generator | RO_RA_00131 | costly_ra | [20 empty] | 6
RBRDS25 _generator | RO_RA_00133 | costly_ra | [20 empty] | 118 |  | 1
RSTUP_5 _generator | RO_RA_00134 | costly_ra | [20 empty] | 0 | 0 | 0
RDAIES5 _generator | RO_RA_00135 | costly_ra | [20 empty] | 0 | 0 | 0
RVILN_5 _generator | RO_RA_00136 | costly_ra | [20 empty] | 0 | 0 | 0
RRIUR15 _generator | RO_RA_00137 | costly_ra | [20 empty] | 0 | 0 | 0
RMARC_5 _generator | RO_RA_00138 | costly_ra | [20 empty] | 0 | 0 | 0
RIONE_5 _generator | RO_RA_00139 | costly_ra | [20 empty] | 0 | 0 | 0
RJIBL_5 _generator | RO_RA_00140 | costly_ra | [20 empty] | 0 | 0 | 0
RZAVI_5 _generator | RO_RA_00141 | costly_ra | [20 empty] | 0 | 0 | 0
RCHTU_5 _generator | RO_RA_00142 | costly_ra | [20 empty] | 0 | 0 | 0
RTRAI_5 _generator | RO_RA_00143 | costly_ra | [20 empty] | 0 | 0 | 0
RHGLOT5 _generator | RO_RA_00144 | costly_ra | [20 empty] | 0 | 0 | 0
RCHESJ5 _generator | RO_RA_00145 | costly_ra | [20 empty] | 0 | 0 | 0
RCHEAC5 _generator | RO_RA_00146 | costly_ra | [20 empty] | 0 | 0 | 0
RCHEST5 _generator | RO_RA_00147 | costly_ra | [20 empty] | 0 | 0 | 0
RCHEIO5 _generator | RO_RA_00148 | costly_ra | [20 empty] | 0 | 0 | 0
RCHDO_5 _generator | RO_RA_00149 | costly_ra | [20 empty] | 0 | 0 | 0
RFRUN_5 _generator | RO_RA_00150 | costly_ra | [20 empty] | 0 | 0 | 0
RCIZBI5 _generator | RO_RA_00151 | costly_ra | [20 empty] | 0 | 0 | 0
RRUSA_5 _generator | RO_RA_00152 | costly_ra | [20 empty] | 0 | 0 | 0
RHCORN5 _generator | RO_RA_00153 | costly_ra | [20 empty] | 0 | 0 | 0
RFAGA_5 _generator | RO_RA_00154 | costly_ra | [20 empty] | 0 | 0 | 20
RUCEA25 _generator | RO_RA_00155 | costly_ra | [20 empty] | 0 | 0 | 32
RUCEA15 _generator | RO_RA_00156 | costly_ra | [20 empty] | 0 | 0 | 0
RCIRT_5 _generator | RO_RA_00157 | costly_ra | [20 empty] | 0 | 41 | 54
RVADU_5 _generator | RO_RA_00160 | costly_ra | [20 empty] | 0 | 0 | 0
RIZVO_5 _generator | RO_RA_00161 | costly_ra | [20 empty] | 0 | 0 | 0
RDUMB_5 _generator | RO_RA_00162 | costly_ra | [20 empty] | 0 | 0 | 0
RCOST_5 _generator | RO_RA_00163 | costly_ra | [20 empty] | 0 | 0 | 0
RBUHU_5 _generator | RO_RA_00164 | costly_ra | [20 empty] | 0 | 0 | 0
RRACO_5 _generator | RO_RA_00165 | costly_ra | [20 empty] | 0 | 0 | 0
RGARL_5 _generator | RO_RA_00166 | costly_ra | [20 empty] | 0 | 0 | 0
RLILI_5 _generator | RO_RA_00167 | costly_ra | [20 empty] | 0 | 0 | 0
RBACS_5 _generator | RO_RA_00168 | costly_ra | [20 empty] | 0 | 0 | 0
RFARA_5 _generator | RO_RA_00169 | costly_ra | [20 empty] | 0 | 0 | 0
RSISC_5 _generator | RO_RA_00170 | costly_ra | [20 empty] | 0 | 0 | 0
RMARA_5 _generator | RO_RA_00171 | costly_ra | [20 empty] | 0 | 0 | 0
RTECU_5 _generator | RO_RA_00172 | costly_ra | [20 empty] | 0 | 0 | 0
RSEBE_5 _generator | RO_RA_00176 | costly_ra | [20 empty] | 0 | 0 | 0
RRETE_5 _generator | RO_RA_00181 | costly_ra | [20 empty] | 0 | 0 | 0
RCIRNA5 _generator | RO_RA_00182 | costly_ra | [20 empty] | 0 | 0 | 0
RCIRNB5 _generator | RO_RA_00183 | costly_ra | [20 empty] | 0 | 0 | 0
RHATE_5 _generator | RO_RA_00184 | costly_ra | [20 empty] | 0 | 0 | 0
RPDF212 _generator | RO_RA_00115 | costly_ra | [21 empty] | 46