## 1230Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2892
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1597 | 1600 | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1511 | 1600 | 1600 | -89 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1473 | 1600 | 1600 | -127 | 92 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1449 | 1600 | 1600 | -151 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1386 | 1600 | 1600 | -214 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1386 | 1600 | 1600 | -214 | 87 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1372 | 1600 | 1600 | -228 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1366 | 1600 | 1600 | -234 | 85 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 | 1600 | 1600 | -262 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1334 | 1600 | 1600 | -266 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1322 | 1600 | 1600 | -278 | 83 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1292 | 1600 | 1600 | -308 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1289 | 1600 | 1600 | -311 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1273 | 1600 | 1600 | -327 | 80 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1246 | 1600 | 1600 | -354 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 | 1600 | 1600 | -357 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1235 | 1600 | 1600 | -365 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 | 1600 | 1600 | -366 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 | 1600 | 1600 | -366 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 | 1600 | 1600 | -367 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 | 1600 | 1600 | -369 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 | 1600 | 1600 | -370 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 | 1600 | 1600 | -370 | 77 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1600 | 1600 | -388 | 76 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1600 | 1600 | -388 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 76 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 | 1600 | 1600 | -400 | 75 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1600 | 1600 | -402 | 75 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 | 1600 | 1600 | -452 | 72 | []

## 1230Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2892
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1597 |  | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1511 |  | 1600 | -89 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1473 |  | 1600 | -127 | 92 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1449 |  | 1600 | -151 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1386 |  | 1600 | -214 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1386 |  | 1600 | -214 | 87 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1372 |  | 1600 | -228 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1366 |  | 1600 | -234 | 85 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 |  | 1600 | -262 | 84 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1334 |  | 1600 | -266 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1322 |  | 1600 | -278 | 83 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1292 |  | 1600 | -308 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1289 |  | 1600 | -311 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1273 |  | 1600 | -327 | 80 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1246 |  | 1600 | -354 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 |  | 1600 | -357 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1235 |  | 1600 | -365 | 77 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 |  | 1600 | -366 | 77 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 |  | 1600 | -366 | 77 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 |  | 1600 | -367 | 77 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 |  | 1600 | -367 | 77 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 |  | 1600 | -369 | 77 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 |  | 1600 | -370 | 77 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 |  | 1600 | -370 | 77 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1600 | -388 | 76 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1600 | -388 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 76 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 |  | 1600 | -400 | 75 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1600 | -402 | 75 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 |  | 1600 | -452 | 72 | []

## 1330Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2677
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1595 | 1600 | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1533 | 1600 | 1600 | -67 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1498 | 1600 | 1600 | -102 | 94 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1461 | 1600 | 1600 | -139 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1393 | 1600 | 1600 | -207 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1384 | 1600 | 1600 | -216 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1359 | 1600 | 1600 | -241 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1356 | 1600 | 1600 | -244 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1346 | 1600 | 1600 | -254 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1317 | 1600 | 1600 | -283 | 82 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1315 | 1600 | 1600 | -285 | 82 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1312 | 1600 | 1600 | -288 | 82 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1312 | 1600 | 1600 | -288 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1300 | 1600 | 1600 | -300 | 81 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1283 | 1600 | 1600 | -317 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1276 | 1600 | 1600 | -324 | 80 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1271 | 1600 | 1600 | -329 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1268 | 1600 | 1600 | -332 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1266 | 1600 | 1600 | -334 | 79 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1247 | 1600 | 1600 | -353 | 78 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 | 1600 | 1600 | -366 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 | 1600 | 1600 | -368 | 77 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 | 1600 | 1600 | -410 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1158 | 1600 | 1600 | -442 | 72 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 | 1600 | 1600 | -447 | 72 | []

## 1330Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2677
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1595 |  | 1600 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1533 |  | 1600 | -67 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1498 |  | 1600 | -102 | 94 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1461 |  | 1600 | -139 | 91 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1393 |  | 1600 | -207 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1384 |  | 1600 | -216 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1359 |  | 1600 | -241 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1356 |  | 1600 | -244 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1346 |  | 1600 | -254 | 84 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1317 |  | 1600 | -283 | 82 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1315 |  | 1600 | -285 | 82 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1312 |  | 1600 | -288 | 82 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1312 |  | 1600 | -288 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1300 |  | 1600 | -300 | 81 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1283 |  | 1600 | -317 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 |  | 1600 | -323 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 |  | 1600 | -323 | 80 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1276 |  | 1600 | -324 | 80 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1271 |  | 1600 | -329 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1268 |  | 1600 | -332 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1266 |  | 1600 | -334 | 79 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1263 |  | 1600 | -337 | 79 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1247 |  | 1600 | -353 | 78 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1234 |  | 1600 | -366 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 |  | 1600 | -368 | 77 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 |  | 1600 | -410 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1158 |  | 1600 | -442 | 72 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 |  | 1600 | -447 | 72 | []

## 1430Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2721
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1593 | 1600 | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1539 | 1600 | 1600 | -61 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1496 | 1600 | 1600 | -104 | 93 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1465 | 1600 | 1600 | -135 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1397 | 1600 | 1600 | -203 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1381 | 1600 | 1600 | -219 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1357 | 1600 | 1600 | -243 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1354 | 1600 | 1600 | -246 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 | 1600 | 1600 | -262 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1315 | 1600 | 1600 | -285 | 82 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1315 | 1600 | 1600 | -285 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1308 | 1600 | 1600 | -292 | 82 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1305 | 1600 | 1600 | -295 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1295 | 1600 | 1600 | -305 | 81 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1276 | 1600 | 1600 | -324 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1273 | 1600 | 1600 | -327 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1272 | 1600 | 1600 | -328 | 80 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1265 | 1600 | 1600 | -335 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 | 1600 | 1600 | -340 | 79 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 | 1600 | 1600 | -344 | 79 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 | 1600 | 1600 | -344 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 | 1600 | 1600 | -347 | 78 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 | 1600 | 1600 | -349 | 78 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1240 | 1600 | 1600 | -360 | 77 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 | 1600 | 1600 | -369 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 | 1600 | 1600 | -424 | 73 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1159 | 1600 | 1600 | -441 | 72 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 | 1600 | 1600 | -447 | 72 | []

## 1430Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2721
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1593 |  | 1600 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1539 |  | 1600 | -61 | 96 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1496 |  | 1600 | -104 | 93 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1465 |  | 1600 | -135 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1397 |  | 1600 | -203 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1381 |  | 1600 | -219 | 86 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1357 |  | 1600 | -243 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1354 |  | 1600 | -246 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 |  | 1600 | -262 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1315 |  | 1600 | -285 | 82 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1315 |  | 1600 | -285 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1308 |  | 1600 | -292 | 82 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1305 |  | 1600 | -295 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1295 |  | 1600 | -305 | 81 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1276 |  | 1600 | -324 | 80 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1273 |  | 1600 | -327 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1272 |  | 1600 | -328 | 80 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1265 |  | 1600 | -335 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1260 |  | 1600 | -340 | 79 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 |  | 1600 | -342 | 79 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 |  | 1600 | -342 | 79 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 |  | 1600 | -342 | 79 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 |  | 1600 | -344 | 79 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 |  | 1600 | -344 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1253 |  | 1600 | -347 | 78 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 |  | 1600 | -349 | 78 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1240 |  | 1600 | -360 | 77 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 |  | 1600 | -369 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 |  | 1600 | -424 | 73 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1159 |  | 1600 | -441 | 72 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 |  | 1600 | -447 | 72 | []

## 1530Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2671
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1597 | 1600 | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1524 | 1600 | 1600 | -76 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1482 | 1600 | 1600 | -118 | 93 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1436 | 1600 | 1600 | -164 | 90 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1395 | 1600 | 1600 | -205 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1363 | 1600 | 1600 | -237 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1349 | 1600 | 1600 | -251 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1348 | 1600 | 1600 | -252 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1334 | 1600 | 1600 | -266 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1330 | 1600 | 1600 | -270 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1320 | 1600 | 1600 | -280 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1296 | 1600 | 1600 | -304 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1265 | 1600 | 1600 | -335 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 | 1600 | 1600 | -336 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 | 1600 | 1600 | -342 | 79 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 | 1600 | 1600 | -344 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 | 1600 | 1600 | -345 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 | 1600 | 1600 | -357 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 | 1600 | 1600 | -357 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 | 1600 | 1600 | -359 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1240 | 1600 | 1600 | -360 | 78 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 | 1600 | 1600 | -364 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 | 1600 | 1600 | -368 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 | 1600 | 1600 | -374 | 77 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 | 1600 | 1600 | -379 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 | 1600 | 1600 | -379 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 | 1600 | 1600 | -392 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1152 | 1600 | 1600 | -448 | 72 | []

## 1530Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2671
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1597 |  | 1600 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1524 |  | 1600 | -76 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1482 |  | 1600 | -118 | 93 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1436 |  | 1600 | -164 | 90 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1395 |  | 1600 | -205 | 87 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1363 |  | 1600 | -237 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1349 |  | 1600 | -251 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1348 |  | 1600 | -252 | 84 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1334 |  | 1600 | -266 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1330 |  | 1600 | -270 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1320 |  | 1600 | -280 | 82 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1296 |  | 1600 | -304 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 |  | 1600 | -323 | 80 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1265 |  | 1600 | -335 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1264 |  | 1600 | -336 | 79 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1258 |  | 1600 | -342 | 79 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 |  | 1600 | -344 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1255 |  | 1600 | -345 | 78 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 |  | 1600 | -357 | 78 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 |  | 1600 | -357 | 78 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1241 |  | 1600 | -359 | 78 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1240 |  | 1600 | -360 | 78 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1236 |  | 1600 | -364 | 77 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1232 |  | 1600 | -368 | 77 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1226 |  | 1600 | -374 | 77 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 |  | 1600 | -379 | 76 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 |  | 1600 | -379 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1600 | -381 | 76 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1600 | -381 | 76 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 |  | 1600 | -392 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1152 |  | 1600 | -448 | 72 | []

## 1630Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3164
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1600 | 1600 | 1600 | 0 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1483 | 1600 | 1600 | -117 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1439 | 1600 | 1600 | -161 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1402 | 1600 | 1600 | -198 | 88 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1393 | 1600 | 1600 | -207 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1393 | 1600 | 1600 | -207 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1373 | 1600 | 1600 | -227 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1363 | 1600 | 1600 | -237 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1355 | 1600 | 1600 | -245 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1302 | 1600 | 1600 | -298 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 | 1600 | 1600 | -338 | 79 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 | 1600 | 1600 | -344 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 | 1600 | 1600 | -358 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 | 1600 | 1600 | -363 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1220 | 1600 | 1600 | -380 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1220 | 1600 | 1600 | -380 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 | 1600 | 1600 | -382 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 | 1600 | 1600 | -387 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 | 1600 | 1600 | -390 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 | 1600 | 1600 | -390 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 | 1600 | 1600 | -391 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1600 | 1600 | -396 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 | 1600 | 1600 | -406 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 | 1600 | 1600 | -407 | 75 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 | 1600 | 1600 | -418 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 | 1600 | 1600 | -422 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 | 1600 | 1600 | -424 | 74 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1138 | 1600 | 1600 | -462 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3164
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1600 |  | 1600 | 0 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1483 |  | 1600 | -117 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1439 |  | 1600 | -161 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1402 |  | 1600 | -198 | 88 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1393 |  | 1600 | -207 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1393 |  | 1600 | -207 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1373 |  | 1600 | -227 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1363 |  | 1600 | -237 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1355 |  | 1600 | -245 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1302 |  | 1600 | -298 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 |  | 1600 | -323 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 |  | 1600 | -338 | 79 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 |  | 1600 | -344 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1242 |  | 1600 | -358 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 |  | 1600 | -363 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1220 |  | 1600 | -380 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1220 |  | 1600 | -380 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 |  | 1600 | -382 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 |  | 1600 | -387 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 |  | 1600 | -390 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 |  | 1600 | -390 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 |  | 1600 | -391 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1600 | -396 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 |  | 1600 | -406 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 |  | 1600 | -407 | 75 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 |  | 1600 | -418 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 |  | 1600 | -422 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 |  | 1600 | -424 | 74 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1138 |  | 1600 | -462 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3471
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1594 | 1600 | 1600 | -6 | 100 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1486 | 1600 | 1600 | -114 | 93 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1410 | 1600 | 1600 | -190 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1410 | 1600 | 1600 | -190 | 88 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1401 | 1600 | 1600 | -199 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1401 | 1600 | 1600 | -199 | 88 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1390 | 1600 | 1600 | -210 | 87 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1387 | 1600 | 1600 | -213 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1387 | 1600 | 1600 | -213 | 87 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1365 | 1600 | 1600 | -235 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1343 | 1600 | 1600 | -257 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1323 | 1600 | 1600 | -277 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1303 | 1600 | 1600 | -297 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1273 | 1600 | 1600 | -327 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 | 1600 | 1600 | -355 | 78 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1220 | 1600 | 1600 | -380 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 | 1600 | 1600 | -387 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 | 1600 | 1600 | -387 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1600 | 1600 | -393 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 | 1600 | 1600 | -394 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 | 1600 | 1600 | -394 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 | 1600 | 1600 | -398 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 | 1600 | 1600 | -407 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 | 1600 | 1600 | -409 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 | 1600 | 1600 | -410 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 | 1600 | 1600 | -421 | 74 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1169 | 1600 | 1600 | -431 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1158 | 1600 | 1600 | -442 | 72 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1157 | 1600 | 1600 | -443 | 72 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 | 1600 | 1600 | -449 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1135 | 1600 | 1600 | -465 | 71 | []

## 1730Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3471
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1594 |  | 1600 | -6 | 100 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1486 |  | 1600 | -114 | 93 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1410 |  | 1600 | -190 | 88 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1410 |  | 1600 | -190 | 88 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1401 |  | 1600 | -199 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1401 |  | 1600 | -199 | 88 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1390 |  | 1600 | -210 | 87 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1387 |  | 1600 | -213 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1387 |  | 1600 | -213 | 87 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1365 |  | 1600 | -235 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1343 |  | 1600 | -257 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1323 |  | 1600 | -277 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1303 |  | 1600 | -297 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1273 |  | 1600 | -327 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1245 |  | 1600 | -355 | 78 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1220 |  | 1600 | -380 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1600 | -381 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1600 | -385 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1600 | -385 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 |  | 1600 | -387 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 |  | 1600 | -387 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1600 | -393 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 |  | 1600 | -394 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 |  | 1600 | -394 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 |  | 1600 | -398 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | -1195 |  | 1600 | -405 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 |  | 1600 | -407 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 |  | 1600 | -409 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 |  | 1600 | -410 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 |  | 1600 | -421 | 74 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1169 |  | 1600 | -431 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1158 |  | 1600 | -442 | 72 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1157 |  | 1600 | -443 | 72 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 |  | 1600 | -449 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1135 |  | 1600 | -465 | 71 | []

## 1830Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3456
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1600 | 1600 | 1600 | 0 | 100 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1485 | 1600 | 1600 | -115 | 93 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1417 | 1600 | 1600 | -183 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1407 | 1600 | 1600 | -193 | 88 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1405 | 1600 | 1600 | -195 | 88 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1405 | 1600 | 1600 | -195 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1402 | 1600 | 1600 | -198 | 88 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1391 | 1600 | 1600 | -209 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1372 | 1600 | 1600 | -228 | 86 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1360 | 1600 | 1600 | -240 | 85 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 | 1600 | 1600 | -262 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1331 | 1600 | 1600 | -269 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1301 | 1600 | 1600 | -299 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1272 | 1600 | 1600 | -328 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 | 1600 | 1600 | -341 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 | 1600 | 1600 | -350 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 | 1600 | 1600 | -350 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 | 1600 | 1600 | -383 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1600 | 1600 | -385 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 | 1600 | 1600 | -386 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1600 | 1600 | -388 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 | 1600 | 1600 | -398 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 | 1600 | 1600 | -398 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1600 | 1600 | -402 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1600 | 1600 | -402 | 75 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1193 | 1600 | 1600 | -407 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 | 1600 | 1600 | -407 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 | 1600 | 1600 | -407 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 | 1600 | 1600 | -408 | 74 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1185 | 1600 | 1600 | -415 | 74 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 | 1600 | 1600 | -421 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 | 1600 | 1600 | -423 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1165 | 1600 | 1600 | -435 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1144 | 1600 | 1600 | -456 | 71 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1135 | 1600 | 1600 | -465 | 71 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1132 | 1600 | 1600 | -468 | 71 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1130 | 1600 | 1600 | -470 | 71 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1130 | 1600 | 1600 | -470 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1128 | 1600 | 1600 | -472 | 70 | []

## 1830Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3456
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1600 |  | 1600 | 0 | 100 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1485 |  | 1600 | -115 | 93 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1417 |  | 1600 | -183 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1407 |  | 1600 | -193 | 88 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1405 |  | 1600 | -195 | 88 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1405 |  | 1600 | -195 | 88 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1402 |  | 1600 | -198 | 88 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1391 |  | 1600 | -209 | 87 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1372 |  | 1600 | -228 | 86 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1360 |  | 1600 | -240 | 85 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 |  | 1600 | -262 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1331 |  | 1600 | -269 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1301 |  | 1600 | -299 | 81 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1272 |  | 1600 | -328 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1259 |  | 1600 | -341 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 |  | 1600 | -350 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 |  | 1600 | -350 | 78 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1600 | -381 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1217 |  | 1600 | -383 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1600 | -385 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 |  | 1600 | -386 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1600 | -388 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 |  | 1600 | -398 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1202 |  | 1600 | -398 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1600 | -402 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1600 | -402 | 75 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1193 |  | 1600 | -407 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 |  | 1600 | -407 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 |  | 1600 | -407 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 |  | 1600 | -408 | 74 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1185 |  | 1600 | -415 | 74 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 |  | 1600 | -421 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 |  | 1600 | -423 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1165 |  | 1600 | -435 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1144 |  | 1600 | -456 | 71 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1135 |  | 1600 | -465 | 71 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1132 |  | 1600 | -468 | 71 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1130 |  | 1600 | -470 | 71 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1130 |  | 1600 | -470 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1128 |  | 1600 | -472 | 70 | []

## 1930Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3234
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1600 | 1600 | 1600 | 0 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1426 | 1600 | 1600 | -174 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1426 | 1600 | 1600 | -174 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1422 | 1600 | 1600 | -178 | 89 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1372 | 1600 | 1600 | -228 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1358 | 1600 | 1600 | -242 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1348 | 1600 | 1600 | -252 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1343 | 1600 | 1600 | -257 | 84 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1340 | 1600 | 1600 | -260 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1306 | 1600 | 1600 | -294 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1271 | 1600 | 1600 | -329 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 | 1600 | 1600 | -344 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 | 1600 | 1600 | -372 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 | 1600 | 1600 | -389 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1600 | 1600 | -396 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1600 | 1600 | -397 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 | 1600 | 1600 | -399 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1600 | 1600 | -403 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1600 | 1600 | -403 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1600 | 1600 | -404 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1194 | 1600 | 1600 | -406 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 | 1600 | 1600 | -408 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 | 1600 | 1600 | -411 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1600 | 1600 | -412 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1600 | 1600 | -412 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 | 1600 | 1600 | -417 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 | 1600 | 1600 | -426 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 | 1600 | 1600 | -434 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1165 | 1600 | 1600 | -435 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 | 1600 | 1600 | -440 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1152 | 1600 | 1600 | -448 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 | 1600 | 1600 | -451 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 | 1600 | 1600 | -452 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 | 1600 | 1600 | -458 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3234
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1600 |  | 1600 | 0 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1426 |  | 1600 | -174 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1426 |  | 1600 | -174 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1422 |  | 1600 | -178 | 89 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1372 |  | 1600 | -228 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1358 |  | 1600 | -242 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1348 |  | 1600 | -252 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1343 |  | 1600 | -257 | 84 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1340 |  | 1600 | -260 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1306 |  | 1600 | -294 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1271 |  | 1600 | -329 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1256 |  | 1600 | -344 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 |  | 1600 | -372 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1211 |  | 1600 | -389 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1600 | -396 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1600 | -397 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 |  | 1600 | -399 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1600 | -403 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1600 | -403 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1600 | -404 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1194 |  | 1600 | -406 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 |  | 1600 | -408 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 |  | 1600 | -411 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1600 | -412 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1600 | -412 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 |  | 1600 | -417 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 |  | 1600 | -426 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 |  | 1600 | -434 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1165 |  | 1600 | -435 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 |  | 1600 | -440 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1152 |  | 1600 | -448 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 |  | 1600 | -451 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 |  | 1600 | -452 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 |  | 1600 | -458 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3250
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1594 | 1600 | 1600 | -6 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1424 | 1600 | 1600 | -176 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1423 | 1600 | 1600 | -177 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1411 | 1600 | 1600 | -189 | 88 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1372 | 1600 | 1600 | -228 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1352 | 1600 | 1600 | -248 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1342 | 1600 | 1600 | -258 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 | 1600 | 1600 | -262 | 84 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1333 | 1600 | 1600 | -267 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1299 | 1600 | 1600 | -301 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1265 | 1600 | 1600 | -335 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 | 1600 | 1600 | -351 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 | 1600 | 1600 | -367 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 | 1600 | 1600 | -379 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 | 1600 | 1600 | -394 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1204 | 1600 | 1600 | -396 | 75 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1600 | 1600 | -403 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1600 | 1600 | -403 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 | 1600 | 1600 | -408 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 | 1600 | 1600 | -409 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 | 1600 | 1600 | -409 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 | 1600 | 1600 | -411 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 | 1600 | 1600 | -411 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1600 | 1600 | -412 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1187 | 1600 | 1600 | -413 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 | 1600 | 1600 | -417 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 | 1600 | 1600 | -418 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 | 1600 | 1600 | -418 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1600 | 1600 | -425 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1168 | 1600 | 1600 | -432 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1159 | 1600 | 1600 | -441 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1154 | 1600 | 1600 | -446 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 | 1600 | 1600 | -447 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1146 | 1600 | 1600 | -454 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 | 1600 | 1600 | -458 | 71 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1141 | 1600 | 1600 | -459 | 71 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 | 1600 | 1600 | -466 | 71 | []

## 2030Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3250
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1594 |  | 1600 | -6 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1424 |  | 1600 | -176 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1423 |  | 1600 | -177 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1411 |  | 1600 | -189 | 88 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1372 |  | 1600 | -228 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1352 |  | 1600 | -248 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1342 |  | 1600 | -258 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 |  | 1600 | -262 | 84 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1333 |  | 1600 | -267 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1299 |  | 1600 | -301 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1265 |  | 1600 | -335 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1249 |  | 1600 | -351 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 |  | 1600 | -367 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1221 |  | 1600 | -379 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 |  | 1600 | -394 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1204 |  | 1600 | -396 | 75 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1600 | -401 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1600 | -403 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1600 | -403 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 |  | 1600 | -408 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 |  | 1600 | -409 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 |  | 1600 | -409 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 |  | 1600 | -411 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 |  | 1600 | -411 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1600 | -412 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1187 |  | 1600 | -413 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 |  | 1600 | -417 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 |  | 1600 | -418 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 |  | 1600 | -418 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1600 | -425 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1168 |  | 1600 | -432 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1159 |  | 1600 | -441 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1154 |  | 1600 | -446 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 |  | 1600 | -447 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1146 |  | 1600 | -454 | 72 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 |  | 1600 | -458 | 71 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1141 |  | 1600 | -459 | 71 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 |  | 1600 | -466 | 71 | []

## 2130Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3335
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1598 | 1600 | 1600 | -2 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1432 | 1600 | 1600 | -168 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1431 | 1600 | 1600 | -169 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1412 | 1600 | 1600 | -188 | 88 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1374 | 1600 | 1600 | -226 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1357 | 1600 | 1600 | -243 | 85 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1342 | 1600 | 1600 | -258 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1341 | 1600 | 1600 | -259 | 84 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1325 | 1600 | 1600 | -275 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1300 | 1600 | 1600 | -300 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1269 | 1600 | 1600 | -331 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 | 1600 | 1600 | -356 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 | 1600 | 1600 | -367 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1600 | 1600 | -396 | 75 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 | 1600 | 1600 | -400 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 | 1600 | 1600 | -405 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 | 1600 | 1600 | -406 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 | 1600 | 1600 | -409 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 | 1600 | 1600 | -409 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 | 1600 | 1600 | -410 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 | 1600 | 1600 | -411 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 | 1600 | 1600 | -414 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 | 1600 | 1600 | -414 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 | 1600 | 1600 | -415 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 | 1600 | 1600 | -418 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 | 1600 | 1600 | -419 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1600 | 1600 | -420 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 | 1600 | 1600 | -427 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1172 | 1600 | 1600 | -428 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 | 1600 | 1600 | -434 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1158 | 1600 | 1600 | -442 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 | 1600 | 1600 | -449 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 | 1600 | 1600 | -451 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 | 1600 | 1600 | -458 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1138 | 1600 | 1600 | -462 | 71 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 | 1600 | 1600 | -468 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3335
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1598 |  | 1600 | -2 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1432 |  | 1600 | -168 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1431 |  | 1600 | -169 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1412 |  | 1600 | -188 | 88 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1374 |  | 1600 | -226 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1357 |  | 1600 | -243 | 85 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1342 |  | 1600 | -258 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1341 |  | 1600 | -259 | 84 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1325 |  | 1600 | -275 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1300 |  | 1600 | -300 | 81 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1277 |  | 1600 | -323 | 80 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1269 |  | 1600 | -331 | 79 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 |  | 1600 | -356 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 |  | 1600 | -367 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1600 | -396 | 75 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 |  | 1600 | -400 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1195 |  | 1600 | -405 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 |  | 1600 | -406 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 |  | 1600 | -409 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 |  | 1600 | -409 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 |  | 1600 | -410 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 |  | 1600 | -411 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 |  | 1600 | -414 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 |  | 1600 | -414 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 |  | 1600 | -415 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 |  | 1600 | -418 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 |  | 1600 | -419 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1600 | -420 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 |  | 1600 | -427 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1172 |  | 1600 | -428 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 |  | 1600 | -434 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1158 |  | 1600 | -442 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 |  | 1600 | -449 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 |  | 1600 | -451 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 |  | 1600 | -458 | 71 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1138 |  | 1600 | -462 | 71 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 |  | 1600 | -468 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3326
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1594 | 1600 | 1600 | -6 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1444 | 1600 | 1600 | -156 | 90 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1443 | 1600 | 1600 | -157 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1391 | 1600 | 1600 | -209 | 87 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1362 | 1600 | 1600 | -238 | 85 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1349 | 1600 | 1600 | -251 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 | 1600 | 1600 | -262 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1323 | 1600 | 1600 | -277 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1293 | 1600 | 1600 | -307 | 81 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 | 1600 | 1600 | -313 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1263 | 1600 | 1600 | -337 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 | 1600 | 1600 | -339 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 | 1600 | 1600 | -378 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 | 1600 | 1600 | -381 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1600 | 1600 | -393 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 | 1600 | 1600 | -410 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 | 1600 | 1600 | -414 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 | 1600 | 1600 | -416 | 74 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 | 1600 | 1600 | -419 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1600 | 1600 | -420 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 | 1600 | 1600 | -422 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 | 1600 | 1600 | -424 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1600 | 1600 | -425 | 73 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1600 | 1600 | -425 | 73 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 | 1600 | 1600 | -430 | 73 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 | 1600 | 1600 | -430 | 73 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1168 | 1600 | 1600 | -432 | 73 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1167 | 1600 | 1600 | -433 | 73 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 | 1600 | 1600 | -434 | 73 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 | 1600 | 1600 | -434 | 73 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1163 | 1600 | 1600 | -437 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1159 | 1600 | 1600 | -441 | 72 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 | 1600 | 1600 | -444 | 72 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 | 1600 | 1600 | -449 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 | 1600 | 1600 | -458 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1133 | 1600 | 1600 | -467 | 71 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 | 1600 | 1600 | -468 | 71 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1124 | 1600 | 1600 | -476 | 70 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1124 | 1600 | 1600 | -476 | 70 | []

## 2230Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3326
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1594 |  | 1600 | -6 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1444 |  | 1600 | -156 | 90 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1443 |  | 1600 | -157 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1391 |  | 1600 | -209 | 87 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1362 |  | 1600 | -238 | 85 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1349 |  | 1600 | -251 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1338 |  | 1600 | -262 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1323 |  | 1600 | -277 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1293 |  | 1600 | -307 | 81 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1287 |  | 1600 | -313 | 80 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1263 |  | 1600 | -337 | 79 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1261 |  | 1600 | -339 | 79 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1222 |  | 1600 | -378 | 76 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1219 |  | 1600 | -381 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1600 | -393 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 |  | 1600 | -410 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 |  | 1600 | -414 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 |  | 1600 | -416 | 74 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 |  | 1600 | -419 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1600 | -420 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 |  | 1600 | -422 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 |  | 1600 | -424 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1600 | -425 | 73 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1600 | -425 | 73 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 |  | 1600 | -430 | 73 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 |  | 1600 | -430 | 73 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1168 |  | 1600 | -432 | 73 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1167 |  | 1600 | -433 | 73 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 |  | 1600 | -434 | 73 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 |  | 1600 | -434 | 73 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1163 |  | 1600 | -437 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1159 |  | 1600 | -441 | 72 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 |  | 1600 | -444 | 72 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 |  | 1600 | -449 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 |  | 1600 | -458 | 71 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1133 |  | 1600 | -467 | 71 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1132 |  | 1600 | -468 | 71 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1124 |  | 1600 | -476 | 70 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1124 |  | 1600 | -476 | 70 | []

## 2330Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3522
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1598 | 1600 | 1600 | -2 | 100 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1464 | 1600 | 1600 | -136 | 92 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1433 | 1600 | 1600 | -167 | 90 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1433 | 1600 | 1600 | -167 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1426 | 1600 | 1600 | -174 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1378 | 1600 | 1600 | -222 | 86 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1350 | 1600 | 1600 | -250 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1349 | 1600 | 1600 | -251 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1335 | 1600 | 1600 | -265 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1326 | 1600 | 1600 | -274 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1301 | 1600 | 1600 | -299 | 81 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1298 | 1600 | 1600 | -302 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1281 | 1600 | 1600 | -319 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 | 1600 | 1600 | -371 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1227 | 1600 | 1600 | -373 | 77 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1227 | 1600 | 1600 | -373 | 77 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1226 | 1600 | 1600 | -374 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 | 1600 | 1600 | -384 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1600 | 1600 | -388 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1600 | 1600 | -395 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 | 1600 | 1600 | -406 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 | 1600 | 1600 | -410 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 | 1600 | 1600 | -411 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 | 1600 | 1600 | -411 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1600 | 1600 | -412 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 | 1600 | 1600 | -415 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 | 1600 | 1600 | -416 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 | 1600 | 1600 | -419 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 | 1600 | 1600 | -419 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 | 1600 | 1600 | -419 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 | 1600 | 1600 | -421 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 | 1600 | 1600 | -421 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1179 | 1600 | 1600 | -421 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 | 1600 | 1600 | -428 | 73 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 | 1600 | 1600 | -428 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 | 1600 | 1600 | -430 | 73 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1163 | 1600 | 1600 | -437 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 | 1600 | 1600 | -440 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 | 1600 | 1600 | -440 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 | 1600 | 1600 | -444 | 72 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1141 | 1600 | 1600 | -459 | 71 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1141 | 1600 | 1600 | -459 | 71 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1140 | 1600 | 1600 | -460 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1139 | 1600 | 1600 | -461 | 71 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1139 | 1600 | 1600 | -461 | 71 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1136 | 1600 | 1600 | -464 | 71 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1129 | 1600 | 1600 | -471 | 71 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1126 | 1600 | 1600 | -474 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3522
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1598 |  | 1600 | -2 | 100 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1464 |  | 1600 | -136 | 92 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1433 |  | 1600 | -167 | 90 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1433 |  | 1600 | -167 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1426 |  | 1600 | -174 | 89 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1378 |  | 1600 | -222 | 86 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1350 |  | 1600 | -250 | 84 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1349 |  | 1600 | -251 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1335 |  | 1600 | -265 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1326 |  | 1600 | -274 | 83 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1301 |  | 1600 | -299 | 81 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1298 |  | 1600 | -302 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1281 |  | 1600 | -319 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1229 |  | 1600 | -371 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1227 |  | 1600 | -373 | 77 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1227 |  | 1600 | -373 | 77 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-TR] [OPP] TIE 400 kV Nea Santa - Babaeski | XNS_BA11_GNSANT11_1:line | 1226 |  | 1600 | -374 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 |  | 1600 | -384 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1600 | -388 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1600 | -395 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 |  | 1600 | -406 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 |  | 1600 | -410 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 |  | 1600 | -411 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 |  | 1600 | -411 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1600 | -412 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 |  | 1600 | -415 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 |  | 1600 | -416 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 |  | 1600 | -419 | 74 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 |  | 1600 | -419 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 |  | 1600 | -419 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 |  | 1600 | -421 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 |  | 1600 | -421 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1179 |  | 1600 | -421 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 |  | 1600 | -428 | 73 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 |  | 1600 | -428 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 |  | 1600 | -430 | 73 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1163 |  | 1600 | -437 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 |  | 1600 | -440 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1160 |  | 1600 | -440 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 |  | 1600 | -444 | 72 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1141 |  | 1600 | -459 | 71 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1141 |  | 1600 | -459 | 71 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1140 |  | 1600 | -460 | 71 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1139 |  | 1600 | -461 | 71 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1139 |  | 1600 | -461 | 71 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1136 |  | 1600 | -464 | 71 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1129 |  | 1600 | -471 | 71 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | 1126 |  | 1600 | -474 | 70 | []