## 1230Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 1648
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1232 | -1248 | -1248 | -17 | 99 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1226 | -1248 | -1248 | -23 | 98 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1169 | -1248 | -1248 | -80 | 94 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -992 | -1248 | -1248 | -257 | 79 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -977 | -1248 | -1248 | -272 | 78 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -909 | -1248 | -1248 | -340 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -908 | -1248 | -1248 | -341 | 73 | []

## 1230Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 1648
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1232 |  | -1248 | -17 | 99 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1226 |  | -1248 | -23 | 98 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1169 |  | -1248 | -80 | 94 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -992 |  | -1248 | -257 | 79 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -977 |  | -1248 | -272 | 78 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -909 |  | -1248 | -340 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -908 |  | -1248 | -341 | 73 | []

## 1330Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3666
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1340 | 1570 | 1570 | -230 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1340 | 1570 | 1570 | -230 | 85 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1317 | 1570 | 1570 | -253 | 84 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1316 | 1570 | 1570 | -254 | 84 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1306 | 1570 | 1570 | -264 | 83 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1024 | -1248 | -1248 | -224 | 82 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1021 | -1248 | -1248 | -227 | 82 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1267 | 1570 | 1570 | -303 | 81 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1267 | 1570 | 1570 | -303 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1267 | 1570 | 1570 | -303 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1257 | 1570 | 1570 | -313 | 80 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1253 | 1570 | 1570 | -317 | 80 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1251 | 1570 | 1570 | -319 | 80 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1244 | 1570 | 1570 | -326 | 79 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1222 | 1570 | 1570 | -348 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1205 | 1570 | 1570 | -365 | 77 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1417 | 1890 | 1890 | -473 | 75 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1417 | 1890 | 1890 | -473 | 75 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1414 | 1920 | 1920 | -506 | 74 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1414 | 1920 | 1920 | -506 | 74 | []

## 1330Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3666
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1340 |  | 1570 | -230 | 85 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1340 |  | 1570 | -230 | 85 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1317 |  | 1570 | -253 | 84 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1316 |  | 1570 | -254 | 84 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1306 |  | 1570 | -264 | 83 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1024 |  | -1248 | -224 | 82 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1021 |  | -1248 | -227 | 82 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1267 |  | 1570 | -303 | 81 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1267 |  | 1570 | -303 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1267 |  | 1570 | -303 | 81 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1257 |  | 1570 | -313 | 80 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1253 |  | 1570 | -317 | 80 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1251 |  | 1570 | -319 | 80 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1244 |  | 1570 | -326 | 79 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1222 |  | 1570 | -348 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1205 |  | 1570 | -365 | 77 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1417 |  | 1890 | -473 | 75 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1417 |  | 1890 | -473 | 75 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1414 |  | 1920 | -506 | 74 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1414 |  | 1920 | -506 | 74 | []

## 1430Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3696
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1330 | 1570 | 1570 | -240 | 85 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1330 | 1570 | 1570 | -240 | 85 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1297 | 1570 | 1570 | -273 | 83 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1296 | 1570 | 1570 | -274 | 83 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1029 | -1248 | -1248 | -220 | 82 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1026 | -1248 | -1248 | -223 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1280 | 1570 | 1570 | -290 | 82 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1251 | 1570 | 1570 | -319 | 80 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1250 | 1570 | 1570 | -320 | 80 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1249 | 1570 | 1570 | -321 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1238 | 1570 | 1570 | -332 | 79 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1234 | 1570 | 1570 | -336 | 79 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1232 | 1570 | 1570 | -338 | 78 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1230 | 1570 | 1570 | -340 | 78 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1466 | 1890 | 1890 | -424 | 78 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1466 | 1890 | 1890 | -424 | 78 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1205 | 1570 | 1570 | -365 | 77 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1464 | 1920 | 1920 | -456 | 76 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1464 | 1920 | 1920 | -456 | 76 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1191 | 1570 | 1570 | -379 | 76 | []

## 1430Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3696
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1330 |  | 1570 | -240 | 85 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1330 |  | 1570 | -240 | 85 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1297 |  | 1570 | -273 | 83 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1296 |  | 1570 | -274 | 83 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1029 |  | -1248 | -220 | 82 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1026 |  | -1248 | -223 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1280 |  | 1570 | -290 | 82 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1251 |  | 1570 | -319 | 80 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1250 |  | 1570 | -320 | 80 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1249 |  | 1570 | -321 | 80 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1238 |  | 1570 | -332 | 79 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1234 |  | 1570 | -336 | 79 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1232 |  | 1570 | -338 | 78 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1230 |  | 1570 | -340 | 78 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1466 |  | 1890 | -424 | 78 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1466 |  | 1890 | -424 | 78 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1205 |  | 1570 | -365 | 77 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1464 |  | 1920 | -456 | 76 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1464 |  | 1920 | -456 | 76 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1191 |  | 1570 | -379 | 76 | []

## 1530Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3528
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 | 1570 | 1570 | -202 | 87 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 | 1570 | 1570 | -202 | 87 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1366 | 1570 | 1570 | -204 | 87 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1359 | 1570 | 1570 | -211 | 87 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1358 | 1570 | 1570 | -212 | 86 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1052 | -1248 | -1248 | -197 | 84 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1049 | -1248 | -1248 | -200 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1309 | 1570 | 1570 | -261 | 83 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1307 | 1570 | 1570 | -263 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1306 | 1570 | 1570 | -264 | 83 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1306 | 1570 | 1570 | -264 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1292 | 1570 | 1570 | -278 | 82 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1292 | 1570 | 1570 | -278 | 82 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1281 | 1570 | 1570 | -289 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1276 | 1570 | 1570 | -294 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1243 | 1570 | 1570 | -327 | 79 | []

## 1530Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3528
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 |  | 1570 | -202 | 87 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 |  | 1570 | -202 | 87 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1366 |  | 1570 | -204 | 87 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1359 |  | 1570 | -211 | 87 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1358 |  | 1570 | -212 | 86 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1052 |  | -1248 | -197 | 84 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1049 |  | -1248 | -200 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1309 |  | 1570 | -261 | 83 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1307 |  | 1570 | -263 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1306 |  | 1570 | -264 | 83 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1306 |  | 1570 | -264 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1292 |  | 1570 | -278 | 82 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1292 |  | 1570 | -278 | 82 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1281 |  | 1570 | -289 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1276 |  | 1570 | -294 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1243 |  | 1570 | -327 | 79 | []

## 1630Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3501
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1416 | -1570 | -1570 | -154 | 90 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1416 | -1570 | -1570 | -154 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1387 | -1570 | -1570 | -183 | 88 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1385 | -1570 | -1570 | -185 | 88 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1351 | -1570 | -1570 | -219 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1340 | -1570 | -1570 | -230 | 85 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 | -1570 | -1570 | -242 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 | -1570 | -1570 | -242 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 | -1570 | -1570 | -242 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1317 | -1570 | -1570 | -253 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1316 | -1570 | -1570 | -254 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1313 | -1570 | -1570 | -257 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1297 | -1570 | -1570 | -273 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1260 | -1570 | -1570 | -310 | 80 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1325 | 1890 | 1890 | -565 | 70 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1325 | 1890 | 1890 | -565 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3501
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1416 |  | -1570 | -154 | 90 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1416 |  | -1570 | -154 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1387 |  | -1570 | -183 | 88 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1385 |  | -1570 | -185 | 88 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1351 |  | -1570 | -219 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1340 |  | -1570 | -230 | 85 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 |  | -1570 | -242 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 |  | -1570 | -242 | 85 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 |  | -1570 | -242 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1317 |  | -1570 | -253 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1316 |  | -1570 | -254 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1313 |  | -1570 | -257 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1297 |  | -1570 | -273 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1260 |  | -1570 | -310 | 80 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1325 |  | 1890 | -565 | 70 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1325 |  | 1890 | -565 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3408
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1157 | -1248 | -1248 | -91 | 93 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1153 | -1248 | -1248 | -95 | 92 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1151 | -1248 | -1248 | -97 | 92 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1147 | -1248 | -1248 | -102 | 92 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1141 | -1248 | -1248 | -108 | 91 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1140 | -1248 | -1248 | -108 | 91 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1433 | -1570 | -1570 | -137 | 91 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1433 | -1570 | -1570 | -137 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1392 | -1570 | -1570 | -178 | 89 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1391 | -1570 | -1570 | -179 | 89 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1377 | -1570 | -1570 | -193 | 88 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1372 | -1570 | -1570 | -198 | 87 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1348 | -1570 | -1570 | -222 | 86 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1343 | -1570 | -1570 | -227 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1341 | -1570 | -1570 | -229 | 85 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1336 | -1570 | -1570 | -234 | 85 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1330 | -1570 | -1570 | -240 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 | -1570 | -1570 | -242 | 85 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1307 | -1570 | -1570 | -263 | 83 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1282 | -1570 | -1570 | -288 | 82 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1386 | 1890 | 1890 | -504 | 73 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1386 | 1890 | 1890 | -504 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -910 | -1248 | -1248 | -338 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -909 | -1248 | -1248 | -339 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -903 | -1248 | -1248 | -345 | 72 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1383 | 1920 | 1920 | -537 | 72 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1383 | 1920 | 1920 | -537 | 72 | []

## 1730Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3408
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1157 |  | -1248 | -91 | 93 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1153 |  | -1248 | -95 | 92 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1151 |  | -1248 | -97 | 92 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1147 |  | -1248 | -102 | 92 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1141 |  | -1248 | -108 | 91 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1140 |  | -1248 | -108 | 91 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1433 |  | -1570 | -137 | 91 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1433 |  | -1570 | -137 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1392 |  | -1570 | -178 | 89 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1391 |  | -1570 | -179 | 89 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1377 |  | -1570 | -193 | 88 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1372 |  | -1570 | -198 | 87 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1348 |  | -1570 | -222 | 86 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1343 |  | -1570 | -227 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1341 |  | -1570 | -229 | 85 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1336 |  | -1570 | -234 | 85 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1330 |  | -1570 | -240 | 85 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 |  | -1570 | -242 | 85 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1307 |  | -1570 | -263 | 83 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1282 |  | -1570 | -288 | 82 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1386 |  | 1890 | -504 | 73 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1386 |  | 1890 | -504 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -910 |  | -1248 | -338 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -909 |  | -1248 | -339 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -903 |  | -1248 | -345 | 72 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1383 |  | 1920 | -537 | 72 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1383 |  | 1920 | -537 | 72 | []

## 1830Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3172
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1155 | -1248 | -1248 | -94 | 93 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1151 | -1248 | -1248 | -98 | 92 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1149 | -1248 | -1248 | -99 | 92 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1144 | -1248 | -1248 | -104 | 92 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1139 | -1248 | -1248 | -109 | 91 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1138 | -1248 | -1248 | -110 | 91 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1365 | 1570 | 1570 | -205 | 87 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1365 | 1570 | 1570 | -205 | 87 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1361 | 1570 | 1570 | -209 | 87 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1348 | 1570 | 1570 | -222 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1347 | 1570 | 1570 | -223 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1326 | 1570 | 1570 | -244 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1309 | 1570 | 1570 | -261 | 83 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1301 | 1570 | 1570 | -269 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1287 | 1570 | 1570 | -283 | 82 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1284 | 1570 | 1570 | -286 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1283 | 1570 | 1570 | -287 | 82 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1266 | 1570 | 1570 | -304 | 81 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1265 | 1570 | 1570 | -305 | 81 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1223 | 1570 | 1570 | -347 | 78 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -929 | -1248 | -1248 | -320 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -928 | -1248 | -1248 | -320 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -923 | -1248 | -1248 | -326 | 74 | []

## 1830Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3172
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1155 |  | -1248 | -94 | 93 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1151 |  | -1248 | -98 | 92 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1149 |  | -1248 | -99 | 92 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1144 |  | -1248 | -104 | 92 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1139 |  | -1248 | -109 | 91 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1138 |  | -1248 | -110 | 91 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1365 |  | 1570 | -205 | 87 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1365 |  | 1570 | -205 | 87 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1361 |  | 1570 | -209 | 87 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1348 |  | 1570 | -222 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1347 |  | 1570 | -223 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1326 |  | 1570 | -244 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1309 |  | 1570 | -261 | 83 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1301 |  | 1570 | -269 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1287 |  | 1570 | -283 | 82 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1284 |  | 1570 | -286 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1283 |  | 1570 | -287 | 82 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1266 |  | 1570 | -304 | 81 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1265 |  | 1570 | -305 | 81 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1223 |  | 1570 | -347 | 78 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -929 |  | -1248 | -320 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -928 |  | -1248 | -320 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -923 |  | -1248 | -326 | 74 | []

## 1930Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3040
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1491 | 1570 | 1570 | -79 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1490 | 1570 | 1570 | -80 | 95 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1490 | 1570 | 1570 | -80 | 95 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 | 1570 | 1570 | -102 | 93 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1466 | 1570 | 1570 | -104 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1466 | 1570 | 1570 | -104 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 | 1570 | 1570 | -118 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1449 | 1570 | 1570 | -121 | 92 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1432 | 1570 | 1570 | -138 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1428 | 1570 | 1570 | -142 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 | 1570 | 1570 | -148 | 91 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1420 | 1570 | 1570 | -150 | 90 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1115 | -1248 | -1248 | -133 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1399 | 1570 | 1570 | -171 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1111 | -1248 | -1248 | -137 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1110 | -1248 | -1248 | -138 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1104 | -1248 | -1248 | -144 | 88 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1386 | 1570 | 1570 | -184 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1100 | -1248 | -1248 | -148 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1099 | -1248 | -1248 | -150 | 88 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -936 | -1248 | -1248 | -312 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -935 | -1248 | -1248 | -313 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -931 | -1248 | -1248 | -318 | 75 | []

## 1930Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3040
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1491 |  | 1570 | -79 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1490 |  | 1570 | -80 | 95 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1490 |  | 1570 | -80 | 95 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 |  | 1570 | -102 | 93 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1466 |  | 1570 | -104 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1466 |  | 1570 | -104 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1570 | -118 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1449 |  | 1570 | -121 | 92 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1432 |  | 1570 | -138 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1428 |  | 1570 | -142 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 |  | 1570 | -148 | 91 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1420 |  | 1570 | -150 | 90 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1115 |  | -1248 | -133 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1399 |  | 1570 | -171 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1111 |  | -1248 | -137 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1110 |  | -1248 | -138 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1104 |  | -1248 | -144 | 88 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1386 |  | 1570 | -184 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1100 |  | -1248 | -148 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1099 |  | -1248 | -150 | 88 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -936 |  | -1248 | -312 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -935 |  | -1248 | -313 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -931 |  | -1248 | -318 | 75 | []

## 2030Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3086
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 | 1570 | 1570 | -98 | 94 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1471 | 1570 | 1570 | -99 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 | 1570 | 1570 | -101 | 94 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1449 | 1570 | 1570 | -121 | 92 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 | 1570 | 1570 | -126 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 | 1570 | 1570 | -126 | 92 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1431 | 1570 | 1570 | -139 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1428 | 1570 | 1570 | -142 | 91 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1408 | 1570 | 1570 | -162 | 90 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1407 | 1570 | 1570 | -163 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1401 | 1570 | 1570 | -169 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 | 1570 | 1570 | -170 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1106 | -1248 | -1248 | -142 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1102 | -1248 | -1248 | -147 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1101 | -1248 | -1248 | -147 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1380 | 1570 | 1570 | -190 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1095 | -1248 | -1248 | -153 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1091 | -1248 | -1248 | -157 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1090 | -1248 | -1248 | -159 | 87 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1365 | 1570 | 1570 | -205 | 87 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -931 | -1248 | -1248 | -317 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -931 | -1248 | -1248 | -318 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -926 | -1248 | -1248 | -322 | 74 | []

## 2030Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3086
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 |  | 1570 | -98 | 94 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1471 |  | 1570 | -99 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 |  | 1570 | -101 | 94 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1449 |  | 1570 | -121 | 92 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1570 | -126 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1444 |  | 1570 | -126 | 92 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1431 |  | 1570 | -139 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1428 |  | 1570 | -142 | 91 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1408 |  | 1570 | -162 | 90 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1407 |  | 1570 | -163 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1401 |  | 1570 | -169 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 |  | 1570 | -170 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1106 |  | -1248 | -142 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1102 |  | -1248 | -147 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1101 |  | -1248 | -147 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1380 |  | 1570 | -190 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1095 |  | -1248 | -153 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1091 |  | -1248 | -157 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1090 |  | -1248 | -159 | 87 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1365 |  | 1570 | -205 | 87 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -931 |  | -1248 | -317 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -931 |  | -1248 | -318 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -926 |  | -1248 | -322 | 74 | []

## 2130Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3126
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 | 1570 | 1570 | -83 | 95 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 | 1570 | 1570 | -106 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 | 1570 | 1570 | -107 | 93 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 | 1570 | 1570 | -117 | 93 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 | 1570 | 1570 | -128 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 | 1570 | 1570 | -128 | 92 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1430 | 1570 | 1570 | -140 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1426 | 1570 | 1570 | -144 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1403 | 1570 | 1570 | -167 | 89 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 | 1570 | 1570 | -170 | 89 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1395 | 1570 | 1570 | -175 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1394 | 1570 | 1570 | -176 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1372 | 1570 | 1570 | -198 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1088 | -1248 | -1248 | -160 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1084 | -1248 | -1248 | -164 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1084 | -1248 | -1248 | -165 | 87 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1361 | 1570 | 1570 | -209 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1077 | -1248 | -1248 | -171 | 86 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1074 | -1248 | -1248 | -175 | 86 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1072 | -1248 | -1248 | -176 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -936 | -1248 | -1248 | -312 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -935 | -1248 | -1248 | -313 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -932 | -1248 | -1248 | -317 | 75 | []

## 2130Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3126
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 |  | 1570 | -83 | 95 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 |  | 1570 | -106 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1463 |  | 1570 | -107 | 93 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 |  | 1570 | -117 | 93 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 |  | 1570 | -128 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 |  | 1570 | -128 | 92 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1430 |  | 1570 | -140 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1426 |  | 1570 | -144 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1403 |  | 1570 | -167 | 89 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 |  | 1570 | -170 | 89 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1395 |  | 1570 | -175 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1394 |  | 1570 | -176 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1372 |  | 1570 | -198 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1088 |  | -1248 | -160 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1084 |  | -1248 | -164 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1084 |  | -1248 | -165 | 87 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1361 |  | 1570 | -209 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1077 |  | -1248 | -171 | 86 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1074 |  | -1248 | -175 | 86 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1072 |  | -1248 | -176 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -936 |  | -1248 | -312 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -935 |  | -1248 | -313 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -932 |  | -1248 | -317 | 75 | []

## 2230Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3351
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 | 1570 | 1570 | -98 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1471 | 1570 | 1570 | -99 | 94 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1470 | 1570 | 1570 | -100 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 | 1570 | 1570 | -106 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 | 1570 | 1570 | -106 | 93 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 | 1570 | 1570 | -119 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1423 | 1570 | 1570 | -147 | 91 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 | 1570 | 1570 | -155 | 90 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1406 | 1570 | 1570 | -164 | 90 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 | 1570 | 1570 | -165 | 89 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 | 1570 | 1570 | -168 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1397 | 1570 | 1570 | -173 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1394 | 1570 | 1570 | -176 | 89 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1375 | 1570 | 1570 | -195 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1073 | -1248 | -1248 | -176 | 86 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1069 | -1248 | -1248 | -179 | 86 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1067 | -1248 | -1248 | -182 | 85 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1062 | -1248 | -1248 | -186 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1057 | -1248 | -1248 | -191 | 85 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1056 | -1248 | -1248 | -192 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -933 | -1248 | -1248 | -315 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -932 | -1248 | -1248 | -316 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -927 | -1248 | -1248 | -322 | 74 | []

## 2230Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3351
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 |  | 1570 | -98 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1471 |  | 1570 | -99 | 94 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1470 |  | 1570 | -100 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 |  | 1570 | -106 | 93 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1464 |  | 1570 | -106 | 93 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 |  | 1570 | -119 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1423 |  | 1570 | -147 | 91 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 |  | 1570 | -155 | 90 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1406 |  | 1570 | -164 | 90 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 |  | 1570 | -165 | 89 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 |  | 1570 | -168 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1397 |  | 1570 | -173 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1394 |  | 1570 | -176 | 89 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1375 |  | 1570 | -195 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1073 |  | -1248 | -176 | 86 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1069 |  | -1248 | -179 | 86 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1067 |  | -1248 | -182 | 85 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1062 |  | -1248 | -186 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1057 |  | -1248 | -191 | 85 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1056 |  | -1248 | -192 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -933 |  | -1248 | -315 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -932 |  | -1248 | -316 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -927 |  | -1248 | -322 | 74 | []

## 2330Preventive
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3502
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1448 | 1570 | 1570 | -122 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1448 | 1570 | 1570 | -122 | 92 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1431 | 1570 | 1570 | -139 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 | 1570 | 1570 | -141 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 | 1570 | 1570 | -141 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 | 1570 | 1570 | -168 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1107 | -1248 | -1248 | -141 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1104 | -1248 | -1248 | -145 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1101 | -1248 | -1248 | -147 | 88 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1384 | 1570 | 1570 | -186 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1097 | -1248 | -1248 | -152 | 88 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1376 | 1570 | 1570 | -194 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1091 | -1248 | -1248 | -157 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1091 | -1248 | -1248 | -158 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 | 1570 | 1570 | -202 | 87 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1365 | 1570 | 1570 | -205 | 87 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1359 | 1570 | 1570 | -211 | 87 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1356 | 1570 | 1570 | -214 | 86 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1348 | 1570 | 1570 | -222 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1334 | 1570 | 1570 | -236 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -938 | -1248 | -1248 | -311 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -937 | -1248 | -1248 | -311 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -931 | -1248 | -1248 | -318 | 75 | []

## 2330Curative
Detailed results
Generated at: | 2026-05-19 08:32
Business day: | 19.05.2026
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3502
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1448 |  | 1570 | -122 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1448 |  | 1570 | -122 | 92 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1431 |  | 1570 | -139 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 |  | 1570 | -141 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 |  | 1570 | -141 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 |  | 1570 | -168 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1107 |  | -1248 | -141 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1104 |  | -1248 | -145 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1101 |  | -1248 | -147 | 88 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1384 |  | 1570 | -186 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1097 |  | -1248 | -152 | 88 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1376 |  | 1570 | -194 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1091 |  | -1248 | -157 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1091 |  | -1248 | -158 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 |  | 1570 | -202 | 87 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1365 |  | 1570 | -205 | 87 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1359 |  | 1570 | -211 | 87 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1356 |  | 1570 | -214 | 86 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1348 |  | 1570 | -222 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1334 |  | 1570 | -236 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -938 |  | -1248 | -311 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -937 |  | -1248 | -311 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -931 |  | -1248 | -318 | 75 | []