## 0030Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 00:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3270
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1561 | 1570 | 1570 | -9 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1561 | 1570 | 1570 | -9 | 99 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1430 | 1570 | 1570 | -140 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 | 1570 | 1570 | -141 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1428 | 1570 | 1570 | -142 | 91 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1423 | 1570 | 1570 | -147 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1414 | 1570 | 1570 | -156 | 90 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1414 | 1570 | 1570 | -156 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 | 1570 | 1570 | -161 | 90 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 | 1570 | 1570 | -168 | 89 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1383 | 1570 | 1570 | -187 | 88 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1354 | 1570 | 1570 | -216 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1320 | 1570 | 1570 | -250 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1315 | 1570 | 1570 | -255 | 84 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1536 | 1890 | 1890 | -354 | 81 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1536 | 1890 | 1890 | -354 | 81 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1523 | 1920 | 1920 | -397 | 79 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1523 | 1920 | 1920 | -397 | 79 | []

## 0030Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 00:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3270
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1561 |  | 1570 | -9 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1561 |  | 1570 | -9 | 99 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1430 |  | 1570 | -140 | 91 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 |  | 1570 | -141 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1428 |  | 1570 | -142 | 91 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1423 |  | 1570 | -147 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1414 |  | 1570 | -156 | 90 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1414 |  | 1570 | -156 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 |  | 1570 | -161 | 90 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 |  | 1570 | -168 | 89 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1383 |  | 1570 | -187 | 88 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1354 |  | 1570 | -216 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1320 |  | 1570 | -250 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1315 |  | 1570 | -255 | 84 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1536 |  | 1890 | -354 | 81 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1536 |  | 1890 | -354 | 81 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1523 |  | 1920 | -397 | 79 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1523 |  | 1920 | -397 | 79 | []

## 0130Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 01:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3598
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1564 | 1570 | 1570 | -6 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1564 | 1570 | 1570 | -6 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 | 1570 | 1570 | -101 | 94 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 | 1570 | 1570 | -103 | 93 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1456 | 1570 | 1570 | -114 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1449 | 1570 | 1570 | -121 | 92 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 | 1570 | 1570 | -129 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 | 1570 | 1570 | -131 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 | 1570 | 1570 | -135 | 91 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 | 1570 | 1570 | -143 | 91 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1713 | 1890 | 1890 | -177 | 91 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1713 | 1890 | 1890 | -177 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 | 1570 | 1570 | -165 | 89 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1701 | 1920 | 1920 | -219 | 89 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1701 | 1920 | 1920 | -219 | 89 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1345 | 1570 | 1570 | -225 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1339 | 1570 | 1570 | -231 | 85 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1336 | 1570 | 1570 | -234 | 85 | []

## 0130Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 01:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3598
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1564 |  | 1570 | -6 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1564 |  | 1570 | -6 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 |  | 1570 | -101 | 94 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 |  | 1570 | -103 | 93 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1456 |  | 1570 | -114 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1449 |  | 1570 | -121 | 92 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 |  | 1570 | -129 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 |  | 1570 | -131 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1570 | -135 | 91 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1570 | -143 | 91 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1713 |  | 1890 | -177 | 91 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1713 |  | 1890 | -177 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1405 |  | 1570 | -165 | 89 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1701 |  | 1920 | -219 | 89 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1701 |  | 1920 | -219 | 89 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1345 |  | 1570 | -225 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1339 |  | 1570 | -231 | 85 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1336 |  | 1570 | -234 | 85 | []

## 0230Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 02:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3683
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 | 1570 | 1570 | 0 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 | 1570 | 1570 | 0 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 | 1570 | 1570 | -95 | 94 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1474 | 1570 | 1570 | -96 | 94 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1459 | 1570 | 1570 | -111 | 93 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1753 | 1890 | 1890 | -137 | 93 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1753 | 1890 | 1890 | -137 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 | 1570 | 1570 | -117 | 93 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1445 | 1570 | 1570 | -125 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1443 | 1570 | 1570 | -127 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 | 1570 | 1570 | -131 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 | 1570 | 1570 | -141 | 91 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1742 | 1920 | 1920 | -178 | 91 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1742 | 1920 | 1920 | -178 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1406 | 1570 | 1570 | -164 | 90 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1348 | 1570 | 1570 | -222 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1338 | 1570 | 1570 | -232 | 85 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1336 | 1570 | 1570 | -234 | 85 | []

## 0230Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 02:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3683
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 |  | 1570 | 0 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1570 |  | 1570 | 0 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 |  | 1570 | -95 | 94 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1474 |  | 1570 | -96 | 94 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1459 |  | 1570 | -111 | 93 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1753 |  | 1890 | -137 | 93 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1753 |  | 1890 | -137 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 |  | 1570 | -117 | 93 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1570 | -125 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1443 |  | 1570 | -127 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 |  | 1570 | -131 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1429 |  | 1570 | -141 | 91 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1742 |  | 1920 | -178 | 91 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1742 |  | 1920 | -178 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1406 |  | 1570 | -164 | 90 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1348 |  | 1570 | -222 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1338 |  | 1570 | -232 | 85 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1336 |  | 1570 | -234 | 85 | []

## 0330Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 03:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3859
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1559 | 1570 | 1570 | -11 | 99 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1559 | 1570 | 1570 | -11 | 99 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1863 | 1890 | 1890 | -27 | 99 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1863 | 1890 | 1890 | -27 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1852 | 1920 | 1920 | -68 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1852 | 1920 | 1920 | -68 | 96 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 | 1570 | 1570 | -108 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 | 1570 | 1570 | -109 | 93 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 | 1570 | 1570 | -128 | 92 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 | 1570 | 1570 | -134 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 | 1570 | 1570 | -143 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1425 | 1570 | 1570 | -145 | 91 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1419 | 1570 | 1570 | -151 | 90 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1410 | 1570 | 1570 | -160 | 90 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1387 | 1570 | 1570 | -183 | 88 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1328 | 1570 | 1570 | -242 | 85 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1322 | 1570 | 1570 | -248 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1314 | 1570 | 1570 | -256 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1349 | 1890 | 1890 | -541 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1349 | 1890 | 1890 | -541 | 71 | []

## 0330Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 03:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3859
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1559 |  | 1570 | -11 | 99 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1559 |  | 1570 | -11 | 99 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1863 |  | 1890 | -27 | 99 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1863 |  | 1890 | -27 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1852 |  | 1920 | -68 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1852 |  | 1920 | -68 | 96 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1462 |  | 1570 | -108 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 |  | 1570 | -109 | 93 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 |  | 1570 | -128 | 92 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1436 |  | 1570 | -134 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1570 | -143 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1425 |  | 1570 | -145 | 91 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1419 |  | 1570 | -151 | 90 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1410 |  | 1570 | -160 | 90 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1387 |  | 1570 | -183 | 88 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1328 |  | 1570 | -242 | 85 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1322 |  | 1570 | -248 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1314 |  | 1570 | -256 | 84 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1349 |  | 1890 | -541 | 71 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1349 |  | 1890 | -541 | 71 | []

## 0430Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 04:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3870
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1531 | 1570 | 1570 | -39 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1531 | 1570 | 1570 | -39 | 98 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1842 | 1890 | 1890 | -48 | 97 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1842 | 1890 | 1890 | -48 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1831 | 1920 | 1920 | -89 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1831 | 1920 | 1920 | -89 | 95 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 | 1570 | 1570 | -129 | 92 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 | 1570 | 1570 | -131 | 92 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 | 1570 | 1570 | -153 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1408 | 1570 | 1570 | -162 | 90 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 | 1570 | 1570 | -168 | 89 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 | 1570 | 1570 | -170 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1393 | 1570 | 1570 | -177 | 89 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1383 | 1570 | 1570 | -187 | 88 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1357 | 1570 | 1570 | -213 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1305 | 1570 | 1570 | -265 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1305 | 1570 | 1570 | -265 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1288 | 1570 | 1570 | -282 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1332 | 1890 | 1890 | -558 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1332 | 1890 | 1890 | -558 | 70 | []

## 0430Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 04:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3870
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1531 |  | 1570 | -39 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1531 |  | 1570 | -39 | 98 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1842 |  | 1890 | -48 | 97 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1842 |  | 1890 | -48 | 97 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1831 |  | 1920 | -89 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1831 |  | 1920 | -89 | 95 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 |  | 1570 | -129 | 92 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1439 |  | 1570 | -131 | 92 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 |  | 1570 | -153 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1408 |  | 1570 | -162 | 90 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1402 |  | 1570 | -168 | 89 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1400 |  | 1570 | -170 | 89 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1393 |  | 1570 | -177 | 89 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1383 |  | 1570 | -187 | 88 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1357 |  | 1570 | -213 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1305 |  | 1570 | -265 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1305 |  | 1570 | -265 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1288 |  | 1570 | -282 | 82 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1332 |  | 1890 | -558 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1332 |  | 1890 | -558 | 70 | []

## 0530Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 05:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3836
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1848 | 1890 | 1890 | -42 | 98 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1848 | 1890 | 1890 | -42 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1836 | 1920 | 1920 | -84 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1836 | 1920 | 1920 | -84 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 | 1570 | 1570 | -118 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 | 1570 | 1570 | -118 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1355 | 1570 | 1570 | -215 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1353 | 1570 | 1570 | -217 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1333 | 1570 | 1570 | -237 | 85 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1316 | 1570 | 1570 | -254 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1315 | 1570 | 1570 | -255 | 84 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1314 | 1570 | 1570 | -256 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1310 | 1570 | 1570 | -260 | 83 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1306 | 1570 | 1570 | -264 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1265 | 1570 | 1570 | -305 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1223 | 1570 | 1570 | -347 | 78 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1221 | 1570 | 1570 | -349 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1210 | 1570 | 1570 | -360 | 77 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1480 | 2000 | 2000 | -520 | 74 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1472 | -2000 | -2000 | -528 | 74 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1461 | 2000 | 2000 | -539 | 73 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1453 | -2000 | -2000 | -547 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1324 | 1890 | 1890 | -566 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1324 | 1890 | 1890 | -566 | 70 | []

## 0530Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 05:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3836
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1848 |  | 1890 | -42 | 98 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1848 |  | 1890 | -42 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1836 |  | 1920 | -84 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1836 |  | 1920 | -84 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1570 | -118 | 92 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1570 | -118 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1355 |  | 1570 | -215 | 86 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1353 |  | 1570 | -217 | 86 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1333 |  | 1570 | -237 | 85 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1316 |  | 1570 | -254 | 84 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1315 |  | 1570 | -255 | 84 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1314 |  | 1570 | -256 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1310 |  | 1570 | -260 | 83 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1306 |  | 1570 | -264 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1265 |  | 1570 | -305 | 81 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1223 |  | 1570 | -347 | 78 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1221 |  | 1570 | -349 | 78 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1210 |  | 1570 | -360 | 77 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1480 |  | 2000 | -520 | 74 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1472 |  | -2000 | -528 | 74 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1461 |  | 2000 | -539 | 73 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1453 |  | -2000 | -547 | 73 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1324 |  | 1890 | -566 | 70 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1324 |  | 1890 | -566 | 70 | []

## 0630Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 06:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3472
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1875 | 1920 | 1920 | -45 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1875 | 1920 | 1920 | -45 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1493 | 2000 | 2000 | -507 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1485 | -2000 | -2000 | -515 | 74 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1474 | 2000 | 2000 | -526 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1465 | -2000 | -2000 | -535 | 73 | []

## 0630Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 06:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3472
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1875 |  | 1920 | -45 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1875 |  | 1920 | -45 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1493 |  | 2000 | -507 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1485 |  | -2000 | -515 | 74 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1474 |  | 2000 | -526 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1465 |  | -2000 | -535 | 73 | []

## 0730Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 07:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3649
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1878 | 1920 | 1920 | -42 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1878 | 1920 | 1920 | -42 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1696 | 2000 | 2000 | -304 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1691 | -2000 | -2000 | -309 | 85 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1677 | 2000 | 2000 | -323 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1672 | -2000 | -2000 | -328 | 84 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1138 | 1570 | 1570 | -432 | 73 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1138 | 1570 | 1570 | -432 | 73 | []

## 0730Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 07:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3649
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1878 |  | 1920 | -42 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1878 |  | 1920 | -42 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1696 |  | 2000 | -304 | 85 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1691 |  | -2000 | -309 | 85 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1677 |  | 2000 | -323 | 84 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1672 |  | -2000 | -328 | 84 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1138 |  | 1570 | -432 | 73 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1138 |  | 1570 | -432 | 73 | []

## 0830Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 08:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3306
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 | 1890 | 1890 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1876 | 1920 | 1920 | -44 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1876 | 1920 | 1920 | -44 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1667 | 2000 | 2000 | -333 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1661 | -2000 | -2000 | -339 | 83 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1649 | 2000 | 2000 | -351 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1643 | -2000 | -2000 | -357 | 82 | []

## 0830Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 08:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3306
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1887 |  | 1890 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1876 |  | 1920 | -44 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1876 |  | 1920 | -44 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1667 |  | 2000 | -333 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1661 |  | -2000 | -339 | 83 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1649 |  | 2000 | -351 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1643 |  | -2000 | -357 | 82 | []

## 0930Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 09:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3344
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1888 | 1890 | 1890 | -2 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1888 | 1890 | 1890 | -2 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1878 | 1920 | 1920 | -42 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1878 | 1920 | 1920 | -42 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1652 | 2000 | 2000 | -348 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1646 | -2000 | -2000 | -354 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1634 | 2000 | 2000 | -366 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1628 | -2000 | -2000 | -372 | 81 | []

## 0930Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 09:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3344
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1888 |  | 1890 | -2 | 100 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1888 |  | 1890 | -2 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1878 |  | 1920 | -42 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1878 |  | 1920 | -42 | 98 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1652 |  | 2000 | -348 | 83 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1646 |  | -2000 | -354 | 82 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1634 |  | 2000 | -366 | 82 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1628 |  | -2000 | -372 | 81 | []

## 1030Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 10:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3687
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1413 | -1570 | -1570 | -157 | 90 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1413 | -1570 | -1570 | -157 | 90 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1669 | 1890 | 1890 | -221 | 88 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1669 | 1890 | 1890 | -221 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1658 | 1920 | 1920 | -262 | 86 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1658 | 1920 | 1920 | -262 | 86 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 | -1570 | -1570 | -242 | 85 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1327 | -1570 | -1570 | -243 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1324 | -1570 | -1570 | -246 | 84 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1321 | -1570 | -1570 | -249 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1320 | -1570 | -1570 | -250 | 84 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1319 | -1570 | -1570 | -251 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1314 | -1570 | -1570 | -256 | 84 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1303 | -1570 | -1570 | -267 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1272 | -1570 | -1570 | -298 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1222 | -1570 | -1570 | -348 | 78 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1531 | 2000 | 2000 | -469 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1525 | -2000 | -2000 | -475 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1514 | 2000 | 2000 | -486 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1508 | -2000 | -2000 | -492 | 75 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1182 | -1570 | -1570 | -388 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1137 | -1570 | -1570 | -433 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [DIR] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -893 | -1248 | -1248 | -355 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [DIR] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -885 | -1248 | -1248 | -363 | 71 | []

## 1030Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 10:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3687
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1413 |  | -1570 | -157 | 90 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1413 |  | -1570 | -157 | 90 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1669 |  | 1890 | -221 | 88 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1669 |  | 1890 | -221 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1658 |  | 1920 | -262 | 86 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1658 |  | 1920 | -262 | 86 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 |  | -1570 | -242 | 85 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1327 |  | -1570 | -243 | 85 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1324 |  | -1570 | -246 | 84 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1321 |  | -1570 | -249 | 84 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1320 |  | -1570 | -250 | 84 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1319 |  | -1570 | -251 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1314 |  | -1570 | -256 | 84 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1303 |  | -1570 | -267 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1272 |  | -1570 | -298 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1222 |  | -1570 | -348 | 78 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1531 |  | 2000 | -469 | 77 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1525 |  | -2000 | -475 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1514 |  | 2000 | -486 | 76 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1508 |  | -2000 | -492 | 75 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1182 |  | -1570 | -388 | 75 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1137 |  | -1570 | -433 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [DIR] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -893 |  | -1248 | -355 | 72 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [DIR] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -885 |  | -1248 | -363 | 71 | []

## 1130Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 11:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3611
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1545 | 1570 | 1570 | -25 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1545 | 1570 | 1570 | -25 | 98 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1498 | 1570 | 1570 | -72 | 95 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1497 | 1570 | 1570 | -73 | 95 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1494 | 1570 | 1570 | -76 | 95 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 | 1570 | 1570 | -83 | 95 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 | 1570 | 1570 | -83 | 95 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1481 | 1570 | 1570 | -89 | 94 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 | 1570 | 1570 | -91 | 94 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 | 1570 | 1570 | -119 | 92 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 | 1570 | 1570 | -135 | 91 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1401 | 1570 | 1570 | -169 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1388 | 1570 | 1570 | -182 | 88 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -858 | -999 | -999 | -141 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1321 | 1570 | 1570 | -249 | 84 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1426 | 1890 | 1890 | -464 | 75 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1426 | 1890 | 1890 | -464 | 75 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1414 | 1920 | 1920 | -506 | 74 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1414 | 1920 | 1920 | -506 | 74 | []
RO_CO_00005 | N-1 OHL 400 kV Tantareni-Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -731 | -999 | -999 | -268 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [DIR] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -882 | -1248 | -1248 | -367 | 71 | []

## 1130Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 11:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3611
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1545 |  | 1570 | -25 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1545 |  | 1570 | -25 | 98 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1498 |  | 1570 | -72 | 95 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1497 |  | 1570 | -73 | 95 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1494 |  | 1570 | -76 | 95 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 |  | 1570 | -83 | 95 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 |  | 1570 | -83 | 95 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1481 |  | 1570 | -89 | 94 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 |  | 1570 | -91 | 94 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 |  | 1570 | -119 | 92 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1435 |  | 1570 | -135 | 91 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1401 |  | 1570 | -169 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1388 |  | 1570 | -182 | 88 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -858 |  | -999 | -141 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1321 |  | 1570 | -249 | 84 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1426 |  | 1890 | -464 | 75 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1426 |  | 1890 | -464 | 75 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1414 |  | 1920 | -506 | 74 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1414 |  | 1920 | -506 | 74 | []
RO_CO_00005 | N-1 OHL 400 kV Tantareni-Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -731 |  | -999 | -268 | 73 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [DIR] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -882 |  | -1248 | -367 | 71 | []

## 1230Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 12:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3520
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1531 | 1570 | 1570 | -39 | 98 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1530 | 1570 | 1570 | -40 | 97 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1526 | 1570 | 1570 | -44 | 97 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1521 | 1570 | 1570 | -49 | 97 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1521 | 1570 | 1570 | -49 | 97 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1513 | 1570 | 1570 | -57 | 96 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1512 | 1570 | 1570 | -58 | 96 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 | 1570 | 1570 | -91 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1460 | 1570 | 1570 | -110 | 93 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1455 | 1570 | 1570 | -115 | 93 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 | 1570 | 1570 | -148 | 91 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1360 | 1570 | 1570 | -210 | 87 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -851 | -999 | -999 | -149 | 85 | []
RO_CO_00005 | N-1 OHL 400 kV Tantareni-Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -739 | -999 | -999 | -260 | 74 | []

## 1230Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 12:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3520
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1531 |  | 1570 | -39 | 98 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1530 |  | 1570 | -40 | 97 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1526 |  | 1570 | -44 | 97 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1521 |  | 1570 | -49 | 97 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1521 |  | 1570 | -49 | 97 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1513 |  | 1570 | -57 | 96 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1512 |  | 1570 | -58 | 96 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 |  | 1570 | -91 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1460 |  | 1570 | -110 | 93 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1455 |  | 1570 | -115 | 93 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1422 |  | 1570 | -148 | 91 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1360 |  | 1570 | -210 | 87 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -851 |  | -999 | -149 | 85 | []
RO_CO_00005 | N-1 OHL 400 kV Tantareni-Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -739 |  | -999 | -260 | 74 | []

## 1330Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 13:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3465
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 | 1570 | 1570 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 | 1570 | 1570 | -3 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1538 | 1570 | 1570 | -32 | 98 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1536 | 1570 | 1570 | -34 | 98 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1531 | 1570 | 1570 | -39 | 98 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1528 | 1570 | 1570 | -42 | 97 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1528 | 1570 | 1570 | -42 | 97 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1519 | 1570 | 1570 | -51 | 97 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1519 | 1570 | 1570 | -51 | 97 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1484 | 1570 | 1570 | -86 | 95 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 | 1570 | 1570 | -103 | 93 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1459 | 1570 | 1570 | -111 | 93 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 | 1570 | 1570 | -143 | 91 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 | 1570 | 1570 | -202 | 87 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -814 | -999 | -999 | -185 | 82 | []
RO_CO_00005 | N-1 OHL 400 kV Tantareni-Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -711 | -999 | -999 | -288 | 71 | []

## 1330Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 13:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3465
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1570 | -3 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1570 | -3 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1538 |  | 1570 | -32 | 98 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1536 |  | 1570 | -34 | 98 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1531 |  | 1570 | -39 | 98 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1528 |  | 1570 | -42 | 97 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1528 |  | 1570 | -42 | 97 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1519 |  | 1570 | -51 | 97 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1519 |  | 1570 | -51 | 97 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1484 |  | 1570 | -86 | 95 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 |  | 1570 | -103 | 93 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1459 |  | 1570 | -111 | 93 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1427 |  | 1570 | -143 | 91 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 |  | 1570 | -202 | 87 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -814 |  | -999 | -185 | 82 | []
RO_CO_00005 | N-1 OHL 400 kV Tantareni-Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -711 |  | -999 | -288 | 71 | []

## 1430Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 14:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3639
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1532 | 1570 | 1570 | -38 | 98 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1531 | 1570 | 1570 | -39 | 97 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1526 | 1570 | 1570 | -44 | 97 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1523 | 1570 | 1570 | -47 | 97 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1522 | 1570 | 1570 | -48 | 97 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1514 | 1570 | 1570 | -56 | 96 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1512 | 1570 | 1570 | -58 | 96 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1477 | 1570 | 1570 | -93 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 | 1570 | 1570 | -119 | 92 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 | 1570 | 1570 | -128 | 92 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 | 1570 | 1570 | -152 | 90 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1361 | 1570 | 1570 | -209 | 87 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -808 | -999 | -999 | -191 | 81 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1387 | 1890 | 1890 | -503 | 73 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1387 | 1890 | 1890 | -503 | 73 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1374 | 1920 | 1920 | -546 | 72 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1374 | 1920 | 1920 | -546 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [DIR] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -877 | -1248 | -1248 | -372 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 14:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3639
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1532 |  | 1570 | -38 | 98 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1531 |  | 1570 | -39 | 97 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1526 |  | 1570 | -44 | 97 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1523 |  | 1570 | -47 | 97 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1522 |  | 1570 | -48 | 97 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1514 |  | 1570 | -56 | 96 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1512 |  | 1570 | -58 | 96 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1477 |  | 1570 | -93 | 94 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 |  | 1570 | -119 | 92 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1442 |  | 1570 | -128 | 92 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 |  | 1570 | -152 | 90 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1361 |  | 1570 | -209 | 87 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -808 |  | -999 | -191 | 81 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1387 |  | 1890 | -503 | 73 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1387 |  | 1890 | -503 | 73 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1374 |  | 1920 | -546 | 72 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1374 |  | 1920 | -546 | 72 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [DIR] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -877 |  | -1248 | -372 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 15:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3726
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 | 1570 | 1570 | -95 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 | 1570 | 1570 | -95 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 | 1570 | 1570 | -152 | 90 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 | 1570 | 1570 | -153 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 | 1570 | 1570 | -155 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1412 | 1570 | 1570 | -158 | 90 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 | 1570 | 1570 | -161 | 90 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1406 | 1570 | 1570 | -164 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1403 | 1570 | 1570 | -167 | 89 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1376 | 1570 | 1570 | -194 | 88 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1325 | 1570 | 1570 | -245 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1302 | 1570 | 1570 | -268 | 83 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1291 | 1570 | 1570 | -279 | 82 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1496 | 1890 | 1890 | -394 | 79 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1496 | 1890 | 1890 | -394 | 79 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1237 | 1570 | 1570 | -333 | 79 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1484 | 1920 | 1920 | -436 | 77 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1484 | 1920 | 1920 | -436 | 77 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1525 | 2000 | 2000 | -475 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1513 | -2000 | -2000 | -487 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1507 | 2000 | 2000 | -493 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1494 | -2000 | -2000 | -506 | 75 | []

## 1530Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 15:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3726
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 |  | 1570 | -95 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 |  | 1570 | -95 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1418 |  | 1570 | -152 | 90 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1417 |  | 1570 | -153 | 90 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1415 |  | 1570 | -155 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1412 |  | 1570 | -158 | 90 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1409 |  | 1570 | -161 | 90 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1406 |  | 1570 | -164 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1403 |  | 1570 | -167 | 89 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1376 |  | 1570 | -194 | 88 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1325 |  | 1570 | -245 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1302 |  | 1570 | -268 | 83 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1291 |  | 1570 | -279 | 82 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1496 |  | 1890 | -394 | 79 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1496 |  | 1890 | -394 | 79 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1237 |  | 1570 | -333 | 79 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1484 |  | 1920 | -436 | 77 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1484 |  | 1920 | -436 | 77 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1525 |  | 2000 | -475 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1513 |  | -2000 | -487 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1507 |  | 2000 | -493 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1494 |  | -2000 | -506 | 75 | []

## 1630Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 16:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3543
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1482 | 1570 | 1570 | -88 | 94 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1481 | 1570 | 1570 | -89 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 | 1570 | 1570 | -95 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1474 | 1570 | 1570 | -96 | 94 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 | 1570 | 1570 | -102 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 | 1570 | 1570 | -103 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1465 | 1570 | 1570 | -105 | 93 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1445 | 1570 | 1570 | -125 | 92 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1396 | 1570 | 1570 | -174 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1375 | 1570 | 1570 | -195 | 88 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1348 | 1570 | 1570 | -222 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1290 | 1570 | 1570 | -280 | 82 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1524 | 2000 | 2000 | -476 | 76 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1431 | 1890 | 1890 | -459 | 76 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1431 | 1890 | 1890 | -459 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1511 | -2000 | -2000 | -489 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1506 | 2000 | 2000 | -494 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1493 | -2000 | -2000 | -507 | 75 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1418 | 1920 | 1920 | -502 | 74 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1418 | 1920 | 1920 | -502 | 74 | []

## 1630Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 16:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3543
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1482 |  | 1570 | -88 | 94 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1481 |  | 1570 | -89 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1475 |  | 1570 | -95 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1474 |  | 1570 | -96 | 94 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 |  | 1570 | -102 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 |  | 1570 | -103 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1465 |  | 1570 | -105 | 93 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1445 |  | 1570 | -125 | 92 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1396 |  | 1570 | -174 | 89 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1375 |  | 1570 | -195 | 88 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1348 |  | 1570 | -222 | 86 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1290 |  | 1570 | -280 | 82 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1524 |  | 2000 | -476 | 76 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1431 |  | 1890 | -459 | 76 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1431 |  | 1890 | -459 | 76 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1511 |  | -2000 | -489 | 76 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1506 |  | 2000 | -494 | 75 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1493 |  | -2000 | -507 | 75 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1418 |  | 1920 | -502 | 74 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1418 |  | 1920 | -502 | 74 | []

## 1730Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 17:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3315
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1562 | -1570 | -1570 | -8 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1562 | -1570 | -1570 | -8 | 99 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1508 | -1570 | -1570 | -62 | 96 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1501 | -1570 | -1570 | -69 | 96 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1497 | -1570 | -1570 | -73 | 95 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1495 | 1570 | 1570 | -75 | 95 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1494 | 1570 | 1570 | -76 | 95 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1493 | -1570 | -1570 | -77 | 95 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1485 | -1570 | -1570 | -85 | 95 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1461 | -1570 | -1570 | -109 | 93 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1412 | -1570 | -1570 | -158 | 90 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1387 | 1570 | 1570 | -183 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1380 | -1570 | -1570 | -190 | 88 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1369 | 1570 | 1570 | -201 | 87 | []

## 1730Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 17:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3315
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1562 |  | -1570 | -8 | 99 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1562 |  | -1570 | -8 | 99 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1508 |  | -1570 | -62 | 96 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1501 |  | -1570 | -69 | 96 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1497 |  | -1570 | -73 | 95 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1495 |  | 1570 | -75 | 95 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1494 |  | 1570 | -76 | 95 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1493 |  | -1570 | -77 | 95 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1485 |  | -1570 | -85 | 95 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1461 |  | -1570 | -109 | 93 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1412 |  | -1570 | -158 | 90 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1387 |  | 1570 | -183 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1380 |  | -1570 | -190 | 88 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1369 |  | 1570 | -201 | 87 | []

## 1830Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 18:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3517
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1564 | -1570 | -1570 | -6 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1564 | -1570 | -1570 | -6 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1496 | -1570 | -1570 | -74 | 95 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 | 1570 | 1570 | -85 | 95 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1484 | 1570 | 1570 | -86 | 95 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1476 | -1570 | -1570 | -94 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1473 | -1570 | -1570 | -97 | 94 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1463 | -1570 | -1570 | -107 | 93 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1462 | -1570 | -1570 | -108 | 93 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1453 | -1570 | -1570 | -117 | 93 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1379 | 1570 | 1570 | -191 | 88 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1370 | 1570 | 1570 | -200 | 87 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1368 | -1570 | -1570 | -202 | 87 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1358 | -1570 | -1570 | -212 | 87 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1509 | 2000 | 2000 | -491 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1495 | -2000 | -2000 | -505 | 75 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1489 | 2000 | 2000 | -511 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1475 | -2000 | -2000 | -525 | 74 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1357 | 1890 | 1890 | -533 | 72 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1357 | 1890 | 1890 | -533 | 72 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1349 | 1920 | 1920 | -571 | 70 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1349 | 1920 | 1920 | -571 | 70 | []

## 1830Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 18:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3517
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1564 |  | -1570 | -6 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1564 |  | -1570 | -6 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1496 |  | -1570 | -74 | 95 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1485 |  | 1570 | -85 | 95 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1484 |  | 1570 | -86 | 95 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1476 |  | -1570 | -94 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1473 |  | -1570 | -97 | 94 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1463 |  | -1570 | -107 | 93 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1462 |  | -1570 | -108 | 93 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1453 |  | -1570 | -117 | 93 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1379 |  | 1570 | -191 | 88 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1370 |  | 1570 | -200 | 87 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1368 |  | -1570 | -202 | 87 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1358 |  | -1570 | -212 | 87 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1509 |  | 2000 | -491 | 75 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1495 |  | -2000 | -505 | 75 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1489 |  | 2000 | -511 | 74 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1475 |  | -2000 | -525 | 74 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1357 |  | 1890 | -533 | 72 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1357 |  | 1890 | -533 | 72 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1349 |  | 1920 | -571 | 70 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1349 |  | 1920 | -571 | 70 | []

## 1930Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 19:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3845
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1504 | -1570 | -1570 | -66 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1504 | -1570 | -1570 | -66 | 96 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1761 | 1890 | 1890 | -129 | 93 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1761 | 1890 | 1890 | -129 | 93 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1748 | 1920 | 1920 | -172 | 91 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1748 | 1920 | 1920 | -172 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1395 | -1570 | -1570 | -175 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1380 | -1570 | -1570 | -190 | 88 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1379 | -1570 | -1570 | -191 | 88 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1371 | -1570 | -1570 | -199 | 87 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1366 | -1570 | -1570 | -204 | 87 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1365 | -1570 | -1570 | -205 | 87 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1361 | -1570 | -1570 | -209 | 87 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1353 | -1570 | -1570 | -217 | 86 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1683 | 2000 | 2000 | -317 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1675 | -2000 | -2000 | -325 | 84 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1661 | 2000 | 2000 | -339 | 83 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1653 | -2000 | -2000 | -347 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1271 | -1570 | -1570 | -299 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1258 | -1570 | -1570 | -312 | 80 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1256 | -1570 | -1570 | -314 | 80 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1241 | -1570 | -1570 | -329 | 79 | []

## 1930Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 19:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3845
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1504 |  | -1570 | -66 | 96 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1504 |  | -1570 | -66 | 96 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1761 |  | 1890 | -129 | 93 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1761 |  | 1890 | -129 | 93 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1748 |  | 1920 | -172 | 91 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1748 |  | 1920 | -172 | 91 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1395 |  | -1570 | -175 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1380 |  | -1570 | -190 | 88 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1379 |  | -1570 | -191 | 88 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1371 |  | -1570 | -199 | 87 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1366 |  | -1570 | -204 | 87 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1365 |  | -1570 | -205 | 87 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1361 |  | -1570 | -209 | 87 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1353 |  | -1570 | -217 | 86 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1683 |  | 2000 | -317 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1675 |  | -2000 | -325 | 84 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1661 |  | 2000 | -339 | 83 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1653 |  | -2000 | -347 | 83 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1271 |  | -1570 | -299 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1258 |  | -1570 | -312 | 80 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1256 |  | -1570 | -314 | 80 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1241 |  | -1570 | -329 | 79 | []

## 2030Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 20:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3738
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1565 | -1570 | -1570 | -5 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1565 | -1570 | -1570 | -5 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1446 | -1570 | -1570 | -124 | 92 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1729 | 1890 | 1890 | -161 | 91 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1729 | 1890 | 1890 | -161 | 91 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1425 | -1570 | -1570 | -145 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1421 | -1570 | -1570 | -149 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1411 | -1570 | -1570 | -159 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1410 | -1570 | -1570 | -160 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1402 | -1570 | -1570 | -168 | 89 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1715 | 1920 | 1920 | -205 | 89 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1715 | 1920 | 1920 | -205 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1375 | -1570 | -1570 | -195 | 88 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1714 | 2000 | 2000 | -286 | 86 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1707 | -2000 | -2000 | -293 | 85 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1691 | 2000 | 2000 | -309 | 85 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1684 | -2000 | -2000 | -316 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1318 | -1570 | -1570 | -252 | 84 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1302 | -1570 | -1570 | -268 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1275 | -1570 | -1570 | -295 | 81 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1259 | -1570 | -1570 | -311 | 80 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1402 | 2000 | 2000 | -598 | 70 | []

## 2030Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 20:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3738
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1565 |  | -1570 | -5 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1565 |  | -1570 | -5 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1446 |  | -1570 | -124 | 92 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1729 |  | 1890 | -161 | 91 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1729 |  | 1890 | -161 | 91 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1425 |  | -1570 | -145 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1421 |  | -1570 | -149 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1411 |  | -1570 | -159 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1410 |  | -1570 | -160 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1402 |  | -1570 | -168 | 89 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1715 |  | 1920 | -205 | 89 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1715 |  | 1920 | -205 | 89 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1375 |  | -1570 | -195 | 88 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1714 |  | 2000 | -286 | 86 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1707 |  | -2000 | -293 | 85 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1691 |  | 2000 | -309 | 85 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1684 |  | -2000 | -316 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1318 |  | -1570 | -252 | 84 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1302 |  | -1570 | -268 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1275 |  | -1570 | -295 | 81 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1259 |  | -1570 | -311 | 80 | []
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [DIR] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1402 |  | 2000 | -598 | 70 | []

## 2130Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 21:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3711
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1563 | -1570 | -1570 | -7 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1563 | -1570 | -1570 | -7 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1451 | -1570 | -1570 | -119 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1429 | -1570 | -1570 | -141 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1426 | -1570 | -1570 | -144 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1418 | -1570 | -1570 | -152 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1414 | -1570 | -1570 | -156 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1412 | -1570 | -1570 | -158 | 90 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1695 | 1890 | 1890 | -195 | 90 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1695 | 1890 | 1890 | -195 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1393 | 1570 | 1570 | -177 | 89 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1682 | 1920 | 1920 | -238 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1682 | 1920 | 1920 | -238 | 88 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1322 | -1570 | -1570 | -248 | 84 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1684 | 2000 | 2000 | -316 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1677 | -2000 | -2000 | -323 | 84 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1312 | -1570 | -1570 | -258 | 84 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1662 | 2000 | 2000 | -338 | 83 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1655 | -2000 | -2000 | -345 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1275 | -1570 | -1570 | -295 | 81 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1264 | -1570 | -1570 | -306 | 81 | []

## 2130Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 21:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3711
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1563 |  | -1570 | -7 | 100 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1563 |  | -1570 | -7 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1451 |  | -1570 | -119 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1429 |  | -1570 | -141 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1426 |  | -1570 | -144 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1418 |  | -1570 | -152 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1414 |  | -1570 | -156 | 90 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1412 |  | -1570 | -158 | 90 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1695 |  | 1890 | -195 | 90 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1695 |  | 1890 | -195 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1393 |  | 1570 | -177 | 89 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1682 |  | 1920 | -238 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1682 |  | 1920 | -238 | 88 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1322 |  | -1570 | -248 | 84 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1684 |  | 2000 | -316 | 84 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1677 |  | -2000 | -323 | 84 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1312 |  | -1570 | -258 | 84 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1662 |  | 2000 | -338 | 83 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1655 |  | -2000 | -345 | 83 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1275 |  | -1570 | -295 | 81 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1264 |  | -1570 | -306 | 81 | []

## 2230Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 22:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3583
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1559 | -1570 | -1570 | -11 | 99 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1559 | -1570 | -1570 | -11 | 99 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1455 | -1570 | -1570 | -115 | 93 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1431 | -1570 | -1570 | -139 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1430 | -1570 | -1570 | -140 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1424 | -1570 | -1570 | -146 | 91 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1417 | -1570 | -1570 | -153 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1416 | -1570 | -1570 | -154 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1402 | -1570 | -1570 | -168 | 89 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1650 | 1890 | 1890 | -240 | 87 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1650 | 1890 | 1890 | -240 | 87 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1636 | 1920 | 1920 | -284 | 85 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1636 | 1920 | 1920 | -284 | 85 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 | -1570 | -1570 | -242 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1325 | -1570 | -1570 | -245 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1291 | -1570 | -1570 | -279 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1285 | -1570 | -1570 | -285 | 82 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1571 | 2000 | 2000 | -429 | 79 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1556 | -2000 | -2000 | -444 | 78 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1553 | 2000 | 2000 | -447 | 78 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1537 | -2000 | -2000 | -463 | 77 | []

## 2230Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 22:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3583
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1559 |  | -1570 | -11 | 99 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1559 |  | -1570 | -11 | 99 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1455 |  | -1570 | -115 | 93 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1431 |  | -1570 | -139 | 91 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1430 |  | -1570 | -140 | 91 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1424 |  | -1570 | -146 | 91 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1417 |  | -1570 | -153 | 90 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1416 |  | -1570 | -154 | 90 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1402 |  | -1570 | -168 | 89 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1650 |  | 1890 | -240 | 87 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1650 |  | 1890 | -240 | 87 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1636 |  | 1920 | -284 | 85 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1636 |  | 1920 | -284 | 85 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 |  | -1570 | -242 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1325 |  | -1570 | -245 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1291 |  | -1570 | -279 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1285 |  | -1570 | -285 | 82 | []
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11_VVARNA11_1:line | -1571 |  | 2000 | -429 | 79 | []
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 _XVA_MG11_1:line | -1556 |  | -2000 | -444 | 78 | []
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11_VDOBRU11_1:line | -1553 |  | 2000 | -447 | 78 | []
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 _XDO_MG11_1:line | -1537 |  | -2000 | -463 | 77 | []

## 2330Preventive
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 23:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3270
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1564 | -1570 | -1570 | -6 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1564 | -1570 | -1570 | -6 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1471 | -1570 | -1570 | -99 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1456 | -1570 | -1570 | -114 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1455 | -1570 | -1570 | -115 | 93 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1451 | -1570 | -1570 | -119 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1451 | -1570 | -1570 | -119 | 92 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1448 | -1570 | -1570 | -122 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1444 | -1570 | -1570 | -126 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1443 | -1570 | -1570 | -127 | 92 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1399 | -1570 | -1570 | -171 | 89 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1362 | -1570 | -1570 | -208 | 87 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1354 | -1570 | -1570 | -216 | 86 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1352 | -1570 | -1570 | -218 | 86 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1464 | 1890 | 1890 | -426 | 77 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1464 | 1890 | 1890 | -426 | 77 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1450 | 1920 | 1920 | -470 | 76 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1450 | 1920 | 1920 | -470 | 76 | []

## 2330Curative
Detailed results
Generated at: | 2026-05-27 20:00
Business day: | 28.05.2026
Timestamp: | 23:30
Border & direction: | South-Romania Import
Horizon: | DA
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3270
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00016 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1564 |  | -1570 | -6 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1564 |  | -1570 | -6 | 100 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1471 |  | -1570 | -99 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1456 |  | -1570 | -114 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1455 |  | -1570 | -115 | 93 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1451 |  | -1570 | -119 | 92 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1451 |  | -1570 | -119 | 92 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1448 |  | -1570 | -122 | 92 | []
BC | Base Case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1444 |  | -1570 | -126 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1443 |  | -1570 | -127 | 92 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1399 |  | -1570 | -171 | 89 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1362 |  | -1570 | -208 | 87 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1354 |  | -1570 | -216 | 86 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1352 |  | -1570 | -218 | 86 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | -1464 |  | 1890 | -426 | 77 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | -1464 |  | 1890 | -426 | 77 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1450 |  | 1920 | -470 | 76 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1450 |  | 1920 | -470 | 76 | []