## SRO borders-exports
SUBMISSION DATE: | 31.05.2026
BUSINESS DATE: | 02.06.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC RO-BG
00:00 | 01:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 97 | 3701 | 3501 | 2451
01:00 | 02:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 98 | 3672 | 3472 | 2430
02:00 | 03:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 97 | 3689 | 3489 | 2442
03:00 | 04:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 96 | 3666 | 3466 | 2426
04:00 | 05:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 99 | 3675 | 3475 | 2432
05:00 | 06:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3422 | 3222 | 2255
06:00 | 07:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 2264 | 2064 | 1445
07:00 | 08:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 101 | 2006 | 1806 | 1264
08:00 | 09:00 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 1896 | 1696 | 1187
09:00 | 10:00 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 2001 | 1801 | 1261
10:00 | 11:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 1946 | 1746 | 1222
11:00 | 12:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3161 | 2961 | 2073
12:00 | 13:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3450 | 3250 | 2275
13:00 | 14:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3224 | 3024 | 2117
14:00 | 15:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3147 | 2947 | 2063
15:00 | 16:00 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 2726 | 2526 | 1768
16:00 | 17:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3464 | 3264 | 2285
17:00 | 18:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 95 | 3591 | 3391 | 2374
18:00 | 19:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 94 | 3407 | 3207 | 2245
19:00 | 20:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3043 | 2843 | 1990
20:00 | 21:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3024 | 2824 | 1977
21:00 | 22:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3033 | 2833 | 1983
22:00 | 23:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 100 | 3214 | 3014 | 2110
23:00 | 00:00 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | 94 | 3491 | 3291 | 2304

## SRO borders-imports
SUBMISSION DATE: | 31.05.2026
BUSINESS DATE: | 02.06.2026
DA CC Remedial Actions
From Hour (CET) | To Hour (CET) | CO | CNE | Loading (%) | TTC South Romania | NTC South Romania | NTC BG-RO
00:00 | 01:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 2948 | 2748 | 1924
01:00 | 02:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3180 | 2980 | 2086
02:00 | 03:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3027 | 2827 | 1979
03:00 | 04:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3044 | 2844 | 1991
04:00 | 05:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 101 | 3064 | 2864 | 2005
05:00 | 06:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 99 | 3351 | 3151 | 2206
06:00 | 07:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 2792 | 2592 | 1814
07:00 | 08:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 2789 | 2589 | 1812
08:00 | 09:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2851 | 2651 | 1856
09:00 | 10:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 2838 | 2638 | 1847
10:00 | 11:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3018 | 2818 | 1973
11:00 | 12:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3086 | 2886 | 2020
12:00 | 13:00 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | 100 | 3278 | 3078 | 2155
13:00 | 14:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3108 | 2908 | 2036
14:00 | 15:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3300 | 3100 | 2170
15:00 | 16:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3666 | 3466 | 2426
16:00 | 17:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3625 | 3425 | 2398
17:00 | 18:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3423 | 3223 | 2256
18:00 | 19:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3729 | 3529 | 2470
19:00 | 20:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3828 | 3628 | 2540
20:00 | 21:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | 100 | 3971 | 3771 | 2640
21:00 | 22:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3938 | 3738 | 2617
22:00 | 23:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | 100 | 3905 | 3705 | 2594
23:00 | 00:00 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | 100 | 3705 | 3505 | 2454

## SRO borders-exports RAs
SUBMISSION DATE: | 31.05.2026
BUSINESS DATE: | 02.06.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | notApplied | notApplied | helpful | helpful | helpful | helpful | notApplied
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | helpful | helpful | helpful | helpful | helpful | helpful | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30

## SRO borders-imports RAs
SUBMISSION DATE: | 31.05.2026
BUSINESS DATE: | 02.06.2026
DA CC Remedial Actions
Initial CCC
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400 kV TINTARENI-KOZLODUI 1 | BG_RA_00001 | topological | helpful | helpful | helpful | helpful | helpful | helpful | [10 empty] | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst | helpful | helpful | helpful | helpful | helpful | helpful | [7 empty] | helpful | helpful |  | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Tantareni-Kozlodui 1 | RO_RA_00010 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | [7 empty] | notApplied | notApplied |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Tantareni-Kozlodui 2 | RO_RA_00013 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | [7 empty] | notApplied | notApplied |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological | helpful | helpful | helpful | helpful | helpful | notApplied | [7 empty] | helpful | helpful |  | helpful | helpful | helpful | helpful | helpful | helpful | helpful | helpful
PRA 400 kV Resita-Pancevo c1 | RO_RA_00016 | topological | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | [7 empty] | notApplied | notApplied |  | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied | notApplied
NonCostly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst_ra | [13 empty] | applied | applied | applied | applied
PST_ARAD 400/220_3 | RO_RA_00101 | pst_ra | [13 empty] | applied | applied | applied | applied
PST_URECHESTI 400/220_1 | RO_RA_00102 | pst_ra | [13 empty] | applied | applied | applied | applied
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological_ra | [15 empty] | applied
NonCostly Step 5
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
PRA 400 kV Resita-Pancevo c2 | RO_RA_00014 | topological_ra | [11 empty] | applied
PRA 400/220kV AT Urechesti | RO_RA_00002 | pst_ra | [11 empty] | applied
Costly Step 4
Name of the RA | RA_ID | Type | 00:30 | 01:30 | 02:30 | 03:30 | 04:30 | 05:30 | 06:30 | 07:30 | 08:30 | 09:30 | 10:30 | 11:30 | 12:30 | 13:30 | 14:30 | 15:30 | 16:30 | 17:30 | 18:30 | 19:30 | 20:30 | 21:30 | 22:30 | 23:30
RPDF222 _generator | RO_RA_00114 | costly_ra | [13 empty] | 408 | 426
RTOPV_5 _generator | RO_RA_00120 | costly_ra | [13 empty] | 0 | 0 | 10 | 0
RFMEP_5 _generator | RO_RA_00121 | costly_ra | [13 empty] | 0 | 0 | 14 | 0
RVLCE15 _generator | RO_RA_00122 | costly_ra | [13 empty] | 0 | 0 | 55 | 0
RVALD_5 _generator | RO_RA_00123 | costly_ra | [13 empty] | 0 | 0 | 15 | 0
RAREF_5 _generator | RO_RA_00125 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RARGS_5 _generator | RO_RA_00126 | costly_ra | [13 empty] | 0 | 0 | 31 | 0
RALBE_5 _generator | RO_RA_00127 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RCERB_5 _generator | RO_RA_00128 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RVLCE25 _generator | RO_RA_00129 | costly_ra | [13 empty] | 0 | 0 | 12 | 0
RCLNG_5 _generator | RO_RA_00130 | costly_ra | [13 empty] | 0 | 0 | 90 | 0
RSTUP_5 _generator | RO_RA_00134 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RDAIES5 _generator | RO_RA_00135 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RVILN_5 _generator | RO_RA_00136 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RRIUR15 _generator | RO_RA_00137 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RMARC_5 _generator | RO_RA_00138 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RIONE_5 _generator | RO_RA_00139 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RJIBL_5 _generator | RO_RA_00140 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RZAVI_5 _generator | RO_RA_00141 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RCHTU_5 _generator | RO_RA_00142 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RTRAI_5 _generator | RO_RA_00143 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RHGLOT5 _generator | RO_RA_00144 | costly_ra | [13 empty] | 0 | 0 | 25 | 0
RCHESJ5 _generator | RO_RA_00145 | costly_ra | [13 empty] | 0 | 0 | 0 | 50
RCHEAC5 _generator | RO_RA_00146 | costly_ra | [13 empty] | 0 | 0 | 0 | 38
RCHEST5 _generator | RO_RA_00147 | costly_ra | [13 empty] | 0 | 0 | 2 | 0
RCHEIO5 _generator | RO_RA_00148 | costly_ra | [13 empty] | 0 | 0 | 0 | 53
RCHDO_5 _generator | RO_RA_00149 | costly_ra | [13 empty] | 0 | 0 | 0 | 53
RFRUN_5 _generator | RO_RA_00150 | costly_ra | [13 empty] | 0 | 0 | 0 | 53
RCIZBI5 _generator | RO_RA_00151 | costly_ra | [13 empty] | 0 | 0 | 0 | 53
RRUSA_5 _generator | RO_RA_00152 | costly_ra | [13 empty] | 0 | 0 | 0 | 53
RHCORN5 _generator | RO_RA_00153 | costly_ra | [13 empty] | 0 | 0 | 9 | 0
RFAGA_5 _generator | RO_RA_00154 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RUCEA25 _generator | RO_RA_00155 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RUCEA15 _generator | RO_RA_00156 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RCIRT_5 _generator | RO_RA_00157 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RRACO_5 _generator | RO_RA_00165 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RGARL_5 _generator | RO_RA_00166 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RLILI_5 _generator | RO_RA_00167 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RBACS_5 _generator | RO_RA_00168 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RFARA_5 _generator | RO_RA_00169 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RSISC_5 _generator | RO_RA_00170 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RMARA_5 _generator | RO_RA_00171 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RTECU_5 _generator | RO_RA_00172 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RMARI22 _generator | RO_RA_00173 | costly_ra | [13 empty] | 4 |  |  | 146
RSEBE_5 _generator | RO_RA_00176 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RRETE_5 _generator | RO_RA_00181 | costly_ra | [13 empty] | 0 | 0 | 20 | 0
RCIRNA5 _generator | RO_RA_00182 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RCIRNB5 _generator | RO_RA_00183 | costly_ra | [13 empty] | 0 | 0 | 0 | 0
RHATE_5 _generator | RO_RA_00184 | costly_ra | [13 empty] | 14 | 0 | 0 | 0
RVMAR_5 _generator | RO_RA_00116 | costly_ra | [15 empty] | 50 | 0
RGODI_5 _generator | RO_RA_00117 | costly_ra | [15 empty] | 114 | 57