## 1230Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3498
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1584 | 1587 | 1587 | -3 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1493 | 1587 | 1587 | -94 | 94 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1493 | 1587 | 1587 | -94 | 94 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1492 | 1587 | 1587 | -95 | 94 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1482 | 1587 | 1587 | -105 | 93 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1481 | 1587 | 1587 | -106 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1469 | 1587 | 1587 | -118 | 93 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1468 | 1587 | 1587 | -119 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1464 | 1587 | 1587 | -123 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1461 | 1587 | 1587 | -126 | 92 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1460 | 1587 | 1587 | -127 | 92 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1459 | 1587 | 1587 | -128 | 92 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1441 | 1587 | 1587 | -146 | 91 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1433 | 1587 | 1587 | -154 | 90 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1425 | 1587 | 1587 | -162 | 90 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1420 | 1587 | 1587 | -167 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1416 | 1587 | 1587 | -171 | 89 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1416 | 1587 | 1587 | -171 | 89 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1408 | 1587 | 1587 | -179 | 89 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1402 | 1587 | 1587 | -185 | 88 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1398 | 1587 | 1587 | -189 | 88 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1395 | 1587 | 1587 | -192 | 88 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1401 | 1600 | 1600 | -199 | 88 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1388 | 1587 | 1587 | -199 | 87 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1379 | 1587 | 1587 | -208 | 87 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1378 | 1587 | 1587 | -209 | 87 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1377 | 1587 | 1587 | -210 | 87 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1377 | 1587 | 1587 | -210 | 87 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1376 | 1587 | 1587 | -211 | 87 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1373 | 1587 | 1587 | -214 | 86 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1368 | 1587 | 1587 | -219 | 86 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1365 | 1587 | 1587 | -222 | 86 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1365 | 1587 | 1587 | -222 | 86 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1363 | 1587 | 1587 | -224 | 86 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1363 | 1587 | 1587 | -224 | 86 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1360 | 1587 | 1587 | -227 | 86 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1360 | 1587 | 1587 | -227 | 86 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1359 | 1587 | 1587 | -228 | 86 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1359 | 1587 | 1587 | -228 | 86 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1359 | 1587 | 1587 | -228 | 86 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1357 | 1587 | 1587 | -230 | 85 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1349 | 1587 | 1587 | -238 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1336 | 1587 | 1587 | -251 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1335 | 1587 | 1587 | -252 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1313 | 1587 | 1587 | -274 | 83 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1198 | 1587 | 1587 | -389 | 75 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1201 | 1600 | 1600 | -399 | 75 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 | 1587 | 1587 | -408 | 74 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1165 | 1587 | 1587 | -422 | 73 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1147 | 1600 | 1600 | -453 | 72 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1131 | 1587 | 1587 | -456 | 71 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 | 1587 | 1587 | -461 | 71 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1117 | 1587 | 1587 | -470 | 70 | []

## 1230Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 12:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3498
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1584 |  | 1587 | -3 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1493 |  | 1587 | -94 | 94 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1493 |  | 1587 | -94 | 94 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1492 |  | 1587 | -95 | 94 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1482 |  | 1587 | -105 | 93 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1481 |  | 1587 | -106 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1469 |  | 1587 | -118 | 93 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1468 |  | 1587 | -119 | 93 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1464 |  | 1587 | -123 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1461 |  | 1587 | -126 | 92 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1460 |  | 1587 | -127 | 92 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1459 |  | 1587 | -128 | 92 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1441 |  | 1587 | -146 | 91 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1433 |  | 1587 | -154 | 90 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1425 |  | 1587 | -162 | 90 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1420 |  | 1587 | -167 | 89 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1416 |  | 1587 | -171 | 89 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1416 |  | 1587 | -171 | 89 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1408 |  | 1587 | -179 | 89 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1402 |  | 1587 | -185 | 88 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1398 |  | 1587 | -189 | 88 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1395 |  | 1587 | -192 | 88 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1401 |  | 1600 | -199 | 88 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1388 |  | 1587 | -199 | 87 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1379 |  | 1587 | -208 | 87 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1378 |  | 1587 | -209 | 87 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1377 |  | 1587 | -210 | 87 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1377 |  | 1587 | -210 | 87 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1376 |  | 1587 | -211 | 87 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1373 |  | 1587 | -214 | 86 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1368 |  | 1587 | -219 | 86 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1365 |  | 1587 | -222 | 86 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1365 |  | 1587 | -222 | 86 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1363 |  | 1587 | -224 | 86 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1363 |  | 1587 | -224 | 86 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1360 |  | 1587 | -227 | 86 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1360 |  | 1587 | -227 | 86 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1359 |  | 1587 | -228 | 86 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1359 |  | 1587 | -228 | 86 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1359 |  | 1587 | -228 | 86 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1357 |  | 1587 | -230 | 85 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1349 |  | 1587 | -238 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1336 |  | 1587 | -251 | 84 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1335 |  | 1587 | -252 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1313 |  | 1587 | -274 | 83 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1198 |  | 1587 | -389 | 75 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1201 |  | 1600 | -399 | 75 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 |  | 1587 | -408 | 74 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1165 |  | 1587 | -422 | 73 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1147 |  | 1600 | -453 | 72 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1131 |  | 1587 | -456 | 71 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 |  | 1587 | -461 | 71 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1117 |  | 1587 | -470 | 70 | []

## 1330Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3745
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1583 | 1587 | 1587 | -4 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1506 | 1587 | 1587 | -81 | 95 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1505 | 1587 | 1587 | -82 | 95 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1495 | 1587 | 1587 | -92 | 94 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1491 | 1587 | 1587 | -96 | 94 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1487 | 1587 | 1587 | -100 | 94 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1485 | 1587 | 1587 | -102 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1481 | 1587 | 1587 | -106 | 93 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1478 | 1587 | 1587 | -109 | 93 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1476 | 1587 | 1587 | -111 | 93 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1472 | 1587 | 1587 | -115 | 93 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1454 | 1587 | 1587 | -133 | 92 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1453 | 1587 | 1587 | -134 | 92 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1453 | 1587 | 1587 | -134 | 92 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1449 | 1587 | 1587 | -138 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1447 | 1587 | 1587 | -140 | 91 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1446 | 1587 | 1587 | -141 | 91 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1436 | 1587 | 1587 | -151 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1424 | 1587 | 1587 | -163 | 90 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1420 | 1587 | 1587 | -167 | 89 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1420 | 1587 | 1587 | -167 | 89 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1415 | 1587 | 1587 | -172 | 89 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1397 | 1587 | 1587 | -190 | 88 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1407 | 1600 | 1600 | -193 | 88 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1396 | 1587 | 1587 | -191 | 88 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1395 | 1587 | 1587 | -192 | 88 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1391 | 1587 | 1587 | -196 | 88 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1385 | 1587 | 1587 | -202 | 87 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1385 | 1587 | 1587 | -202 | 87 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1384 | 1587 | 1587 | -203 | 87 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1383 | 1587 | 1587 | -204 | 87 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1381 | 1587 | 1587 | -206 | 87 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1378 | 1587 | 1587 | -209 | 87 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1375 | 1587 | 1587 | -212 | 87 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1369 | 1587 | 1587 | -218 | 86 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1367 | 1587 | 1587 | -220 | 86 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1366 | 1587 | 1587 | -221 | 86 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1365 | 1587 | 1587 | -222 | 86 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1364 | 1587 | 1587 | -223 | 86 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1361 | 1587 | 1587 | -226 | 86 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1361 | 1587 | 1587 | -226 | 86 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1360 | 1587 | 1587 | -227 | 86 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1360 | 1587 | 1587 | -227 | 86 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1360 | 1587 | 1587 | -227 | 86 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1358 | 1587 | 1587 | -229 | 86 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1314 | 1587 | 1587 | -273 | 83 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1286 | 1600 | 1600 | -314 | 80 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1274 | 1587 | 1587 | -313 | 80 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1225 | 1587 | 1587 | -362 | 77 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1228 | 1600 | 1600 | -372 | 77 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1216 | 1600 | 1600 | -384 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1214 | 1600 | 1600 | -386 | 76 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1587 | 1587 | -384 | 76 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1212 | 1600 | 1600 | -388 | 76 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1202 | 1587 | 1587 | -385 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1178 | 1587 | 1587 | -409 | 74 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1161 | 1587 | 1587 | -426 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1146 | 1587 | 1587 | -441 | 72 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1143 | 1587 | 1587 | -444 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 | 1587 | 1587 | -445 | 72 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1115 | 1587 | 1587 | -472 | 70 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1114 | 1587 | 1587 | -473 | 70 | []

## 1330Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 13:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3745
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1583 |  | 1587 | -4 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1506 |  | 1587 | -81 | 95 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1505 |  | 1587 | -82 | 95 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1495 |  | 1587 | -92 | 94 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1491 |  | 1587 | -96 | 94 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1487 |  | 1587 | -100 | 94 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1485 |  | 1587 | -102 | 94 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1481 |  | 1587 | -106 | 93 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1478 |  | 1587 | -109 | 93 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1476 |  | 1587 | -111 | 93 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1472 |  | 1587 | -115 | 93 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1454 |  | 1587 | -133 | 92 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1453 |  | 1587 | -134 | 92 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1453 |  | 1587 | -134 | 92 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1449 |  | 1587 | -138 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1447 |  | 1587 | -140 | 91 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1446 |  | 1587 | -141 | 91 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1436 |  | 1587 | -151 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1424 |  | 1587 | -163 | 90 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1420 |  | 1587 | -167 | 89 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1420 |  | 1587 | -167 | 89 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1415 |  | 1587 | -172 | 89 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1397 |  | 1587 | -190 | 88 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1407 |  | 1600 | -193 | 88 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1396 |  | 1587 | -191 | 88 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1395 |  | 1587 | -192 | 88 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1391 |  | 1587 | -196 | 88 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1385 |  | 1587 | -202 | 87 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1385 |  | 1587 | -202 | 87 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1384 |  | 1587 | -203 | 87 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1383 |  | 1587 | -204 | 87 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1381 |  | 1587 | -206 | 87 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1378 |  | 1587 | -209 | 87 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1375 |  | 1587 | -212 | 87 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1369 |  | 1587 | -218 | 86 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1367 |  | 1587 | -220 | 86 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1366 |  | 1587 | -221 | 86 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1365 |  | 1587 | -222 | 86 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1364 |  | 1587 | -223 | 86 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1361 |  | 1587 | -226 | 86 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1361 |  | 1587 | -226 | 86 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1360 |  | 1587 | -227 | 86 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1360 |  | 1587 | -227 | 86 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1360 |  | 1587 | -227 | 86 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1358 |  | 1587 | -229 | 86 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1314 |  | 1587 | -273 | 83 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1286 |  | 1600 | -314 | 80 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1274 |  | 1587 | -313 | 80 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1225 |  | 1587 | -362 | 77 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1228 |  | 1600 | -372 | 77 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1216 |  | 1600 | -384 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1214 |  | 1600 | -386 | 76 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1587 | -384 | 76 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1212 |  | 1600 | -388 | 76 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1202 |  | 1587 | -385 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1178 |  | 1587 | -409 | 74 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1161 |  | 1587 | -426 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1146 |  | 1587 | -441 | 72 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1143 |  | 1587 | -444 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 |  | 1587 | -445 | 72 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1115 |  | 1587 | -472 | 70 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1114 |  | 1587 | -473 | 70 | []

## 1430Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3515
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1582 | 1587 | 1587 | -5 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1498 | 1587 | 1587 | -89 | 94 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1498 | 1587 | 1587 | -89 | 94 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1489 | 1587 | 1587 | -98 | 94 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1481 | 1587 | 1587 | -106 | 93 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1480 | 1587 | 1587 | -107 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1472 | 1587 | 1587 | -115 | 93 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1468 | 1587 | 1587 | -119 | 93 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1465 | 1587 | 1587 | -122 | 92 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1464 | 1587 | 1587 | -123 | 92 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1463 | 1587 | 1587 | -124 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1461 | 1587 | 1587 | -126 | 92 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1446 | 1587 | 1587 | -141 | 91 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1445 | 1587 | 1587 | -142 | 91 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1428 | 1587 | 1587 | -159 | 90 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1425 | 1587 | 1587 | -162 | 90 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1421 | 1587 | 1587 | -166 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1418 | 1587 | 1587 | -169 | 89 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1404 | 1587 | 1587 | -183 | 88 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1404 | 1587 | 1587 | -183 | 88 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1403 | 1587 | 1587 | -184 | 88 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1399 | 1587 | 1587 | -188 | 88 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1399 | 1587 | 1587 | -188 | 88 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1394 | 1587 | 1587 | -193 | 88 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1390 | 1587 | 1587 | -197 | 88 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1402 | 1600 | 1600 | -198 | 88 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1388 | 1587 | 1587 | -199 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1387 | 1587 | 1587 | -200 | 87 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1381 | 1587 | 1587 | -206 | 87 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1378 | 1587 | 1587 | -209 | 87 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1378 | 1587 | 1587 | -209 | 87 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1375 | 1587 | 1587 | -212 | 87 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1373 | 1587 | 1587 | -214 | 87 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1370 | 1587 | 1587 | -217 | 86 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1367 | 1587 | 1587 | -220 | 86 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1366 | 1587 | 1587 | -221 | 86 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1365 | 1587 | 1587 | -222 | 86 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1365 | 1587 | 1587 | -222 | 86 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1363 | 1587 | 1587 | -224 | 86 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1362 | 1587 | 1587 | -225 | 86 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1361 | 1587 | 1587 | -226 | 86 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1361 | 1587 | 1587 | -226 | 86 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1361 | 1587 | 1587 | -226 | 86 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1359 | 1587 | 1587 | -228 | 86 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1334 | 1587 | 1587 | -253 | 84 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1256 | 1587 | 1587 | -331 | 79 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1587 | 1587 | -389 | 75 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1182 | 1600 | 1600 | -418 | 74 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1171 | 1587 | 1587 | -416 | 74 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1171 | 1587 | 1587 | -416 | 74 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 | 1587 | 1587 | -438 | 72 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 | 1587 | 1587 | -453 | 71 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1127 | 1600 | 1600 | -473 | 70 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1115 | 1587 | 1587 | -472 | 70 | []

## 1430Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 14:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3515
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1582 |  | 1587 | -5 | 100 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1498 |  | 1587 | -89 | 94 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1498 |  | 1587 | -89 | 94 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1489 |  | 1587 | -98 | 94 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1481 |  | 1587 | -106 | 93 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1480 |  | 1587 | -107 | 93 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1472 |  | 1587 | -115 | 93 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1468 |  | 1587 | -119 | 93 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1465 |  | 1587 | -122 | 92 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1464 |  | 1587 | -123 | 92 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1463 |  | 1587 | -124 | 92 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1461 |  | 1587 | -126 | 92 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1446 |  | 1587 | -141 | 91 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1445 |  | 1587 | -142 | 91 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1428 |  | 1587 | -159 | 90 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1425 |  | 1587 | -162 | 90 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1421 |  | 1587 | -166 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1418 |  | 1587 | -169 | 89 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1404 |  | 1587 | -183 | 88 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1404 |  | 1587 | -183 | 88 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1403 |  | 1587 | -184 | 88 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1399 |  | 1587 | -188 | 88 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1399 |  | 1587 | -188 | 88 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1394 |  | 1587 | -193 | 88 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1390 |  | 1587 | -197 | 88 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1402 |  | 1600 | -198 | 88 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1388 |  | 1587 | -199 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1387 |  | 1587 | -200 | 87 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1381 |  | 1587 | -206 | 87 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1378 |  | 1587 | -209 | 87 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1378 |  | 1587 | -209 | 87 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1375 |  | 1587 | -212 | 87 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1373 |  | 1587 | -214 | 87 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1370 |  | 1587 | -217 | 86 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1367 |  | 1587 | -220 | 86 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1366 |  | 1587 | -221 | 86 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1365 |  | 1587 | -222 | 86 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1365 |  | 1587 | -222 | 86 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1363 |  | 1587 | -224 | 86 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1362 |  | 1587 | -225 | 86 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1361 |  | 1587 | -226 | 86 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1361 |  | 1587 | -226 | 86 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1361 |  | 1587 | -226 | 86 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1359 |  | 1587 | -228 | 86 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1334 |  | 1587 | -253 | 84 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1256 |  | 1587 | -331 | 79 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1587 | -389 | 75 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1182 |  | 1600 | -418 | 74 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1171 |  | 1587 | -416 | 74 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1171 |  | 1587 | -416 | 74 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 |  | 1587 | -438 | 72 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1134 |  | 1587 | -453 | 71 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1127 |  | 1600 | -473 | 70 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1115 |  | 1587 | -472 | 70 | []

## 1530Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3172
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1585 | 1587 | 1587 | -2 | 100 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1504 | 1587 | 1587 | -83 | 95 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1503 | 1587 | 1587 | -84 | 95 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1503 | 1587 | 1587 | -84 | 95 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1478 | 1587 | 1587 | -109 | 93 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1475 | 1587 | 1587 | -112 | 93 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1472 | 1587 | 1587 | -115 | 93 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1471 | 1587 | 1587 | -116 | 93 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1467 | 1587 | 1587 | -120 | 92 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1465 | 1587 | 1587 | -122 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1461 | 1587 | 1587 | -126 | 92 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1451 | 1587 | 1587 | -136 | 91 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1447 | 1587 | 1587 | -140 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1446 | 1587 | 1587 | -141 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1443 | 1587 | 1587 | -144 | 91 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1442 | 1587 | 1587 | -145 | 91 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1434 | 1587 | 1587 | -153 | 90 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1431 | 1587 | 1587 | -156 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1423 | 1587 | 1587 | -164 | 90 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1417 | 1587 | 1587 | -170 | 89 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1411 | 1587 | 1587 | -176 | 89 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1410 | 1587 | 1587 | -177 | 89 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1399 | 1600 | 1600 | -201 | 87 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1385 | 1587 | 1587 | -202 | 87 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1384 | 1587 | 1587 | -203 | 87 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1383 | 1587 | 1587 | -204 | 87 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1380 | 1587 | 1587 | -207 | 87 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1378 | 1587 | 1587 | -209 | 87 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1377 | 1587 | 1587 | -210 | 87 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1374 | 1587 | 1587 | -213 | 87 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1373 | 1587 | 1587 | -214 | 87 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1373 | 1587 | 1587 | -214 | 86 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1373 | 1587 | 1587 | -214 | 86 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1371 | 1587 | 1587 | -216 | 86 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1371 | 1587 | 1587 | -216 | 86 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1370 | 1587 | 1587 | -217 | 86 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1370 | 1587 | 1587 | -217 | 86 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1370 | 1587 | 1587 | -217 | 86 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1368 | 1587 | 1587 | -219 | 86 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1357 | 1587 | 1587 | -230 | 86 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1354 | 1587 | 1587 | -233 | 85 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1347 | 1587 | 1587 | -240 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1342 | 1587 | 1587 | -245 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1341 | 1587 | 1587 | -246 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1295 | 1587 | 1587 | -292 | 82 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1195 | 1587 | 1587 | -392 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1177 | 1587 | 1587 | -410 | 74 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 | 1587 | 1587 | -434 | 73 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1128 | 1587 | 1587 | -459 | 71 | []

## 1530Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 15:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3172
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1585 |  | 1587 | -2 | 100 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1504 |  | 1587 | -83 | 95 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1503 |  | 1587 | -84 | 95 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1503 |  | 1587 | -84 | 95 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1478 |  | 1587 | -109 | 93 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1475 |  | 1587 | -112 | 93 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1472 |  | 1587 | -115 | 93 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1471 |  | 1587 | -116 | 93 | []
RS_BG_CO_00001 | N-1 TIE 400 kV Sofia Zapad - Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1467 |  | 1587 | -120 | 92 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1465 |  | 1587 | -122 | 92 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1461 |  | 1587 | -126 | 92 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1451 |  | 1587 | -136 | 91 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1447 |  | 1587 | -140 | 91 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1446 |  | 1587 | -141 | 91 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1443 |  | 1587 | -144 | 91 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1442 |  | 1587 | -145 | 91 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1434 |  | 1587 | -153 | 90 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1431 |  | 1587 | -156 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1423 |  | 1587 | -164 | 90 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1417 |  | 1587 | -170 | 89 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1411 |  | 1587 | -176 | 89 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1410 |  | 1587 | -177 | 89 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1399 |  | 1600 | -201 | 87 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1385 |  | 1587 | -202 | 87 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1384 |  | 1587 | -203 | 87 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1383 |  | 1587 | -204 | 87 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1380 |  | 1587 | -207 | 87 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1378 |  | 1587 | -209 | 87 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1377 |  | 1587 | -210 | 87 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1374 |  | 1587 | -213 | 87 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1373 |  | 1587 | -214 | 87 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1373 |  | 1587 | -214 | 86 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1373 |  | 1587 | -214 | 86 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1371 |  | 1587 | -216 | 86 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1371 |  | 1587 | -216 | 86 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1370 |  | 1587 | -217 | 86 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1370 |  | 1587 | -217 | 86 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1370 |  | 1587 | -217 | 86 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1368 |  | 1587 | -219 | 86 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1357 |  | 1587 | -230 | 86 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1354 |  | 1587 | -233 | 85 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1347 |  | 1587 | -240 | 85 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1342 |  | 1587 | -245 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1341 |  | 1587 | -246 | 84 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1295 |  | 1587 | -292 | 82 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1195 |  | 1587 | -392 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1177 |  | 1587 | -410 | 74 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 |  | 1587 | -434 | 73 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1128 |  | 1587 | -459 | 71 | []

## 1630Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3536
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1584 | 1587 | 1587 | -3 | 100 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1539 | 1587 | 1587 | -48 | 97 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1538 | 1587 | 1587 | -49 | 97 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1512 | 1587 | 1587 | -75 | 95 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1511 | 1587 | 1587 | -76 | 95 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1506 | 1587 | 1587 | -81 | 95 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1505 | 1587 | 1587 | -82 | 95 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1501 | 1587 | 1587 | -86 | 95 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1500 | 1587 | 1587 | -87 | 95 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1496 | 1587 | 1587 | -91 | 94 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1495 | 1587 | 1587 | -92 | 94 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1491 | 1587 | 1587 | -96 | 94 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1488 | 1587 | 1587 | -99 | 94 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1485 | 1587 | 1587 | -102 | 94 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1485 | 1587 | 1587 | -102 | 94 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1470 | 1587 | 1587 | -117 | 93 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1464 | 1587 | 1587 | -123 | 92 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1460 | 1587 | 1587 | -127 | 92 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1459 | 1587 | 1587 | -128 | 92 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1456 | 1587 | 1587 | -131 | 92 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1455 | 1587 | 1587 | -132 | 92 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1451 | 1587 | 1587 | -136 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1441 | 1587 | 1587 | -146 | 91 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1437 | 1587 | 1587 | -150 | 91 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1432 | 1587 | 1587 | -155 | 90 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1423 | 1587 | 1587 | -164 | 90 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1428 | 1600 | 1600 | -172 | 89 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1410 | 1587 | 1587 | -177 | 89 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1410 | 1587 | 1587 | -177 | 89 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1403 | 1587 | 1587 | -184 | 88 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1402 | 1587 | 1587 | -185 | 88 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1400 | 1587 | 1587 | -187 | 88 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1399 | 1587 | 1587 | -188 | 88 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1396 | 1587 | 1587 | -191 | 88 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1396 | 1587 | 1587 | -191 | 88 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1396 | 1587 | 1587 | -191 | 88 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1395 | 1587 | 1587 | -192 | 88 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1394 | 1587 | 1587 | -193 | 88 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1394 | 1587 | 1587 | -193 | 88 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1392 | 1587 | 1587 | -195 | 88 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1392 | 1587 | 1587 | -195 | 88 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1391 | 1587 | 1587 | -196 | 88 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1391 | 1587 | 1587 | -196 | 88 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1390 | 1587 | 1587 | -197 | 88 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1344 | 1587 | 1587 | -243 | 85 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1333 | 1587 | 1587 | -254 | 84 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 | 1587 | 1587 | -337 | 79 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1245 | 1587 | 1587 | -342 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1231 | 1587 | 1587 | -356 | 78 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 | 1587 | 1587 | -398 | 75 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1185 | 1587 | 1587 | -402 | 75 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1159 | 1587 | 1587 | -428 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1154 | 1587 | 1587 | -433 | 73 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1140 | 1587 | 1587 | -447 | 72 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1138 | 1587 | 1587 | -449 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1111 | 1587 | 1587 | -476 | 70 | []

## 1630Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 16:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3536
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1584 |  | 1587 | -3 | 100 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1539 |  | 1587 | -48 | 97 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1538 |  | 1587 | -49 | 97 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1512 |  | 1587 | -75 | 95 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1511 |  | 1587 | -76 | 95 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1506 |  | 1587 | -81 | 95 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1505 |  | 1587 | -82 | 95 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1501 |  | 1587 | -86 | 95 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1500 |  | 1587 | -87 | 95 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1496 |  | 1587 | -91 | 94 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1495 |  | 1587 | -92 | 94 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1491 |  | 1587 | -96 | 94 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1488 |  | 1587 | -99 | 94 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1485 |  | 1587 | -102 | 94 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1485 |  | 1587 | -102 | 94 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1470 |  | 1587 | -117 | 93 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | 1464 |  | 1587 | -123 | 92 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1460 |  | 1587 | -127 | 92 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1459 |  | 1587 | -128 | 92 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1456 |  | 1587 | -131 | 92 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1455 |  | 1587 | -132 | 92 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1451 |  | 1587 | -136 | 91 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1441 |  | 1587 | -146 | 91 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1437 |  | 1587 | -150 | 91 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1432 |  | 1587 | -155 | 90 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1423 |  | 1587 | -164 | 90 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1428 |  | 1600 | -172 | 89 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1410 |  | 1587 | -177 | 89 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1410 |  | 1587 | -177 | 89 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1403 |  | 1587 | -184 | 88 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1402 |  | 1587 | -185 | 88 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1400 |  | 1587 | -187 | 88 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1399 |  | 1587 | -188 | 88 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1396 |  | 1587 | -191 | 88 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1396 |  | 1587 | -191 | 88 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1396 |  | 1587 | -191 | 88 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1395 |  | 1587 | -192 | 88 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1394 |  | 1587 | -193 | 88 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1394 |  | 1587 | -193 | 88 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1392 |  | 1587 | -195 | 88 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1392 |  | 1587 | -195 | 88 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1391 |  | 1587 | -196 | 88 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1391 |  | 1587 | -196 | 88 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1390 |  | 1587 | -197 | 88 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1344 |  | 1587 | -243 | 85 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1333 |  | 1587 | -254 | 84 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1250 |  | 1587 | -337 | 79 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1245 |  | 1587 | -342 | 78 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1231 |  | 1587 | -356 | 78 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 |  | 1587 | -398 | 75 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1185 |  | 1587 | -402 | 75 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1159 |  | 1587 | -428 | 73 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1154 |  | 1587 | -433 | 73 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1140 |  | 1587 | -447 | 72 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1138 |  | 1587 | -449 | 72 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1111 |  | 1587 | -476 | 70 | []

## 1730Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3878
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1565 | 1587 | 1587 | -22 | 99 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1564 | 1587 | 1587 | -23 | 99 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1555 | 1587 | 1587 | -32 | 98 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1438 | 1587 | 1587 | -149 | 91 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1378 | 1587 | 1587 | -209 | 87 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1356 | 1587 | 1587 | -231 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1354 | 1587 | 1587 | -233 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1332 | 1587 | 1587 | -255 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1332 | 1587 | 1587 | -255 | 84 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1318 | 1587 | 1587 | -269 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1297 | 1587 | 1587 | -290 | 82 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1281 | 1587 | 1587 | -306 | 81 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1276 | 1587 | 1587 | -311 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1276 | 1587 | 1587 | -311 | 80 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1275 | 1587 | 1587 | -312 | 80 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1266 | 1587 | 1587 | -321 | 80 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1266 | 1587 | 1587 | -321 | 80 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 | 1587 | 1587 | -325 | 80 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1249 | 1587 | 1587 | -338 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1249 | 1587 | 1587 | -338 | 79 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1252 | 1600 | 1600 | -348 | 78 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1239 | 1587 | 1587 | -348 | 78 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1235 | 1587 | 1587 | -352 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1233 | 1587 | 1587 | -354 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1239 | 1600 | 1600 | -361 | 77 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1227 | 1587 | 1587 | -360 | 77 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1225 | 1587 | 1587 | -362 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1223 | 1587 | 1587 | -364 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1219 | 1587 | 1587 | -368 | 77 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 | 1587 | 1587 | -369 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1218 | 1587 | 1587 | -369 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1210 | 1587 | 1587 | -377 | 76 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1207 | 1587 | 1587 | -380 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1206 | 1587 | 1587 | -381 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1204 | 1587 | 1587 | -383 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1202 | 1587 | 1587 | -385 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1194 | 1587 | 1587 | -393 | 75 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 | 1587 | 1587 | -393 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1192 | 1587 | 1587 | -395 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1199 | 1600 | 1600 | -401 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1189 | 1587 | 1587 | -398 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1189 | 1587 | 1587 | -398 | 75 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1187 | 1587 | 1587 | -400 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1187 | 1587 | 1587 | -400 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1184 | 1587 | 1587 | -403 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1184 | 1587 | 1587 | -403 | 75 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1184 | 1587 | 1587 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1181 | 1587 | 1587 | -406 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1179 | 1587 | 1587 | -408 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1179 | 1587 | 1587 | -408 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1178 | 1587 | 1587 | -409 | 74 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1178 | 1587 | 1587 | -409 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1178 | 1587 | 1587 | -409 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1178 | 1587 | 1587 | -409 | 74 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1174 | 1587 | 1587 | -413 | 74 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1163 | 1587 | 1587 | -424 | 73 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1159 | 1587 | 1587 | -428 | 73 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 | 1587 | 1587 | -431 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1147 | 1600 | 1600 | -453 | 72 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1120 | 1587 | 1587 | -467 | 71 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1119 | 1587 | 1587 | -468 | 70 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1116 | 1587 | 1587 | -471 | 70 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1113 | 1587 | 1587 | -474 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 17:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3878
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1565 |  | 1587 | -22 | 99 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1564 |  | 1587 | -23 | 99 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1555 |  | 1587 | -32 | 98 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1438 |  | 1587 | -149 | 91 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1378 |  | 1587 | -209 | 87 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1356 |  | 1587 | -231 | 85 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1354 |  | 1587 | -233 | 85 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1332 |  | 1587 | -255 | 84 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1332 |  | 1587 | -255 | 84 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1318 |  | 1587 | -269 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1297 |  | 1587 | -290 | 82 | []
MK_CO_00001 | N-1 OHL 400 kV Bitola 2 - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1281 |  | 1587 | -306 | 81 | []
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1276 |  | 1587 | -311 | 80 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1276 |  | 1587 | -311 | 80 | []
MK_CO_00002 | N-1 OHL 400 kV Dubrovo - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1275 |  | 1587 | -312 | 80 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1266 |  | 1587 | -321 | 80 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1266 |  | 1587 | -321 | 80 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1262 |  | 1587 | -325 | 80 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1249 |  | 1587 | -338 | 79 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1249 |  | 1587 | -338 | 79 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1252 |  | 1600 | -348 | 78 | []
MK_CO_00003 | N-1 OHL 400 kV Skopje 4 - Skopje 5 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1239 |  | 1587 | -348 | 78 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1235 |  | 1587 | -352 | 78 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1233 |  | 1587 | -354 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1239 |  | 1600 | -361 | 77 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1227 |  | 1587 | -360 | 77 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1225 |  | 1587 | -362 | 77 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1223 |  | 1587 | -364 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1219 |  | 1587 | -368 | 77 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1218 |  | 1587 | -369 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1218 |  | 1587 | -369 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1210 |  | 1587 | -377 | 76 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1207 |  | 1587 | -380 | 76 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1206 |  | 1587 | -381 | 76 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1204 |  | 1587 | -383 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1202 |  | 1587 | -385 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1194 |  | 1587 | -393 | 75 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1194 |  | 1587 | -393 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1192 |  | 1587 | -395 | 75 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1199 |  | 1600 | -401 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1189 |  | 1587 | -398 | 75 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1189 |  | 1587 | -398 | 75 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1187 |  | 1587 | -400 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1187 |  | 1587 | -400 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1184 |  | 1587 | -403 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1184 |  | 1587 | -403 | 75 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1184 |  | 1587 | -403 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1181 |  | 1587 | -406 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1179 |  | 1587 | -408 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1179 |  | 1587 | -408 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1178 |  | 1587 | -409 | 74 | []
BC | Base Case | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1178 |  | 1587 | -409 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1178 |  | 1587 | -409 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1178 |  | 1587 | -409 | 74 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1174 |  | 1587 | -413 | 74 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-AL] [OPP] TIE 400 kV Kardia - Zemblak | XZE_KA11_GKARDI13_1:line | 1163 |  | 1587 | -424 | 73 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | 1159 |  | 1587 | -428 | 73 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 |  | 1587 | -431 | 73 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1147 |  | 1600 | -453 | 72 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1120 |  | 1587 | -467 | 71 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1119 |  | 1587 | -468 | 70 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1116 |  | 1587 | -471 | 70 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1113 |  | 1587 | -474 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3339
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1580 | 1587 | 1587 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1477 | 1587 | 1587 | -110 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1428 | 1587 | 1587 | -159 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1428 | 1587 | 1587 | -159 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1384 | 1587 | 1587 | -203 | 87 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1364 | 1587 | 1587 | -223 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1363 | 1587 | 1587 | -224 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1361 | 1587 | 1587 | -226 | 86 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1343 | 1587 | 1587 | -244 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1320 | 1587 | 1587 | -267 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 | 1600 | 1600 | -323 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 | 1587 | 1587 | -336 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 | 1587 | 1587 | -343 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 | 1587 | 1587 | -356 | 78 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 | 1587 | 1587 | -359 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1220 | 1587 | 1587 | -367 | 77 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 | 1587 | 1587 | -372 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 | 1587 | 1587 | -374 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1587 | 1587 | -375 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1587 | 1587 | -375 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 | 1587 | 1587 | -377 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 | 1587 | 1587 | -377 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 | 1587 | 1587 | -379 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 | 1587 | 1587 | -380 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 | 1587 | 1587 | -382 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 | 1587 | 1587 | -383 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1587 | 1587 | -384 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1587 | 1587 | -384 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 | 1587 | 1587 | -387 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1587 | 1587 | -389 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1587 | 1587 | -390 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 | 1587 | 1587 | -395 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 | 1587 | 1587 | -395 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 | 1587 | 1587 | -395 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 | 1587 | 1587 | -397 | 75 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 | 1587 | 1587 | -409 | 74 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 | 1587 | 1587 | -413 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 | 1587 | 1587 | -421 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 | 1587 | 1587 | -421 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1161 | 1587 | 1587 | -426 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1157 | 1587 | 1587 | -430 | 73 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1159 | 1600 | 1600 | -441 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1134 | 1600 | 1600 | -466 | 71 | []

## 1830Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 18:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3339
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1580 |  | 1587 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1477 |  | 1587 | -110 | 93 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1428 |  | 1587 | -159 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1428 |  | 1587 | -159 | 90 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1384 |  | 1587 | -203 | 87 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1364 |  | 1587 | -223 | 86 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1363 |  | 1587 | -224 | 86 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1361 |  | 1587 | -226 | 86 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1343 |  | 1587 | -244 | 85 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1320 |  | 1587 | -267 | 83 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 |  | 1600 | -323 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1251 |  | 1587 | -336 | 79 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1244 |  | 1587 | -343 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1231 |  | 1587 | -356 | 78 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 |  | 1587 | -359 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1220 |  | 1587 | -367 | 77 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1215 |  | 1587 | -372 | 77 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1213 |  | 1587 | -374 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1587 | -375 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1587 | -375 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 |  | 1587 | -377 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1210 |  | 1587 | -377 | 76 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 |  | 1587 | -379 | 76 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1207 |  | 1587 | -380 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1205 |  | 1587 | -382 | 76 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1204 |  | 1587 | -383 | 76 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1587 | -384 | 76 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1587 | -384 | 76 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 |  | 1587 | -387 | 76 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1587 | -389 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1587 | -390 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 |  | 1587 | -395 | 75 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 |  | 1587 | -395 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1192 |  | 1587 | -395 | 75 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 |  | 1587 | -397 | 75 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 |  | 1587 | -409 | 74 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1174 |  | 1587 | -413 | 74 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 |  | 1587 | -421 | 74 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 |  | 1587 | -421 | 74 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1161 |  | 1587 | -426 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1157 |  | 1587 | -430 | 73 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1159 |  | 1600 | -441 | 72 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-BG] [OPP] TIE 400 kV Lagadas - Blagoevgrad | XBG_LA11_GLAGAD11_1:line | 1134 |  | 1600 | -466 | 71 | []

## 1930Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3090
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1584 | 1587 | 1587 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1487 | 1587 | 1587 | -100 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1432 | 1587 | 1587 | -155 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1385 | 1587 | 1587 | -202 | 87 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1382 | 1587 | 1587 | -205 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1381 | 1587 | 1587 | -206 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1344 | 1587 | 1587 | -243 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1330 | 1587 | 1587 | -257 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1326 | 1587 | 1587 | -261 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1299 | 1587 | 1587 | -288 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 | 1600 | 1600 | -346 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 | 1587 | 1587 | -344 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1235 | 1587 | 1587 | -352 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 | 1587 | 1587 | -359 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 | 1587 | 1587 | -373 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1587 | 1587 | -375 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 | 1587 | 1587 | -379 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 | 1587 | 1587 | -381 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1587 | 1587 | -384 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 | 1587 | 1587 | -386 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 | 1587 | 1587 | -386 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 | 1587 | 1587 | -387 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1587 | 1587 | -389 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1587 | 1587 | -389 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1587 | 1587 | -390 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1587 | 1587 | -390 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1587 | 1587 | -390 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1587 | 1587 | -391 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1587 | 1587 | -391 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1587 | 1587 | -391 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 | 1587 | 1587 | -396 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 | 1587 | 1587 | -397 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 | 1587 | 1587 | -402 | 75 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 | 1587 | 1587 | -406 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1587 | 1587 | -407 | 74 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 | 1587 | 1587 | -408 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 | 1587 | 1587 | -421 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 | 1587 | 1587 | -421 | 73 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 | 1587 | 1587 | -434 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1147 | 1587 | 1587 | -440 | 72 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 | 1587 | 1587 | -461 | 71 | []

## 1930Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 19:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3090
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1584 |  | 1587 | -3 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1487 |  | 1587 | -100 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1432 |  | 1587 | -155 | 90 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1385 |  | 1587 | -202 | 87 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1382 |  | 1587 | -205 | 87 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1381 |  | 1587 | -206 | 87 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1344 |  | 1587 | -243 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1330 |  | 1587 | -257 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1326 |  | 1587 | -261 | 84 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1299 |  | 1587 | -288 | 82 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1254 |  | 1600 | -346 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1243 |  | 1587 | -344 | 78 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1235 |  | 1587 | -352 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1228 |  | 1587 | -359 | 77 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 |  | 1587 | -373 | 77 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1587 | -375 | 76 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1208 |  | 1587 | -379 | 76 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1206 |  | 1587 | -381 | 76 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1587 | -384 | 76 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 |  | 1587 | -386 | 76 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1201 |  | 1587 | -386 | 76 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1200 |  | 1587 | -387 | 76 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1587 | -389 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1587 | -389 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1587 | -390 | 75 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1587 | -390 | 75 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1587 | -390 | 75 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1587 | -391 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1587 | -391 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1587 | -391 | 75 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 |  | 1587 | -396 | 75 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 |  | 1587 | -397 | 75 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 |  | 1587 | -402 | 75 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 |  | 1587 | -406 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1587 | -407 | 74 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 |  | 1587 | -408 | 74 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 |  | 1587 | -421 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 |  | 1587 | -421 | 73 | []
MK_AL_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1153 |  | 1587 | -434 | 73 | []
MK_KS_CO_00001 | N-1 TIE 400 kV Skopje 5 - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1147 |  | 1587 | -440 | 72 | []
GR_CO_00008 | N-1 OHL 400 kV Kardia - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1126 |  | 1587 | -461 | 71 | []

## 2030Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3145
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 | 1587 | 1587 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1492 | 1587 | 1587 | -95 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1426 | 1587 | 1587 | -161 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1407 | 1587 | 1587 | -180 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1406 | 1587 | 1587 | -181 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1361 | 1587 | 1587 | -226 | 86 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1310 | 1587 | 1587 | -277 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1306 | 1587 | 1587 | -281 | 82 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1296 | 1587 | 1587 | -291 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1281 | 1587 | 1587 | -306 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 | 1587 | 1587 | -357 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1235 | 1600 | 1600 | -365 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 | 1587 | 1587 | -371 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 | 1587 | 1587 | -378 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1587 | 1587 | -390 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 | 1587 | 1587 | -394 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1587 | 1587 | -399 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 | 1587 | 1587 | -402 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 | 1587 | 1587 | -402 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 | 1587 | 1587 | -403 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 | 1587 | 1587 | -404 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 | 1587 | 1587 | -405 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 | 1587 | 1587 | -405 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1587 | 1587 | -407 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1587 | 1587 | -407 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 | 1587 | 1587 | -408 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 | 1587 | 1587 | -410 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 | 1587 | 1587 | -411 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 | 1587 | 1587 | -411 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 | 1587 | 1587 | -415 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1168 | 1587 | 1587 | -419 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1168 | 1587 | 1587 | -419 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 | 1587 | 1587 | -423 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1162 | 1587 | 1587 | -425 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1157 | 1587 | 1587 | -430 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1155 | 1587 | 1587 | -432 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 | 1587 | 1587 | -436 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1140 | 1587 | 1587 | -447 | 72 | []

## 2030Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 20:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3145
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 |  | 1587 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1492 |  | 1587 | -95 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1426 |  | 1587 | -161 | 90 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1407 |  | 1587 | -180 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1406 |  | 1587 | -181 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1361 |  | 1587 | -226 | 86 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1310 |  | 1587 | -277 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1306 |  | 1587 | -281 | 82 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1296 |  | 1587 | -291 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1281 |  | 1587 | -306 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 |  | 1587 | -357 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1235 |  | 1600 | -365 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1216 |  | 1587 | -371 | 77 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 |  | 1587 | -378 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1587 | -390 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 |  | 1587 | -394 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1587 | -399 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 |  | 1587 | -402 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 |  | 1587 | -402 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 |  | 1587 | -403 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 |  | 1587 | -404 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 |  | 1587 | -405 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 |  | 1587 | -405 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1587 | -407 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1587 | -407 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 |  | 1587 | -408 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 |  | 1587 | -410 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 |  | 1587 | -411 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 |  | 1587 | -411 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 |  | 1587 | -415 | 74 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1168 |  | 1587 | -419 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1168 |  | 1587 | -419 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 |  | 1587 | -423 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1162 |  | 1587 | -425 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1157 |  | 1587 | -430 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1155 |  | 1587 | -432 | 73 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 |  | 1587 | -436 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1140 |  | 1587 | -447 | 72 | []

## 2130Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3172
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 | 1587 | 1587 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1504 | 1587 | 1587 | -83 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1437 | 1587 | 1587 | -150 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1417 | 1587 | 1587 | -170 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1416 | 1587 | 1587 | -171 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1350 | 1587 | 1587 | -237 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1303 | 1587 | 1587 | -284 | 82 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1299 | 1587 | 1587 | -288 | 82 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1280 | 1587 | 1587 | -307 | 81 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 | 1587 | 1587 | -310 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 | 1587 | 1587 | -354 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1227 | 1600 | 1600 | -373 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 | 1587 | 1587 | -378 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 | 1587 | 1587 | -388 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 | 1587 | 1587 | -390 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1587 | 1587 | -399 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 | 1587 | 1587 | -401 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1587 | 1587 | -407 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 | 1587 | 1587 | -410 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 | 1587 | 1587 | -410 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 | 1587 | 1587 | -415 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1171 | 1587 | 1587 | -416 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1171 | 1587 | 1587 | -416 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 | 1587 | 1587 | -418 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 | 1587 | 1587 | -418 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 | 1587 | 1587 | -418 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 | 1587 | 1587 | -421 | 73 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1163 | 1587 | 1587 | -424 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1162 | 1587 | 1587 | -425 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 | 1587 | 1587 | -431 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1155 | 1587 | 1587 | -432 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1146 | 1587 | 1587 | -441 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 | 1587 | 1587 | -445 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 | 1587 | 1587 | -445 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1131 | 1587 | 1587 | -456 | 71 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1125 | 1587 | 1587 | -462 | 71 | []

## 2130Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 21:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3172
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1582 |  | 1587 | -5 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1504 |  | 1587 | -83 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1437 |  | 1587 | -150 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1417 |  | 1587 | -170 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1416 |  | 1587 | -171 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1350 |  | 1587 | -237 | 85 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1303 |  | 1587 | -284 | 82 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1299 |  | 1587 | -288 | 82 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1280 |  | 1587 | -307 | 81 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1277 |  | 1587 | -310 | 80 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1233 |  | 1587 | -354 | 78 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1227 |  | 1600 | -373 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1209 |  | 1587 | -378 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1199 |  | 1587 | -388 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1197 |  | 1587 | -390 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1587 | -399 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 |  | 1587 | -401 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1587 | -407 | 74 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 |  | 1587 | -410 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 |  | 1587 | -410 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 |  | 1587 | -415 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1171 |  | 1587 | -416 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1171 |  | 1587 | -416 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 |  | 1587 | -418 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 |  | 1587 | -418 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1169 |  | 1587 | -418 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1166 |  | 1587 | -421 | 73 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1163 |  | 1587 | -424 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1162 |  | 1587 | -425 | 73 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1156 |  | 1587 | -431 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1155 |  | 1587 | -432 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1146 |  | 1587 | -441 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 |  | 1587 | -445 | 72 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1142 |  | 1587 | -445 | 72 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1131 |  | 1587 | -456 | 71 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1125 |  | 1587 | -462 | 71 | []

## 2230Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3208
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1580 | 1587 | 1587 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1503 | 1587 | 1587 | -84 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1440 | 1587 | 1587 | -147 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1408 | 1587 | 1587 | -179 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1407 | 1587 | 1587 | -180 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1358 | 1587 | 1587 | -229 | 86 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1317 | 1587 | 1587 | -270 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1310 | 1587 | 1587 | -277 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1298 | 1587 | 1587 | -289 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1283 | 1587 | 1587 | -304 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 | 1587 | 1587 | -357 | 77 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 | 1600 | 1600 | -361 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 | 1587 | 1587 | -373 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 | 1587 | 1587 | -384 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1587 | 1587 | -391 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 | 1587 | 1587 | -394 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 | 1587 | 1587 | -403 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 | 1587 | 1587 | -403 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 | 1587 | 1587 | -406 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 | 1587 | 1587 | -407 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 | 1587 | 1587 | -408 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 | 1587 | 1587 | -409 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 | 1587 | 1587 | -409 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 | 1587 | 1587 | -410 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 | 1587 | 1587 | -414 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 | 1587 | 1587 | -417 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 | 1587 | 1587 | -417 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 | 1587 | 1587 | -423 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1161 | 1587 | 1587 | -426 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1157 | 1587 | 1587 | -430 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1152 | 1587 | 1587 | -435 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 | 1587 | 1587 | -436 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 | 1587 | 1587 | -438 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1141 | 1587 | 1587 | -446 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1136 | 1587 | 1587 | -451 | 72 | []

## 2230Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 22:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3208
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1580 |  | 1587 | -7 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1503 |  | 1587 | -84 | 95 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1440 |  | 1587 | -147 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1408 |  | 1587 | -179 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1407 |  | 1587 | -180 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1358 |  | 1587 | -229 | 86 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1317 |  | 1587 | -270 | 83 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1310 |  | 1587 | -277 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1298 |  | 1587 | -289 | 82 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1283 |  | 1587 | -304 | 81 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1230 |  | 1587 | -357 | 77 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1239 |  | 1600 | -361 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1214 |  | 1587 | -373 | 76 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1203 |  | 1587 | -384 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1587 | -391 | 75 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1193 |  | 1587 | -394 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 |  | 1587 | -403 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1184 |  | 1587 | -403 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1181 |  | 1587 | -406 | 74 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1180 |  | 1587 | -407 | 74 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 |  | 1587 | -408 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 |  | 1587 | -409 | 74 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1178 |  | 1587 | -409 | 74 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1177 |  | 1587 | -410 | 74 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1173 |  | 1587 | -414 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 |  | 1587 | -417 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 |  | 1587 | -417 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1164 |  | 1587 | -423 | 73 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1161 |  | 1587 | -426 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1157 |  | 1587 | -430 | 73 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1152 |  | 1587 | -435 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1151 |  | 1587 | -436 | 73 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1149 |  | 1587 | -438 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1141 |  | 1587 | -446 | 72 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1136 |  | 1587 | -451 | 72 | []

## 2330Preventive
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3379
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1587 | 1587 | 1587 | 0 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1497 | 1587 | 1587 | -90 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1442 | 1587 | 1587 | -145 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1406 | 1587 | 1587 | -181 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1405 | 1587 | 1587 | -182 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1394 | 1587 | 1587 | -193 | 88 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1336 | 1587 | 1587 | -251 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1323 | 1587 | 1587 | -264 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1318 | 1587 | 1587 | -269 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1293 | 1587 | 1587 | -294 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 | 1600 | 1600 | -352 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 | 1587 | 1587 | -350 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1227 | 1587 | 1587 | -360 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 | 1587 | 1587 | -375 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 | 1587 | 1587 | -389 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 | 1587 | 1587 | -391 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 | 1587 | 1587 | -396 | 75 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 | 1587 | 1587 | -397 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 | 1587 | 1587 | -398 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 | 1587 | 1587 | -398 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1587 | 1587 | -399 | 75 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 | 1587 | 1587 | -399 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1187 | 1587 | 1587 | -400 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 | 1587 | 1587 | -401 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 | 1587 | 1587 | -402 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 | 1587 | 1587 | -404 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 | 1587 | 1587 | -404 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 | 1587 | 1587 | -405 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 | 1587 | 1587 | -408 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 | 1587 | 1587 | -411 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 | 1587 | 1587 | -412 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 | 1587 | 1587 | -415 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 | 1587 | 1587 | -417 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1163 | 1587 | 1587 | -424 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1162 | 1587 | 1587 | -425 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1159 | 1587 | 1587 | -428 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 | 1587 | 1587 | -439 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1144 | 1587 | 1587 | -443 | 72 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1124 | 1600 | 1600 | -476 | 70 | []

## 2330Curative
Detailed results
Generated at: | 2026-06-05 08:29
Business day: | 05.06.2026
Timestamp: | 23:30
Border & direction: | North-Greece Exporting
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3379
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
GR_MK_CO_00002 | N-1 TIE 400 kV Thessaloniki - Dubrovo | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1587 |  | 1587 | 0 | 100 | []
GR_AL_CO_00001 | N-1 TIE 400 kV Kardia - Zemblak / N-1 TIE 150 kV Mourtos - Bistrica | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1497 |  | 1587 | -90 | 94 | []
AL_CO_00002 | N-1 OHL 400 kV Elbasan 2 - Zemblak | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1442 |  | 1587 | -145 | 91 | []
GR_CO_00003 | N-1 OHL 400 kV Meliti - Amideo ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1406 |  | 1587 | -181 | 89 | []
GR_MK_CO_00001 | N-1 TIE 400 kV Meliti - Bitola | [GR-MK] [OPP] TIE 400 kV Thessaloniki - Dubrovo | XTH_DU11_GTHESS11_1:line | -1405 |  | 1587 | -182 | 89 | []
GR_CO_00006 | N-1 OHL 400 kV Komotini - Nea Santa ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1394 |  | 1587 | -193 | 88 | []
GR_CO_00007 | N-1 OHL 400 kV Thessaloniki - Agios Dimitrios ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1336 |  | 1587 | -251 | 84 | []
GR_BG_CO_00001 | N-1 TIE 400 kV Lagadas - Blagoevgrad | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1323 |  | 1587 | -264 | 83 | []
GR_CO_00004 | N-1 OHL 400 kV Amideo - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1318 |  | 1587 | -269 | 83 | []
BG-CO_00001, BG_CO_00001 | N-1 OHL 400 kV Chervena Mogila - Blagoevgrad ck. 1&2, N-1 OHL 400 kV CHERVENA MOGILA - BLAGOEVGRAD CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1293 |  | 1587 | -294 | 81 | []
GR_BG_CO_00002 | N-1 TIE 400 kV Nea Santa - Maritsa Iztok | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1248 |  | 1600 | -352 | 78 | []
AL_CO_00001 | N-1 OHL 400 kV Elbasan 2 - Tirana 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1237 |  | 1587 | -350 | 78 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1227 |  | 1587 | -360 | 77 | []
BG-CO_00012 | N-1 OHL 400 kV Varna - Burgas | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1212 |  | 1587 | -375 | 76 | []
RS_BG_CO_00001, RO_CO_00052 | N-1 TIE 400 kV Sofia Zapad - Nis, N-1 OHL 400 kV Sofia Zapad -Nis | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1198 |  | 1587 | -389 | 76 | []
BG-CO_00013 | N-1 OHL 400 kV Maritsa Iztok - Plovdiv | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1196 |  | 1587 | -391 | 75 | []
BG-CO_00018 | N-1 OHL 400 kV Burgas- Maritsa Iztok 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1191 |  | 1587 | -396 | 75 | []
GR_CO_00001 | N-1 OHL 400 kV Filippoi - Komotini ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1190 |  | 1587 | -397 | 75 | []
KS_ME_CO_00001 | N-1 TIE 400 kV Pec 3 - Ribarevina | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 |  | 1587 | -398 | 75 | []
TR_CO_00001 | N-1 OHL 400 kV Habitabat NGCC - Babaeski | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1189 |  | 1587 | -398 | 75 | []
AL_ME_CO_00001 | N-1 TIE 400 kV Tirana 2 – Podgorica 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1587 | -399 | 75 | []
GR_CO_00002 | N-1 OHL 400 kV Filippoi - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1188 |  | 1587 | -399 | 75 | []
TR_BG_CO_00002 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1187 |  | 1587 | -400 | 75 | []
TR_BG_CO_00001 | N-1 TIE 400 kV Maritsa 3 - Hamitabat 1 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1186 |  | 1587 | -401 | 75 | []
BG-CO_00005, BG_CO_00003 | N-1 OHL 400 kV Vetren - Chervena Mogila, N-1 OHL 400 kV VETREN - CHERVENA MOGILA | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1185 |  | 1587 | -402 | 75 | []
BG-CO_00019 | N-1 OHL 400 kV Maritsa Iztok 2 - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 |  | 1587 | -404 | 75 | []
BG-CO_00020 | N-1 OHL 400 kV Maritsa Iztok - Maritsa Iztok 3 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1183 |  | 1587 | -404 | 75 | []
BC | Base Case | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1182 |  | 1587 | -405 | 74 | []
BG-CO_00002, BG_CO_00002 | N-1 OHL 400 kV Sofia Zapad - Chervena Mogila ck. 1&2, N-1 OHL 400 kV SOFIA ZAPAD - CHERVENA MOGILA CK. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1179 |  | 1587 | -408 | 74 | []
BG-CO_00006, BG_CO_00004 | N-1 OHL 400 kV Plovdiv - Vetren, N-1 OHL 400 kV PLOVDIV - VETREN | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1176 |  | 1587 | -411 | 74 | []
RS_CO_00004 | N-1 OHL 400 kV Nis 2 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1175 |  | 1587 | -412 | 74 | []
BG-CO_00017 | N-1 OHL 400 kV Kozloduy - Sofia Zapad ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1172 |  | 1587 | -415 | 74 | []
RS_KS_CO_00002 | N-1 TIE 400 kV Kosovo B - Nis 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1170 |  | 1587 | -417 | 74 | []
KS_CO_00001 | N-1 OHL 400 kV Kosovo B - Urosevac | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1163 |  | 1587 | -424 | 73 | []
RS_CO_00003 | N-1 OHL 400 kV Vranje 4 - Leskovac 2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1162 |  | 1587 | -425 | 73 | []
MK_BG_CO_00001 | N-1 TIE 400 kV Chervena Mogila - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1159 |  | 1587 | -428 | 73 | []
RS_MK_CO_00001 | N-1 TIE 400 kV Vranje 4 - Stip | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1148 |  | 1587 | -439 | 72 | []
GR_CO_00005 | N-1 OHL 400 kV Thessaloniki - Lagadas ck. 1&2 | [GR-MK] [OPP] TIE 400 kV Meliti - Bitola | XFL_BI11_GMELIT11_1:line | -1144 |  | 1587 | -443 | 72 | []
GR_TR_CO_00001 | N-1 TIE 400 kV Nea Santa - Babaeski | [GR-BG] [OPP] TIE 400 kV Nea Santa - Maritsa Iztok | XMI_NS11_GNSANT15_1:line | -1124 |  | 1600 | -476 | 70 | []