## 0030
Detailed results
Generated at: | 05/06/2026 21:28:57
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3722.1
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1534 | 1570 | -36 | 98 | 1072 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1534 | 1570 | -36 | 98 | 1072 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1482 | 1570 | -88 | 94 | 1028 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1482 | 1570 | -88 | 94 | 1028 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1477 | 1570 | -93 | 94 | 1029 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 662 | 721 | -59 | 92 | 460 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 662 | 721 | -59 | 92 | 460 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 661 | 721 | -60 | 92 | 458 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 661 | 721 | -60 | 92 | 458 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 658 | 721 | -63 | 91 | 457 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 658 | 721 | -63 | 91 | 457 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1570 | -144 | 91 | 994 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1425 | 1570 | -145 | 91 | 992 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1422 | 1570 | -148 | 91 | 991 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1570 | -152 | 90 | 988 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1416 | 1570 | -154 | 90 | 986 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1415 | 1570 | -155 | 90 | 987 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1413 | 1570 | -157 | 90 | 985 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1403 | 1570 | -167 | 89 | 979 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1400 | 1570 | -170 | 89 | 976 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 539 | 721 | -182 | 75 | 369 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1453 | 2000 | -547 | 73 | -1013 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1453 | 2000 | -547 | 73 | 1029 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1445 | 2000 | -555 | 72 | -1005 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1445 | 2000 | -555 | 72 | 1023 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1363 | 1890 | -527 | 72 | -952 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1363 | 1890 | -527 | 72 | -952 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1363 | 1920 | -557 | 71 | 973 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1363 | 1920 | -557 | 71 | 973 | AC

## 0130
Detailed results
Generated at: | 05/06/2026 21:28:57
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3714.91
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1538 | 1570 | -32 | 98 | 1077 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1538 | 1570 | -32 | 98 | 1077 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1490 | 1570 | -80 | 95 | 1035 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1490 | 1570 | -80 | 95 | 1035 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1482 | 1570 | -88 | 94 | 1034 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 662 | 721 | -59 | 92 | 460 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 662 | 721 | -59 | 92 | 460 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 661 | 721 | -60 | 92 | 458 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 661 | 721 | -60 | 92 | 458 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 658 | 721 | -63 | 91 | 457 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 658 | 721 | -63 | 91 | 457 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1432 | 1570 | -138 | 91 | 1000 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1431 | 1570 | -139 | 91 | 998 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1427 | 1570 | -143 | 91 | 997 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1423 | 1570 | -147 | 91 | 993 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1423 | 1570 | -147 | 91 | 994 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1421 | 1570 | -149 | 91 | 993 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1419 | 1570 | -151 | 90 | 991 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1409 | 1570 | -161 | 90 | 985 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1405 | 1570 | -165 | 90 | 981 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 538 | 721 | -183 | 75 | 368 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1444 | 2000 | -556 | 72 | 1023 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1444 | 2000 | -556 | 72 | -1007 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1437 | 2000 | -563 | 72 | 1018 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1437 | 2000 | -563 | 72 | -1000 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1347 | 1890 | -543 | 71 | -941 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1347 | 1890 | -543 | 71 | -941 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1347 | 1920 | -573 | 70 | 962 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1347 | 1920 | -573 | 70 | 962 | AC

## 0230
Detailed results
Generated at: | 05/06/2026 21:28:58
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3698.84
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1570 | -40 | 97 | 1072 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1570 | -40 | 97 | 1072 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1484 | 1570 | -86 | 95 | 1031 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1484 | 1570 | -86 | 95 | 1031 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | 1031 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 660 | 721 | -61 | 92 | 458 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 660 | 721 | -61 | 92 | 458 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 658 | 721 | -63 | 91 | 456 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 658 | 721 | -63 | 91 | 456 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 656 | 721 | -65 | 91 | 455 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 656 | 721 | -65 | 91 | 455 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1427 | 1570 | -143 | 91 | 997 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1570 | -144 | 91 | 995 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1419 | 1570 | -151 | 90 | 991 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1570 | -152 | 90 | 990 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1417 | 1570 | -153 | 90 | 991 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1416 | 1570 | -154 | 90 | 990 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1412 | 1570 | -158 | 90 | 986 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1403 | 1570 | -167 | 89 | 982 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1400 | 1570 | -170 | 89 | 978 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 539 | 721 | -182 | 75 | 368 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1424 | 2000 | -576 | 71 | 1008 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1424 | 2000 | -576 | 71 | -993 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1340 | 1890 | -550 | 71 | -937 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1340 | 1890 | -550 | 71 | -937 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1416 | 2000 | -584 | 71 | 1004 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1416 | 2000 | -584 | 71 | -986 | AC

## 0330
Detailed results
Generated at: | 05/06/2026 21:28:58
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3759.22
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1537 | 1570 | -33 | 98 | 1078 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1537 | 1570 | -33 | 98 | 1078 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 676 | 721 | -45 | 94 | 470 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 676 | 721 | -45 | 94 | 470 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 674 | 721 | -47 | 94 | 468 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 674 | 721 | -47 | 94 | 468 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1467 | 1570 | -103 | 93 | 1019 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1467 | 1570 | -103 | 93 | 1019 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 672 | 721 | -49 | 93 | 467 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 672 | 721 | -49 | 93 | 467 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1462 | 1570 | -108 | 93 | 1022 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1416 | 1570 | -154 | 90 | 990 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1414 | 1570 | -156 | 90 | 988 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1410 | 1570 | -160 | 90 | 986 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1408 | 1570 | -162 | 90 | 985 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1407 | 1570 | -163 | 90 | 983 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1406 | 1570 | -164 | 90 | 984 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1405 | 1570 | -165 | 89 | 982 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1570 | -175 | 89 | 977 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1389 | 1570 | -181 | 88 | 972 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1461 | 1890 | -429 | 77 | -1018 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1461 | 1890 | -429 | 77 | -1018 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1461 | 1920 | -459 | 76 | 1043 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1461 | 1920 | -459 | 76 | 1043 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 539 | 721 | -182 | 75 | 368 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1474 | 2000 | -526 | 74 | 1044 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1474 | 2000 | -526 | 74 | -1027 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1466 | 2000 | -534 | 73 | 1038 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1466 | 2000 | -534 | 73 | -1020 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1404 | 2000 | -596 | 70 | 995 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1404 | 2000 | -596 | 70 | 1001 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1402 | 2000 | -598 | 70 | 995 | AC

## 0430
Detailed results
Generated at: | 05/06/2026 21:28:58
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3688.25
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1551 | 1570 | -19 | 99 | 1086 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1551 | 1570 | -19 | 99 | 1086 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1570 | -65 | 96 | 1046 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1570 | -65 | 96 | 1046 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1498 | 1570 | -72 | 95 | 1046 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1447 | 1570 | -123 | 92 | 1010 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1445 | 1570 | -125 | 92 | 1009 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1442 | 1570 | -128 | 92 | 1008 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1441 | 1570 | -129 | 92 | 1006 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1570 | -131 | 92 | 1004 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1437 | 1570 | -133 | 92 | 1004 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1432 | 1570 | -138 | 91 | 1000 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 657 | 721 | -64 | 91 | 455 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 657 | 721 | -64 | 91 | 455 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 655 | 721 | -66 | 91 | 454 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 655 | 721 | -66 | 91 | 454 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1424 | 1570 | -146 | 91 | 996 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1421 | 1570 | -149 | 91 | 992 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 652 | 721 | -69 | 90 | 452 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 652 | 721 | -69 | 90 | 452 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 539 | 721 | -182 | 75 | 368 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1346 | 1890 | -544 | 71 | -941 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1346 | 1890 | -544 | 71 | -941 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1346 | 1920 | -574 | 70 | 961 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1346 | 1920 | -574 | 70 | 961 | AC

## 0530
Detailed results
Generated at: | 05/06/2026 21:28:58
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3642.33
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1573 | 1570 | 3 | 100 | 1093 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1573 | 1570 | 3 | 100 | 1093 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1539 | 1570 | -31 | 98 | 1061 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1539 | 1570 | -31 | 98 | 1061 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1524 | 1570 | -46 | 97 | 1055 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1490 | 1570 | -80 | 95 | 1033 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1483 | 1570 | -87 | 94 | 1026 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1570 | -92 | 94 | 1023 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1471 | 1570 | -99 | 94 | 1018 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1468 | 1570 | -102 | 94 | 1016 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1459 | 1570 | -111 | 93 | 1010 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1457 | 1570 | -113 | 93 | 1009 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1454 | 1570 | -116 | 93 | 1007 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1440 | 1570 | -130 | 92 | 1000 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 659 | 721 | -62 | 91 | 457 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 659 | 721 | -62 | 91 | 457 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 657 | 721 | -64 | 91 | 456 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 657 | 721 | -64 | 91 | 456 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 655 | 721 | -66 | 91 | 454 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 655 | 721 | -66 | 91 | 454 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 542 | 721 | -179 | 75 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 538 | 721 | -183 | 75 | 368 | AC

## 0630
Detailed results
Generated at: | 05/06/2026 21:28:58
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3045.12
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1579 | 1570 | 9 | 101 | 1084 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1579 | 1570 | 9 | 101 | 1084 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | 1082 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1558 | 1570 | -12 | 99 | 1074 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1558 | 1570 | -12 | 99 | 1074 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1540 | 1570 | -30 | 98 | 1062 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1570 | -40 | 97 | 1052 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1519 | 1570 | -51 | 97 | 1044 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1508 | 1570 | -62 | 96 | 1037 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1504 | 1570 | -66 | 96 | 1035 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1497 | 1570 | -73 | 95 | 1030 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1491 | 1570 | -79 | 95 | 1026 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1488 | 1570 | -82 | 95 | 1024 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1483 | 1570 | -87 | 94 | 1021 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 635 | 721 | -86 | 88 | 440 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 635 | 721 | -86 | 88 | 440 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 633 | 721 | -88 | 88 | 438 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 633 | 721 | -88 | 88 | 438 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 631 | 721 | -90 | 88 | 437 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 631 | 721 | -90 | 88 | 437 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 541 | 721 | -180 | 75 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 541 | 721 | -180 | 75 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 538 | 721 | -183 | 75 | 368 | AC

## 0730
Detailed results
Generated at: | 05/06/2026 21:28:58
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3401.16
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | 1106 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | 1106 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1540 | 1570 | -30 | 98 | 1085 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1540 | 1570 | -30 | 98 | 1079 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1512 | 1570 | -58 | 96 | 1063 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1498 | 1570 | -72 | 95 | 1053 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1481 | 1570 | -89 | 94 | 1043 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1481 | 1570 | -89 | 94 | 1043 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1570 | -92 | 94 | 1041 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1477 | 1570 | -93 | 94 | 1040 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1471 | 1570 | -99 | 94 | 1037 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1450 | 1570 | -120 | 92 | 1023 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1447 | 1570 | -123 | 92 | 1020 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1570 | -127 | 92 | 1017 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 999 | 1248 | -250 | 80 | 404 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 999 | 1248 | -250 | 80 | 404 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 996 | 1248 | -252 | 80 | 403 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 996 | 1248 | -252 | 80 | 403 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 573 | 721 | -148 | 79 | 402 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 573 | 721 | -148 | 79 | 402 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 535 | 721 | -186 | 74 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 535 | 721 | -186 | 74 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 532 | 721 | -189 | 74 | 372 | AC

## 0830
Detailed results
Generated at: | 05/06/2026 21:28:58
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3139.72
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | 1119 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | 1119 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1545 | 1570 | -25 | 98 | 1102 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1544 | 1570 | -26 | 98 | 1097 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1503 | 1570 | -67 | 96 | 1071 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1496 | 1570 | -74 | 95 | 1066 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1479 | 1570 | -91 | 94 | 1054 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | 1053 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1469 | 1570 | -101 | 94 | 1048 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1570 | -104 | 93 | 1046 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1570 | -104 | 93 | 1046 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1570 | -122 | 92 | 1033 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1447 | 1570 | -123 | 92 | 1033 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1438 | 1570 | -132 | 92 | 1026 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 955 | 1248 | -294 | 76 | 389 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 955 | 1248 | -294 | 76 | 389 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 952 | 1248 | -296 | 76 | 388 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 952 | 1248 | -296 | 76 | 388 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 949 | 1248 | -300 | 76 | 387 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 949 | 1248 | -300 | 76 | 387 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 920 | 1248 | -329 | 74 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 920 | 1248 | -329 | 74 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 914 | 1248 | -335 | 73 | 372 | AC

## 0930
Detailed results
Generated at: | 05/06/2026 21:28:58
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3466.36
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1567 | 1570 | -3 | 100 | 1118 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1567 | 1570 | -3 | 100 | 1118 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1544 | 1570 | -26 | 98 | 1098 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1534 | 1570 | -36 | 98 | 1094 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1570 | -85 | 95 | 1059 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1484 | 1570 | -86 | 94 | 1058 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1474 | 1570 | -96 | 94 | 1051 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1470 | 1570 | -100 | 94 | 1049 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1470 | 1570 | -100 | 94 | 1049 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1470 | 1570 | -100 | 94 | 1049 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1463 | 1570 | -107 | 93 | 1044 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1445 | 1570 | -125 | 92 | 1031 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1441 | 1570 | -129 | 92 | 1028 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1436 | 1570 | -134 | 91 | 1024 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 985 | 1248 | -263 | 79 | 402 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 985 | 1248 | -263 | 79 | 402 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 982 | 1248 | -266 | 79 | 401 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 982 | 1248 | -266 | 79 | 401 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 979 | 1248 | -270 | 78 | 400 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 979 | 1248 | -270 | 78 | 400 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 922 | 1248 | -327 | 74 | 376 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 922 | 1248 | -327 | 74 | 376 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 916 | 1248 | -333 | 73 | 374 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1458 | 2000 | -542 | 73 | 1035 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1437 | 2000 | -563 | 72 | 1021 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1433 | 2000 | -567 | 72 | 1014 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1427 | 2000 | -573 | 71 | 1011 | AC

## 1030
Detailed results
Generated at: | 05/06/2026 21:28:58
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3683.01
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1570 | -131 | 92 | 1024 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1570 | -131 | 92 | 1024 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1407 | 1570 | -163 | 90 | 1002 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1402 | 1570 | -168 | 89 | 997 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1570 | -205 | 87 | 971 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1570 | -205 | 87 | 971 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1356 | 1570 | -214 | 86 | 964 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1353 | 1570 | -217 | 86 | 962 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1349 | 1570 | -221 | 86 | 959 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1349 | 1570 | -221 | 86 | 958 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1341 | 1570 | -229 | 85 | 953 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1327 | 1570 | -243 | 85 | 943 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1322 | 1570 | -248 | 84 | 939 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1319 | 1570 | -251 | 84 | 937 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1037 | 1248 | -212 | 83 | 424 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1037 | 1248 | -212 | 83 | 424 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1034 | 1248 | -214 | 83 | 423 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1034 | 1248 | -214 | 83 | 423 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1030 | 1248 | -218 | 83 | 421 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1030 | 1248 | -218 | 83 | 421 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1572 | 2000 | -428 | 79 | 1118 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1547 | 2000 | -453 | 77 | 1098 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1544 | 2000 | -456 | 77 | 1099 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1539 | 2000 | -461 | 77 | 1093 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1485 | 2000 | -515 | 74 | 1057 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 920 | 1248 | -329 | 74 | 376 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 920 | 1248 | -329 | 74 | 376 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 914 | 1248 | -335 | 73 | 373 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1461 | 2000 | -539 | 73 | 1039 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1459 | 2000 | -541 | 73 | 1035 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1455 | 2000 | -545 | 73 | 1033 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1453 | 2000 | -547 | 73 | 1037 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1450 | 2000 | -550 | 72 | 1032 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1414 | 2000 | -586 | 71 | 1007 | AC

## 1130
Detailed results
Generated at: | 05/06/2026 21:28:58
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3855.43
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1101 | 1248 | -147 | 88 | 450 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1101 | 1248 | -147 | 88 | 450 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1098 | 1248 | -150 | 88 | 449 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1098 | 1248 | -150 | 88 | 449 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1094 | 1248 | -154 | 88 | 447 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1094 | 1248 | -154 | 88 | 447 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1655 | 2000 | -345 | 83 | 1176 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1637 | 2000 | -363 | 82 | 1165 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1620 | 2000 | -380 | 81 | 1150 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1619 | 2000 | -381 | 81 | 1150 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1585 | 2000 | -415 | 79 | 1125 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1583 | 2000 | -417 | 79 | 1127 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1583 | 2000 | -417 | 79 | 1123 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1581 | 2000 | -419 | 79 | 1128 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1575 | 2000 | -425 | 79 | 1121 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1558 | 2000 | -442 | 78 | 1108 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1466 | 1890 | -424 | 78 | -1020 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1466 | 1890 | -424 | 78 | -1020 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1209 | 1570 | -361 | 77 | 854 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1209 | 1570 | -361 | 77 | 854 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1466 | 1920 | -454 | 76 | 1044 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1466 | 1920 | -454 | 76 | 1044 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1520 | 2000 | -480 | 76 | 1082 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1186 | 1570 | -384 | 76 | 836 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1179 | 1570 | -391 | 75 | 831 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1179 | 1570 | -391 | 75 | 831 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1179 | 1570 | -391 | 75 | 831 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1487 | 2000 | -513 | 74 | -1035 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1487 | 2000 | -513 | 74 | 1052 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1479 | 2000 | -521 | 74 | 1047 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1479 | 2000 | -521 | 74 | -1027 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 917 | 1248 | -332 | 73 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 917 | 1248 | -332 | 73 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 911 | 1248 | -338 | 73 | 372 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1457 | 2000 | -543 | 73 | 1036 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1128 | 1570 | -442 | 72 | 795 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1435 | 2000 | -565 | 72 | 1020 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1126 | 1570 | -444 | 72 | 793 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1124 | 1570 | -446 | 72 | 792 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1120 | 1570 | -450 | 71 | 789 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1426 | 2000 | -574 | 71 | 1014 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1118 | 1570 | -452 | 71 | 788 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1117 | 1570 | -453 | 71 | 787 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1115 | 1570 | -455 | 71 | 785 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1107 | 1570 | -463 | 70 | 779 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1409 | 2000 | -591 | 70 | 995 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1403 | 2000 | -597 | 70 | 992 | AC

## 1230
Detailed results
Generated at: | 05/06/2026 21:28:59
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3826.68
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1146 | 1248 | -103 | 92 | 468 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1146 | 1248 | -103 | 92 | 468 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1570 | -131 | 92 | 1022 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1143 | 1248 | -106 | 92 | 467 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1143 | 1248 | -106 | 92 | 467 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1139 | 1248 | -110 | 91 | 465 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1139 | 1248 | -110 | 91 | 465 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1598 | 1890 | -292 | 85 | -1108 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1598 | 1890 | -292 | 85 | -1108 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1690 | 2000 | -310 | 84 | 1201 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1671 | 2000 | -329 | 84 | 1189 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1598 | 1920 | -322 | 83 | 1138 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1598 | 1920 | -322 | 83 | 1138 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1654 | 2000 | -346 | 83 | 1173 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1653 | 2000 | -347 | 83 | 1174 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1623 | 2000 | -377 | 81 | 1150 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1620 | 2000 | -380 | 81 | 1149 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1618 | 2000 | -382 | 81 | 1153 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1618 | 2000 | -382 | 81 | 1151 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1612 | 2000 | -388 | 81 | 1147 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1592 | 2000 | -408 | 80 | 1132 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1555 | 2000 | -445 | 78 | 1106 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1528 | 2000 | -472 | 76 | 1081 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1528 | 2000 | -472 | 76 | -1063 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1520 | 2000 | -480 | 76 | 1075 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1520 | 2000 | -480 | 76 | -1055 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1183 | 1570 | -387 | 75 | 836 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1181 | 1570 | -389 | 75 | 834 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1181 | 1570 | -389 | 75 | 834 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1487 | 2000 | -513 | 74 | 1056 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 917 | 1248 | -331 | 73 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 917 | 1248 | -331 | 73 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1153 | 1570 | -417 | 73 | 815 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1464 | 2000 | -536 | 73 | 1040 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 911 | 1248 | -337 | 73 | 372 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1454 | 2000 | -546 | 73 | 1033 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1440 | 2000 | -560 | 72 | 1016 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1433 | 2000 | -567 | 72 | 1012 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1118 | 1570 | -452 | 71 | 787 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1115 | 1570 | -455 | 71 | 785 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1113 | 1570 | -457 | 71 | 784 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1112 | 1570 | -458 | 71 | 783 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1110 | 1570 | -460 | 71 | 782 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1106 | 1570 | -464 | 70 | 779 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1100 | 1570 | -470 | 70 | 774 | AC

## 1330
Detailed results
Generated at: | 05/06/2026 21:28:59
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3870
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1167 | 1248 | -82 | 93 | 477 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1167 | 1248 | -82 | 93 | 477 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1163 | 1248 | -85 | 93 | 475 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1163 | 1248 | -85 | 93 | 475 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1159 | 1248 | -89 | 93 | 474 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1159 | 1248 | -89 | 93 | 474 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1691 | 1890 | -199 | 89 | -1170 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1691 | 1890 | -199 | 89 | -1170 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1691 | 1920 | -229 | 88 | 1203 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1691 | 1920 | -229 | 88 | 1203 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1723 | 2000 | -277 | 86 | 1224 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1708 | 2000 | -292 | 85 | 1214 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1327 | 1570 | -243 | 85 | 941 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1687 | 2000 | -313 | 84 | 1197 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1686 | 2000 | -314 | 84 | 1195 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1677 | 2000 | -323 | 84 | 1188 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1675 | 2000 | -325 | 84 | 1187 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1672 | 2000 | -328 | 84 | 1191 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1665 | 2000 | -335 | 83 | 1184 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1659 | 2000 | -341 | 83 | 1179 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1633 | 2000 | -367 | 82 | 1160 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1611 | 2000 | -389 | 81 | 1138 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1611 | 2000 | -389 | 81 | -1118 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1602 | 2000 | -398 | 80 | -1110 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1602 | 2000 | -398 | 80 | 1132 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1600 | 2000 | -400 | 80 | 1137 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1525 | 2000 | -475 | 76 | 1082 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1501 | 2000 | -499 | 75 | 1065 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1489 | 2000 | -511 | 74 | 1057 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1473 | 2000 | -527 | 74 | 1038 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 916 | 1248 | -332 | 73 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 916 | 1248 | -332 | 73 | 374 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1466 | 2000 | -534 | 73 | 1034 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 910 | 1248 | -338 | 73 | 372 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1113 | 1570 | -457 | 71 | 782 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1113 | 1570 | -457 | 71 | 782 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1102 | 1570 | -468 | 70 | 775 | AC

## 1430
Detailed results
Generated at: | 05/06/2026 21:28:59
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | False
Final step | Adjustment
TTC [MW]: | 3959.21
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1169 | 1248 | -79 | 94 | 478 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1169 | 1248 | -79 | 94 | 478 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1166 | 1248 | -82 | 93 | 476 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1166 | 1248 | -82 | 93 | 476 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1162 | 1248 | -86 | 93 | 475 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1162 | 1248 | -86 | 93 | 475 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1712 | 1890 | -178 | 91 | -1184 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1712 | 1890 | -178 | 91 | -1184 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1712 | 1920 | -208 | 89 | 1218 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1712 | 1920 | -208 | 89 | 1218 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1751 | 2000 | -249 | 88 | 1243 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1366 | 1570 | -204 | 87 | 975 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1734 | 2000 | -266 | 87 | 1232 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1720 | 2000 | -280 | 86 | 1219 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1719 | 2000 | -281 | 86 | 1219 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1709 | 2000 | -291 | 85 | 1211 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1707 | 2000 | -293 | 85 | 1210 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1705 | 2000 | -295 | 85 | 1214 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1697 | 2000 | -303 | 85 | 1207 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1690 | 2000 | -310 | 84 | 1201 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1663 | 2000 | -337 | 83 | 1181 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1650 | 2000 | -350 | 82 | 1165 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1650 | 2000 | -350 | 82 | -1145 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1641 | 2000 | -359 | 82 | -1136 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1641 | 2000 | -359 | 82 | 1159 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1629 | 2000 | -371 | 81 | 1158 | AC
RO_CO_00019 | N-1 OHL 400 kV Gura Ialomitei - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1554 | 2000 | -446 | 78 | 1103 | AC
RO_CO_00018 | N-1 OHL 400 kV Cernavoda - Pelicanu | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1529 | 2000 | -471 | 76 | 1085 | AC
RO_CO_00037 | N-1 OHL 400 kV Pelicanu - Bucuresti Sud | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1520 | 2000 | -480 | 76 | 1079 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1499 | 2000 | -501 | 75 | 1057 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1492 | 2000 | -508 | 75 | 1053 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 918 | 1248 | -331 | 73 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 918 | 1248 | -331 | 73 | 374 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 912 | 1248 | -337 | 73 | 372 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1136 | 1570 | -434 | 72 | 808 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1136 | 1570 | -434 | 72 | 808 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1127 | 1570 | -443 | 72 | 801 | AC

## 1530
Detailed results
Generated at: | 05/06/2026 21:28:59
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3638.77
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1570 | -208 | 87 | 972 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1360 | 1570 | -210 | 87 | 970 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1360 | 1570 | -210 | 87 | 970 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1067 | 1248 | -181 | 85 | 436 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1067 | 1248 | -181 | 85 | 436 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1064 | 1248 | -184 | 85 | 435 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1064 | 1248 | -184 | 85 | 435 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1060 | 1248 | -188 | 85 | 433 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1060 | 1248 | -188 | 85 | 433 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1328 | 1570 | -242 | 85 | 946 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1304 | 1570 | -266 | 83 | 929 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1304 | 1570 | -266 | 83 | 929 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1281 | 1570 | -289 | 82 | 912 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1276 | 1570 | -294 | 81 | 909 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1273 | 1570 | -297 | 81 | 907 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1622 | 2000 | -378 | 81 | 1153 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1272 | 1570 | -298 | 81 | 905 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1265 | 1570 | -305 | 81 | 900 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1258 | 1570 | -312 | 80 | 895 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1256 | 1570 | -314 | 80 | 894 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1599 | 2000 | -401 | 80 | 1134 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1251 | 1570 | -319 | 80 | 890 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1585 | 2000 | -415 | 79 | 1126 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1584 | 2000 | -416 | 79 | 1127 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1519 | 2000 | -481 | 76 | 1080 | AC
Base case | Base case | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1492 | 2000 | -508 | 75 | 1061 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 922 | 1248 | -327 | 74 | 376 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 922 | 1248 | -327 | 74 | 376 | AC
RO_CO_00041 | N-1 OHL 400 kV Medgidia Sud - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1474 | 2000 | -526 | 74 | 1045 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 916 | 1248 | -332 | 73 | 374 | AC
RO_CO_00036 | N-1 OHL 400 kV Medgidia Sud - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1467 | 2000 | -533 | 73 | 1046 | AC
RO_CO_00010 | N-1 OHL 400 kV Isaccea - Stupina | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1466 | 2000 | -534 | 73 | 1040 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1461 | 2000 | -539 | 73 | 1040 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1432 | 2000 | -568 | 72 | 1020 | AC

## 1630
Detailed results
Generated at: | 05/06/2026 21:28:59
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3570.42
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1570 | -202 | 87 | 975 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1570 | -202 | 87 | 975 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1570 | -205 | 87 | 974 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1337 | 1570 | -233 | 85 | 952 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1057 | 1248 | -191 | 85 | 432 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1057 | 1248 | -191 | 85 | 432 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1054 | 1248 | -194 | 84 | 431 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1054 | 1248 | -194 | 84 | 431 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1050 | 1248 | -198 | 84 | 429 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1050 | 1248 | -198 | 84 | 429 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1317 | 1570 | -253 | 84 | 938 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1317 | 1570 | -253 | 84 | 938 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1306 | 1570 | -264 | 83 | 930 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1292 | 1570 | -278 | 82 | 919 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1288 | 1570 | -282 | 82 | 917 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1282 | 1570 | -288 | 82 | 912 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1276 | 1570 | -294 | 81 | 908 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1267 | 1570 | -303 | 81 | 901 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1265 | 1570 | -305 | 81 | 899 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1259 | 1570 | -311 | 80 | 895 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1501 | 2000 | -499 | 75 | 1065 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1474 | 2000 | -526 | 74 | 1043 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 918 | 1248 | -330 | 74 | 375 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 918 | 1248 | -330 | 74 | 375 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1465 | 2000 | -535 | 73 | 1040 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1464 | 2000 | -536 | 73 | 1037 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 912 | 1248 | -336 | 73 | 372 | AC

## 1730
Detailed results
Generated at: | 05/06/2026 21:28:59
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3525
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1456 | 1570 | -114 | 93 | 1041 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1131 | 1248 | -118 | 91 | 460 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1131 | 1248 | -118 | 91 | 460 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1128 | 1248 | -121 | 90 | 459 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1128 | 1248 | -121 | 90 | 459 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 649 | 721 | -72 | 90 | 457 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 649 | 721 | -72 | 90 | 457 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1521 | 1890 | -369 | 80 | -1058 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1521 | 1890 | -369 | 80 | -1058 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1521 | 1920 | -399 | 79 | 1085 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1521 | 1920 | -399 | 79 | 1085 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1216 | 1570 | -354 | 77 | 870 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1200 | 1570 | -370 | 76 | 859 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1200 | 1570 | -370 | 76 | 859 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1174 | 1570 | -396 | 75 | 840 | AC
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1480 | 2000 | -520 | 74 | 1050 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 920 | 1248 | -328 | 74 | 373 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 920 | 1248 | -328 | 74 | 373 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 528 | 721 | -193 | 73 | 370 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1149 | 1570 | -421 | 73 | 823 | AC
RO_CO_00017 | N-1 OHL 400 kV Constanta Nord- Cernavoda | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1454 | 2000 | -546 | 73 | 1033 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1141 | 1570 | -429 | 73 | 817 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1138 | 1570 | -432 | 73 | 815 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1136 | 1570 | -434 | 72 | 814 | AC
RO_CO_00012 | N-1 OHL 400 kV Isaccea - Tulcea Vest | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1445 | 2000 | -555 | 72 | 1023 | AC
RO_CO_00015 | N-1 OHL 400 kV Tulcea Vest - Tariverde | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 RCERN41 1 | 1441 | 2000 | -559 | 72 | 1021 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1129 | 1570 | -441 | 72 | 809 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1125 | 1570 | -445 | 72 | 806 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1119 | 1570 | -451 | 71 | 801 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1108 | 1570 | -462 | 71 | 794 | AC

## 1830
Detailed results
Generated at: | 05/06/2026 21:28:59
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3482.26
Loading threshold | 0.7
Limiting CNEC | N-1 TRA 400/220 kV AT2 Portile de Fier/[RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1152 | 1248 | -97 | 92 | 469 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1152 | 1248 | -97 | 92 | 469 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1149 | 1248 | -100 | 92 | 467 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1149 | 1248 | -100 | 92 | 467 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1144 | 1248 | -104 | 92 | 466 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1144 | 1248 | -104 | 92 | 466 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1434 | 1570 | -136 | 91 | 1025 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1546 | 1890 | -344 | 82 | -1076 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1546 | 1890 | -344 | 82 | -1076 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1546 | 1920 | -374 | 81 | 1104 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1546 | 1920 | -374 | 81 | 1104 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1188 | 1570 | -382 | 76 | 850 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1182 | 1570 | -388 | 75 | 846 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1182 | 1570 | -388 | 75 | 846 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 914 | 1248 | -334 | 73 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 914 | 1248 | -334 | 73 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1148 | 1570 | -422 | 73 | 821 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 525 | 721 | -196 | 73 | 368 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1139 | 1570 | -431 | 73 | 816 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1124 | 1570 | -446 | 72 | 805 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1119 | 1570 | -451 | 71 | 802 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1113 | 1570 | -457 | 71 | 797 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1113 | 1570 | -457 | 71 | 797 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1107 | 1570 | -463 | 70 | 793 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1100 | 1570 | -470 | 70 | 788 | AC

## 1930
Detailed results
Generated at: | 05/06/2026 21:29:00
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3184.43
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1569 | 1570 | -1 | 100 | 1123 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1568 | 1570 | -2 | 100 | 1122 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1568 | 1570 | -2 | 100 | 1122 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1560 | 1570 | -10 | 99 | 1116 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1556 | 1570 | -14 | 99 | 1113 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1556 | 1570 | -14 | 99 | 1113 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1539 | 1570 | -31 | 98 | 1101 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1509 | 1570 | -61 | 96 | 1080 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1570 | -65 | 96 | 1077 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1570 | -76 | 95 | 1069 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1493 | 1570 | -77 | 95 | 1068 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1473 | 1570 | -97 | 94 | 1054 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1471 | 1570 | -99 | 94 | 1053 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1464 | 1570 | -106 | 93 | 1048 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1113 | 1248 | -136 | 89 | 454 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1113 | 1248 | -136 | 89 | 454 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1110 | 1248 | -139 | 89 | 453 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1110 | 1248 | -139 | 89 | 453 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1106 | 1248 | -143 | 89 | 451 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1106 | 1248 | -143 | 89 | 451 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 911 | 1248 | -337 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 911 | 1248 | -337 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 905 | 1248 | -343 | 72 | 369 | AC

## 2030
Detailed results
Generated at: | 05/06/2026 21:29:00
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3135
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1572 | 1570 | 2 | 100 | 1127 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1571 | 1570 | 1 | 100 | 1126 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1571 | 1570 | 1 | 100 | 1126 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | 1124 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1555 | 1570 | -15 | 99 | 1115 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1555 | 1570 | -15 | 99 | 1115 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1540 | 1570 | -30 | 98 | 1104 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1511 | 1570 | -59 | 96 | 1083 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1507 | 1570 | -63 | 96 | 1080 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1570 | -76 | 95 | 1071 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1570 | -76 | 95 | 1071 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1473 | 1570 | -97 | 94 | 1056 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1471 | 1570 | -99 | 94 | 1055 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1463 | 1570 | -107 | 93 | 1049 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1111 | 1248 | -137 | 89 | 453 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1111 | 1248 | -137 | 89 | 453 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1108 | 1248 | -140 | 89 | 452 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1108 | 1248 | -140 | 89 | 452 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1104 | 1248 | -144 | 88 | 450 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 1104 | 1248 | -144 | 88 | 450 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 913 | 1248 | -336 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 913 | 1248 | -336 | 73 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 524 | 721 | -197 | 73 | 368 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] OHL 220 kV Alba Iulia-Mintia | RAIUL22 RMINT12 1 | 628 | 890 | -262 | 71 | 254 | AC

## 2130
Detailed results
Generated at: | 05/06/2026 21:29:00
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3194.93
Loading threshold | 0.7
Limiting CNEC | N-1 OHL 400 kV Sofia Zapad -Nis/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | 1119 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | 1119 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1567 | 1570 | -3 | 100 | 1116 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1559 | 1570 | -11 | 99 | 1114 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1555 | 1570 | -15 | 99 | 1111 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1555 | 1570 | -15 | 99 | 1111 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1540 | 1570 | -30 | 98 | 1097 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1509 | 1570 | -61 | 96 | 1076 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1499 | 1570 | -71 | 95 | 1070 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1492 | 1570 | -78 | 95 | 1065 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1492 | 1570 | -78 | 95 | 1066 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1470 | 1570 | -100 | 94 | 1051 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1469 | 1570 | -101 | 94 | 1050 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1462 | 1570 | -108 | 93 | 1044 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1126 | 1248 | -123 | 90 | 456 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1126 | 1248 | -123 | 90 | 456 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1123 | 1248 | -126 | 90 | 454 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1123 | 1248 | -126 | 90 | 454 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 646 | 721 | -75 | 90 | 453 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 646 | 721 | -75 | 90 | 453 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 533 | 721 | -188 | 74 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 533 | 721 | -188 | 74 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 530 | 721 | -191 | 74 | 368 | AC

## 2230
Detailed results
Generated at: | 05/06/2026 21:29:00
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3453.14
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1575 | 1570 | 5 | 100 | 1118 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1575 | 1570 | 5 | 100 | 1118 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1571 | 1570 | 1 | 100 | 1114 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1571 | 1570 | 1 | 100 | 1114 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1555 | 1570 | -15 | 99 | 1100 | AC no reactive limits
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1550 | 1570 | -20 | 99 | 1100 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1549 | 1570 | -21 | 99 | 1100 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1511 | 1570 | -59 | 96 | 1071 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1496 | 1570 | -74 | 95 | 1062 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1495 | 1570 | -75 | 95 | 1061 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1491 | 1570 | -79 | 95 | 1058 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1478 | 1570 | -92 | 94 | 1049 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1475 | 1570 | -95 | 94 | 1047 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1461 | 1570 | -109 | 93 | 1036 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1113 | 1248 | -136 | 89 | 450 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1113 | 1248 | -136 | 89 | 450 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 1110 | 1248 | -139 | 89 | 449 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 1110 | 1248 | -139 | 89 | 449 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 638 | 721 | -83 | 89 | 447 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 638 | 721 | -83 | 89 | 447 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 534 | 721 | -187 | 74 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 534 | 721 | -187 | 74 | 371 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 530 | 721 | -191 | 74 | 369 | AC

## 2330
Detailed results
Generated at: | 05/06/2026 21:29:00
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | South-Romania Exporting
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3732.66
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1512 | 1570 | -58 | 96 | 1051 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1512 | 1570 | -58 | 96 | 1051 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1470 | 1570 | -100 | 94 | 1015 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1470 | 1570 | -100 | 94 | 1015 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1459 | 1570 | -111 | 93 | 1010 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 665 | 721 | -56 | 92 | 462 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 665 | 721 | -56 | 92 | 462 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 664 | 721 | -57 | 92 | 461 | AC
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 664 | 721 | -57 | 92 | 461 | AC
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 661 | 721 | -60 | 92 | 459 | AC
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 661 | 721 | -60 | 92 | 459 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1412 | 1570 | -158 | 90 | 979 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1408 | 1570 | -162 | 90 | 975 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1400 | 1570 | -170 | 89 | 969 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1398 | 1570 | -172 | 89 | 968 | AC
Base case | Base case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1397 | 1570 | -173 | 89 | 968 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1397 | 1570 | -173 | 89 | 968 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1393 | 1570 | -177 | 89 | 965 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1383 | 1570 | -187 | 88 | 960 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1374 | 1570 | -196 | 88 | 953 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 RPDF222 2 | 540 | 721 | -181 | 75 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 RPDF222 1 | 540 | 721 | -181 | 75 | 370 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 RPDF212 3 | 537 | 721 | -184 | 74 | 367 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1371 | 1890 | -519 | 73 | -957 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1371 | 1890 | -519 | 73 | -957 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1433 | 2000 | -567 | 72 | 1015 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [DIR] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1433 | 2000 | -567 | 72 | -999 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1371 | 1920 | -549 | 71 | 979 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1371 | 1920 | -549 | 71 | 979 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1426 | 2000 | -574 | 71 | 1010 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [DIR] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1426 | 2000 | -574 | 71 | -992 | AC