## 0030
Detailed results
Generated at: | 05/06/2026 22:00:41
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3502.49
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1586 | 1570 | 16 | 101 | -1141 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1586 | 1570 | 16 | 101 | -1141 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1534 | 1570 | -36 | 98 | -1100 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1534 | 1570 | -36 | 98 | -1100 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1517 | 1570 | -53 | 97 | -1089 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1504 | 1570 | -66 | 96 | -1080 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 957 | 999 | -42 | 96 | 353 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1504 | 1570 | -66 | 96 | -1080 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1497 | 1570 | -73 | 95 | -1076 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | -1062 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 937 | 999 | -63 | 94 | 360 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1462 | 1570 | -108 | 93 | -1052 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 928 | 999 | -71 | 93 | 358 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 926 | 999 | -73 | 93 | 350 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1453 | 1570 | -117 | 93 | -1045 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1405 | 1570 | -165 | 90 | -1010 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1570 | -166 | 89 | -1007 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1570 | -175 | 89 | -1006 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 780 | 999 | -219 | 78 | 288 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1396 | 1890 | -494 | 74 | 985 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1396 | 1890 | -494 | 74 | 985 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1396 | 1920 | -524 | 73 | -963 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1396 | 1920 | -524 | 73 | -963 | AC

## 0130
Detailed results
Generated at: | 05/06/2026 22:00:41
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3482.95
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1586 | 1570 | 16 | 101 | -1143 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1586 | 1570 | 16 | 101 | -1143 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1570 | -40 | 97 | -1099 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1570 | -40 | 97 | -1099 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1515 | 1570 | -55 | 97 | -1090 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1504 | 1570 | -66 | 96 | -1082 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1504 | 1570 | -66 | 96 | -1082 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1497 | 1570 | -73 | 95 | -1078 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 944 | 999 | -55 | 94 | 351 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | -1064 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1462 | 1570 | -108 | 93 | -1053 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 924 | 999 | -75 | 93 | 355 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1452 | 1570 | -118 | 92 | -1047 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 917 | 999 | -82 | 92 | 348 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 916 | 999 | -83 | 92 | 353 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1407 | 1570 | -163 | 90 | -1013 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1402 | 1570 | -168 | 89 | -1007 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1570 | -175 | 89 | -1007 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 769 | 999 | -230 | 77 | 285 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1393 | 1890 | -497 | 74 | 983 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1393 | 1890 | -497 | 74 | 983 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1393 | 1920 | -527 | 73 | -961 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1393 | 1920 | -527 | 73 | -961 | AC

## 0230
Detailed results
Generated at: | 05/06/2026 22:00:41
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3659.84
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1587 | 1570 | 17 | 101 | -1145 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1587 | 1570 | 17 | 101 | -1145 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1529 | 1570 | -41 | 97 | -1099 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1529 | 1570 | -41 | 97 | -1099 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1509 | 1570 | -61 | 96 | -1086 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1496 | 1570 | -74 | 95 | -1077 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1496 | 1570 | -74 | 95 | -1076 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1489 | 1570 | -81 | 95 | -1073 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1469 | 1570 | -101 | 94 | -1059 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 928 | 999 | -72 | 93 | 350 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1456 | 1570 | -114 | 93 | -1050 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 925 | 999 | -74 | 93 | 356 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1444 | 1570 | -126 | 92 | -1041 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 917 | 999 | -82 | 92 | 354 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 903 | 999 | -96 | 90 | 345 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1403 | 1570 | -167 | 89 | -1011 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1397 | 1570 | -173 | 89 | -1004 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1570 | -182 | 88 | -1002 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1481 | 1890 | -409 | 78 | 1046 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1481 | 1890 | -409 | 78 | 1046 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1481 | 1920 | -439 | 77 | -1021 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1481 | 1920 | -439 | 77 | -1021 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 764 | 999 | -235 | 76 | 285 | AC

## 0330
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3603.8
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1588 | 1570 | 18 | 101 | -1142 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1588 | 1570 | 18 | 101 | -1142 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1002 | 999 | 3 | 100 | 371 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1554 | 1570 | -16 | 99 | -1113 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1554 | 1570 | -16 | 99 | -1113 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 976 | 999 | -23 | 98 | 369 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1529 | 1570 | -41 | 97 | -1096 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1518 | 1570 | -52 | 97 | -1088 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1515 | 1570 | -55 | 97 | -1086 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1508 | 1570 | -62 | 96 | -1082 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 951 | 999 | -48 | 95 | 366 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1484 | 1570 | -86 | 94 | -1066 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 940 | 999 | -59 | 94 | 363 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1467 | 1570 | -103 | 93 | -1054 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1463 | 1570 | -107 | 93 | -1051 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1421 | 1570 | -149 | 91 | -1021 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1417 | 1570 | -153 | 90 | -1015 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1403 | 1570 | -167 | 89 | -1011 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 814 | 999 | -186 | 81 | 300 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1248 | 1600 | -352 | 78 | -834 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1364 | 1890 | -526 | 72 | 963 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1364 | 1890 | -526 | 72 | 963 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1364 | 1920 | -556 | 71 | -941 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1364 | 1920 | -556 | 71 | -941 | AC

## 0430
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3784.45
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1588 | 1570 | 18 | 101 | -1145 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1588 | 1570 | 18 | 101 | -1145 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1570 | -40 | 97 | -1099 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1570 | -40 | 97 | -1099 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1506 | 1570 | -64 | 96 | -1084 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1493 | 1570 | -77 | 95 | -1074 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1492 | 1570 | -78 | 95 | -1073 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1487 | 1570 | -83 | 95 | -1071 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 940 | 999 | -60 | 94 | 362 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1570 | -104 | 93 | -1056 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 931 | 999 | -68 | 93 | 360 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 930 | 999 | -69 | 93 | 350 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1453 | 1570 | -117 | 93 | -1047 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1444 | 1570 | -126 | 92 | -1041 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 904 | 999 | -95 | 90 | 346 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1396 | 1570 | -174 | 89 | -1006 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1570 | -178 | 89 | -1000 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1383 | 1570 | -187 | 88 | -998 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1519 | 1890 | -371 | 80 | 1072 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1519 | 1890 | -371 | 80 | 1072 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1519 | 1920 | -401 | 79 | -1046 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1519 | 1920 | -401 | 79 | -1046 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 770 | 999 | -229 | 77 | 287 | AC

## 0530
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3852.43
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Rosiori-Mukacevo/[RO-RO] [DIR] TRA 400/220 kV AT2 Iernut
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1021 | 999 | 22 | 102 | 389 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1002 | 999 | 3 | 100 | 384 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 955 | 999 | -44 | 96 | 367 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1498 | 1570 | -72 | 95 | -1082 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1498 | 1570 | -72 | 95 | -1082 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 943 | 999 | -56 | 94 | 364 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1434 | 1570 | -136 | 91 | -1032 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1434 | 1570 | -136 | 91 | -1032 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1420 | 1570 | -150 | 90 | -1023 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1406 | 1570 | -164 | 90 | -1013 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1396 | 1570 | -174 | 89 | -1006 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1388 | 1570 | -182 | 88 | -1001 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1373 | 1570 | -197 | 87 | -991 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1360 | 1570 | -210 | 87 | -981 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1341 | 1570 | -229 | 85 | -968 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1570 | 1890 | -320 | 83 | 1108 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1570 | 1890 | -320 | 83 | 1108 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1300 | 1570 | -270 | 83 | -935 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1291 | 1570 | -279 | 82 | -933 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1285 | 1570 | -285 | 82 | -926 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1570 | 1920 | -350 | 82 | -1080 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1570 | 1920 | -350 | 82 | -1080 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 801 | 999 | -198 | 80 | 296 | AC

## 0630
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3862.69
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1570 | -85 | 95 | -1074 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1570 | -85 | 95 | -1074 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 915 | 999 | -84 | 92 | 354 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 909 | 999 | -90 | 91 | 349 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1570 | -166 | 89 | -1011 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1404 | 1570 | -166 | 89 | -1011 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1400 | 1570 | -170 | 89 | -1011 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 888 | 999 | -111 | 89 | 342 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1390 | 1570 | -180 | 89 | -1003 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1378 | 1570 | -192 | 88 | -996 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1375 | 1570 | -195 | 88 | -993 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1364 | 1570 | -206 | 87 | -985 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1641 | 1890 | -249 | 87 | 1159 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1641 | 1890 | -249 | 87 | 1159 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 863 | 999 | -136 | 86 | 334 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1354 | 1570 | -216 | 86 | -978 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1641 | 1920 | -279 | 85 | -1128 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1641 | 1920 | -279 | 85 | -1128 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1323 | 1570 | -247 | 84 | -956 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1283 | 1570 | -287 | 82 | -928 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1282 | 1570 | -288 | 82 | -923 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1234 | 1570 | -336 | 79 | -891 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1523 | 2000 | -477 | 76 | 1072 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1523 | 2000 | -477 | 76 | -1054 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1509 | 2000 | -491 | 75 | 1061 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1509 | 2000 | -491 | 75 | -1041 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 708 | 999 | -291 | 71 | 263 | AC

## 0730
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3492
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1884 | 1890 | -6 | 100 | 1327 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1884 | 1890 | -6 | 100 | 1327 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1884 | 1920 | -36 | 98 | -1287 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1884 | 1920 | -36 | 98 | -1287 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1650 | 2000 | -350 | 82 | 1160 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1650 | 2000 | -350 | 82 | -1140 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1634 | 2000 | -366 | 82 | 1148 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1634 | 2000 | -366 | 82 | -1125 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 722 | 999 | -277 | 72 | 273 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 716 | 999 | -283 | 72 | 274 | AC

## 0830
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3387
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 24 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 53 | 114 |  | 114 | 0 | FALSE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 8 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 7 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 30 |  | 30 | 0 | FALSE | FALSE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 57 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 10 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 16 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 10 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 21 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 9 | 3 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 17 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 8 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 17 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 16 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 18 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 6 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 26 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 20 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 13 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 27 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 27 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 27 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 27 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 27 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 15 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 16 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 23 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 23 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 27 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 11 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 9 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1884 | 1890 | -6 | 100 | 1328 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1884 | 1890 | -6 | 100 | 1328 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1884 | 1920 | -36 | 98 | -1288 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1884 | 1920 | -36 | 98 | -1288 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1668 | 2000 | -332 | 83 | 1172 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1668 | 2000 | -332 | 83 | -1151 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1653 | 2000 | -347 | 83 | -1137 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1653 | 2000 | -347 | 83 | 1161 | AC

## 0930
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3559
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1884 | 1890 | -6 | 100 | 1328 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1884 | 1890 | -6 | 100 | 1328 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1884 | 1920 | -36 | 98 | -1288 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1884 | 1920 | -36 | 98 | -1288 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1651 | 2000 | -349 | 83 | -1143 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1651 | 2000 | -349 | 83 | 1164 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1636 | 2000 | -364 | 82 | -1129 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1636 | 2000 | -364 | 82 | 1153 | AC

## 1030
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | False
Final step | Adjustment
TTC [MW]: | 3947.38
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1832 | 1890 | -58 | 97 | 1292 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1832 | 1890 | -58 | 97 | 1292 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1832 | 1920 | -88 | 95 | -1253 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1832 | 1920 | -88 | 95 | -1253 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1435 | 1570 | -135 | 91 | -1004 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1435 | 1570 | -135 | 91 | -1004 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1418 | 1570 | -152 | 90 | -999 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1377 | 1570 | -193 | 88 | -964 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1367 | 1570 | -203 | 87 | -957 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1366 | 1570 | -204 | 87 | -956 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1570 | -205 | 87 | -956 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1356 | 1570 | -214 | 86 | -949 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1570 | -218 | 86 | -946 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1699 | 2000 | -301 | 85 | 1200 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1699 | 2000 | -301 | 85 | -1178 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1684 | 2000 | -316 | 84 | -1164 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1684 | 2000 | -316 | 84 | 1189 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1315 | 1570 | -255 | 84 | -920 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1295 | 1570 | -275 | 82 | -906 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1284 | 1570 | -286 | 82 | -898 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1268 | 1570 | -302 | 81 | -887 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 747 | 999 | -252 | 75 | 285 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 742 | 999 | -257 | 74 | 286 | AC

## 1130
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3479.05
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1573 | 1570 | 3 | 100 | -1105 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1573 | 1570 | 3 | 100 | -1105 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1552 | 1570 | -18 | 99 | -1090 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1551 | 1570 | -19 | 99 | -1091 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1551 | 1570 | -19 | 99 | -1091 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1550 | 1570 | -20 | 99 | -1089 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1548 | 1570 | -22 | 99 | -1087 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1542 | 1570 | -28 | 98 | -1083 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1527 | 1570 | -43 | 97 | -1073 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1517 | 1570 | -53 | 97 | -1066 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1512 | 1570 | -58 | 96 | -1062 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1493 | 1570 | -77 | 95 | -1049 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1468 | 1570 | -102 | 93 | -1031 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1455 | 1570 | -115 | 93 | -1022 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 805 | 999 | -194 | 81 | 310 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 801 | 999 | -198 | 80 | 305 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 756 | 999 | -243 | 76 | 293 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 748 | 999 | -252 | 75 | 290 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1329 | 1890 | -561 | 70 | 936 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1329 | 1890 | -561 | 70 | 936 | AC

## 1230
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3353
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 341 |  | 389 | 0 | TRUE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 6 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 13 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 8 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 14 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 9 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 18 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 8 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 14 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 14 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 13 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 15 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 5 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 8 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 6 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 15 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 15 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 22 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 22 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 13 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 4 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 7 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 3 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1569 | 1570 | -1 | 100 | -1110 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1569 | 1570 | -1 | 100 | -1110 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1563 | 1570 | -7 | 100 | -1106 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1559 | 1570 | -11 | 99 | -1103 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1555 | 1570 | -15 | 99 | -1100 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1555 | 1570 | -15 | 99 | -1100 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1555 | 1570 | -15 | 99 | -1100 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1550 | 1570 | -20 | 99 | -1096 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1531 | 1570 | -39 | 98 | -1082 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1528 | 1570 | -42 | 97 | -1079 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1521 | 1570 | -49 | 97 | -1074 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1493 | 1570 | -77 | 95 | -1055 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1466 | 1570 | -104 | 93 | -1032 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1455 | 1570 | -115 | 93 | -1029 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 874 | 999 | -125 | 87 | 336 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 868 | 999 | -131 | 87 | 331 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 860 | 999 | -139 | 86 | 329 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 853 | 999 | -146 | 85 | 328 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1561 | 1920 | -359 | 81 | 1109 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1415 | 1920 | -505 | 74 | 1006 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1128 | 1600 | -472 | 71 | -764 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 703 | 999 | -296 | 70 | 254 | AC

## 1330
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3203
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 347 |  | 389 | 0 | TRUE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 6 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 4 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 13 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 9 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 14 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 9 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 18 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 8 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 13 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 15 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 5 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 8 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 6 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 8 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 15 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 15 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 22 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 23 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 14 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 4 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 7 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 3 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 5 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1565 | 1570 | -5 | 100 | -1107 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1561 | 1570 | -9 | 99 | -1104 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1561 | 1570 | -9 | 99 | -1104 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1560 | 1570 | -10 | 99 | -1103 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1559 | 1570 | -11 | 99 | -1102 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1559 | 1570 | -11 | 99 | -1102 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1553 | 1570 | -17 | 99 | -1098 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1551 | 1570 | -19 | 99 | -1095 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1531 | 1570 | -39 | 98 | -1081 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1570 | -40 | 97 | -1079 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1517 | 1570 | -53 | 97 | -1071 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1492 | 1570 | -78 | 95 | -1053 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1472 | 1570 | -98 | 94 | -1035 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1461 | 1570 | -109 | 93 | -1032 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 899 | 999 | -100 | 90 | 342 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 895 | 999 | -104 | 90 | 342 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 895 | 999 | -104 | 90 | 342 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 886 | 999 | -113 | 89 | 337 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1670 | 1920 | -250 | 87 | 1187 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1294 | 1600 | -306 | 81 | -870 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1507 | 1920 | -413 | 78 | 1071 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 729 | 999 | -270 | 73 | 265 | AC

## 1430
Detailed results
Generated at: | 05/06/2026 22:00:42
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3283.01
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1579 | 1570 | 9 | 101 | -1121 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1579 | 1570 | 9 | 101 | -1121 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | -1115 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | -1114 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | -1114 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1568 | 1570 | -2 | 100 | -1112 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1561 | 1570 | -9 | 99 | -1108 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1559 | 1570 | -11 | 99 | -1105 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1540 | 1570 | -30 | 98 | -1091 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1538 | 1570 | -32 | 98 | -1091 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1526 | 1570 | -44 | 97 | -1081 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1508 | 1570 | -62 | 96 | -1069 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1495 | 1570 | -75 | 95 | -1060 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1475 | 1570 | -95 | 94 | -1043 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 916 | 999 | -83 | 92 | 352 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 908 | 999 | -91 | 91 | 346 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 898 | 999 | -102 | 90 | 343 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 890 | 999 | -109 | 89 | 341 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1249 | 1600 | -351 | 78 | -844 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 727 | 999 | -272 | 73 | 266 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1373 | 1920 | -547 | 72 | 975 | AC

## 1530
Detailed results
Generated at: | 05/06/2026 22:00:43
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3821.37
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1710 | 1890 | -180 | 90 | 1206 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1710 | 1890 | -180 | 90 | 1206 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1710 | 1920 | -210 | 89 | -1172 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1710 | 1920 | -210 | 89 | -1172 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1379 | 1570 | -191 | 88 | -979 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1299 | 1570 | -271 | 83 | -916 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1299 | 1570 | -271 | 83 | -916 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1631 | 2000 | -369 | 82 | 1152 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1631 | 2000 | -369 | 82 | -1132 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1616 | 2000 | -384 | 81 | 1141 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1616 | 2000 | -384 | 81 | -1118 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1260 | 1570 | -310 | 80 | -889 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1251 | 1570 | -319 | 80 | -882 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1248 | 1570 | -322 | 80 | -880 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 791 | 999 | -208 | 79 | 303 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 788 | 999 | -211 | 79 | 305 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1238 | 1570 | -332 | 79 | -872 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1233 | 1570 | -337 | 79 | -869 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1224 | 1570 | -346 | 78 | -862 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1204 | 1570 | -366 | 77 | -847 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1180 | 1570 | -390 | 75 | -829 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1173 | 1570 | -397 | 75 | -827 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1121 | 1570 | -449 | 71 | -787 | AC

## 1630
Detailed results
Generated at: | 05/06/2026 22:00:43
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | False
Final step | Adjustment
TTC [MW]: | 3968.58
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1865 | 1890 | -25 | 99 | 1315 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1865 | 1890 | -25 | 99 | 1315 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1865 | 1920 | -55 | 97 | -1276 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1865 | 1920 | -55 | 97 | -1276 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1707 | 2000 | -293 | 85 | -1181 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1707 | 2000 | -293 | 85 | 1202 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1692 | 2000 | -308 | 85 | -1165 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1692 | 2000 | -308 | 85 | 1190 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1309 | 1570 | -261 | 83 | -930 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 830 | 999 | -169 | 83 | 317 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 820 | 999 | -179 | 82 | 318 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1260 | 1570 | -310 | 80 | -889 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1260 | 1570 | -310 | 80 | -889 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1205 | 1570 | -365 | 77 | -850 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1193 | 1570 | -377 | 76 | -842 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1193 | 1570 | -377 | 76 | -841 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1185 | 1570 | -385 | 76 | -836 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1180 | 1570 | -390 | 75 | -831 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1172 | 1570 | -398 | 75 | -826 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1136 | 1570 | -434 | 72 | -799 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1121 | 1570 | -449 | 71 | -787 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1114 | 1570 | -456 | 71 | -785 | AC

## 1730
Detailed results
Generated at: | 05/06/2026 22:00:43
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3988
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00104 | TOP_CLOSE_400kV_Resita_Pancevo_c2 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 918 | 999 | -81 | 92 | 349 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1433 | 1570 | -137 | 91 | -1030 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1433 | 1570 | -137 | 91 | -1030 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 908 | 999 | -91 | 91 | 347 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 906 | 999 | -93 | 91 | 349 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1415 | 1570 | -155 | 90 | -1017 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1415 | 1570 | -155 | 90 | -1017 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1406 | 1570 | -164 | 90 | -1010 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1396 | 1570 | -174 | 89 | -1003 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1570 | -175 | 89 | -1002 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1570 | -178 | 89 | -1000 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1384 | 1570 | -186 | 88 | -994 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 877 | 999 | -122 | 88 | 334 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1362 | 1570 | -208 | 87 | -979 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1349 | 1570 | -221 | 86 | -969 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1339 | 1570 | -231 | 85 | -962 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 491 | 577 | -86 | 85 | 317 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1324 | 1570 | -246 | 84 | -951 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1586 | 1890 | -304 | 84 | 1118 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1586 | 1890 | -304 | 84 | 1118 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1586 | 1920 | -334 | 83 | -1090 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1586 | 1920 | -334 | 83 | -1090 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1286 | 1570 | -284 | 82 | -924 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1628 | 2000 | -372 | 81 | 1146 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1628 | 2000 | -372 | 81 | -1126 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1613 | 2000 | -387 | 81 | 1134 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1613 | 2000 | -387 | 81 | -1111 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 762 | 999 | -237 | 76 | 277 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1196 | 1600 | -404 | 75 | -808 | AC

## 1830
Detailed results
Generated at: | 05/06/2026 22:00:43
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | Reduction
TTC [MW]: | 3844
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 580 |  | 580 | 0 | TRUE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 117 |  | 389 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 52 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 2 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 7 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 4 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 4 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 56 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 16 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 26 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 16 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 33 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 13 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 26 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 13 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 26 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 24 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 28 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 9 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 28 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 21 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 15 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 15 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 9 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 10 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 22 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 15 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 26 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 11 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 11 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 8 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 92 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 24 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 997 | 999 | -2 | 100 | 375 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1545 | 1570 | -25 | 98 | -1107 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1545 | 1570 | -25 | 98 | -1107 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 982 | 999 | -17 | 98 | 371 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1522 | 1570 | -48 | 97 | -1090 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1519 | 1570 | -51 | 97 | -1088 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1516 | 1570 | -54 | 97 | -1086 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1570 | -65 | 96 | -1079 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1570 | -65 | 96 | -1077 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1570 | -65 | 96 | -1077 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1835 | 1920 | -85 | 96 | 1318 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1496 | 1570 | -74 | 95 | -1072 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | -1058 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1455 | 1570 | -115 | 93 | -1044 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 918 | 999 | -81 | 92 | 351 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1442 | 1570 | -128 | 92 | -1032 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 908 | 999 | -92 | 91 | 346 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1407 | 1570 | -163 | 90 | -1010 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1402 | 1570 | -168 | 89 | -1003 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1660 | 1920 | -260 | 86 | 1186 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1668 | 2000 | -332 | 83 | -1156 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1668 | 2000 | -332 | 83 | 1177 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1653 | 2000 | -347 | 83 | 1166 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1653 | 2000 | -347 | 83 | -1142 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 789 | 999 | -210 | 79 | 286 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1479 | 1890 | -411 | 78 | 1052 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1479 | 1890 | -411 | 78 | 1052 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1479 | 1920 | -441 | 77 | -1027 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1479 | 1920 | -441 | 77 | -1027 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 425 | 577 | -152 | 74 | 267 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1172 | 1600 | -428 | 73 | -789 | AC

## 1930
Detailed results
Generated at: | 05/06/2026 22:00:43
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3925.83
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1541 | 1570 | -29 | 98 | -1096 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1541 | 1570 | -29 | 98 | -1096 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1444 | 1570 | -126 | 92 | -1027 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1428 | 1570 | -142 | 91 | -1017 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1428 | 1570 | -142 | 91 | -1017 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1570 | -144 | 91 | -1013 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1570 | -144 | 91 | -1013 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1423 | 1570 | -147 | 91 | -1010 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1410 | 1570 | -160 | 90 | -1001 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1405 | 1570 | -165 | 89 | -997 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1630 | 1890 | -260 | 86 | 1159 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1630 | 1890 | -260 | 86 | 1159 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1630 | 1920 | -290 | 85 | -1129 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1630 | 1920 | -290 | 85 | -1129 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1328 | 1570 | -242 | 85 | -943 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1324 | 1570 | -246 | 84 | -939 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1323 | 1570 | -247 | 84 | -939 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1682 | 2000 | -318 | 84 | -1158 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1682 | 2000 | -318 | 84 | 1179 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1666 | 2000 | -334 | 83 | -1142 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1666 | 2000 | -334 | 83 | 1166 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1263 | 1570 | -307 | 80 | -899 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 790 | 999 | -209 | 79 | 301 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 779 | 999 | -220 | 78 | 301 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 732 | 999 | -267 | 73 | 280 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 692 | 960 | -268 | 72 | 280 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 703 | 999 | -296 | 70 | 270 | AC

## 2030
Detailed results
Generated at: | 05/06/2026 22:00:43
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3770.82
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1578 | 1570 | 8 | 100 | -1127 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1578 | 1570 | 8 | 100 | -1127 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1570 | -85 | 95 | -1060 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1468 | 1570 | -102 | 93 | -1048 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1467 | 1570 | -103 | 93 | -1047 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1463 | 1570 | -107 | 93 | -1045 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1458 | 1570 | -112 | 93 | -1043 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1458 | 1570 | -112 | 93 | -1043 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1452 | 1570 | -118 | 92 | -1036 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1570 | -122 | 92 | -1033 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1369 | 1570 | -201 | 87 | -976 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1366 | 1570 | -204 | 87 | -975 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1356 | 1570 | -214 | 86 | -968 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1302 | 1570 | -268 | 83 | -929 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1634 | 2000 | -366 | 82 | 1145 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1634 | 2000 | -366 | 82 | -1125 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1543 | 1890 | -347 | 82 | 1098 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1543 | 1890 | -347 | 82 | 1098 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1618 | 2000 | -382 | 81 | 1133 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1618 | 2000 | -382 | 81 | -1110 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1543 | 1920 | -377 | 80 | -1071 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1543 | 1920 | -377 | 80 | -1071 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 724 | 999 | -275 | 72 | 272 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 688 | 960 | -272 | 72 | 278 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 713 | 999 | -286 | 71 | 271 | AC

## 2130
Detailed results
Generated at: | 05/06/2026 22:00:43
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3571
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 216 |  | 580 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 51 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 55 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00131 | RO | RLOTR22 _generator | 0 | 170 |  |  | 0 | 170 |  | 170 | 0 | TRUE | FALSE
RO_RA_00132 | RO | RLOT212 _generator | 0 | 340 |  |  | 0 | 241 |  | 340 | 0 | TRUE | FALSE
RO_RA_00133 | RO | RBRDS25 _generator | 0 | 118 |  |  | 0 | 118 |  | 118 | 0 | TRUE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 14 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 23 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 30 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 12 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 24 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 12 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 24 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 22 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 25 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 8 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 28 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 21 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 15 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 30 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 14 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 7 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 7 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 22 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 15 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 27 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 7 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 11 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 10 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 8 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 23 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1566 | 1570 | -4 | 100 | -1130 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1566 | 1570 | -4 | 100 | -1130 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1477 | 1570 | -93 | 94 | -1066 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1464 | 1570 | -106 | 93 | -1056 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1463 | 1570 | -107 | 93 | -1056 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1456 | 1570 | -114 | 93 | -1051 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1453 | 1570 | -117 | 93 | -1049 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1441 | 1570 | -129 | 92 | -1040 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1441 | 1570 | -129 | 92 | -1040 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1440 | 1570 | -130 | 92 | -1040 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1375 | 1570 | -195 | 88 | -992 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1363 | 1570 | -207 | 87 | -982 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1353 | 1570 | -217 | 86 | -977 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 852 | 999 | -147 | 85 | 325 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 844 | 999 | -155 | 84 | 324 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1312 | 1570 | -258 | 84 | -947 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1483 | 1890 | -407 | 78 | 1055 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1483 | 1890 | -407 | 78 | 1055 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1483 | 1920 | -437 | 77 | -1030 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1483 | 1920 | -437 | 77 | -1030 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1533 | 2000 | -467 | 77 | -1058 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1533 | 2000 | -467 | 77 | 1075 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1518 | 2000 | -482 | 76 | 1064 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1518 | 2000 | -482 | 76 | -1044 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 707 | 999 | -292 | 71 | 270 | AC

## 2230
Detailed results
Generated at: | 05/06/2026 22:00:43
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3484.61
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1577 | 1570 | 7 | 100 | -1138 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1577 | 1570 | 7 | 100 | -1138 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1500 | 1570 | -70 | 96 | -1082 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1499 | 1570 | -71 | 95 | -1082 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1486 | 1570 | -84 | 95 | -1072 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1484 | 1570 | -86 | 95 | -1070 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1484 | 1570 | -86 | 95 | -1070 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1480 | 1570 | -90 | 94 | -1068 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1468 | 1570 | -102 | 94 | -1060 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1459 | 1570 | -111 | 93 | -1053 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1570 | -178 | 89 | -1005 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1392 | 1570 | -178 | 89 | -1004 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1379 | 1570 | -191 | 88 | -995 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1344 | 1570 | -226 | 86 | -970 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 851 | 999 | -148 | 85 | 325 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 840 | 999 | -159 | 84 | 324 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 825 | 999 | -174 | 83 | 315 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 801 | 999 | -199 | 80 | 308 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1403 | 1890 | -487 | 74 | 990 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1403 | 1890 | -487 | 74 | 990 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1403 | 1920 | -517 | 73 | -967 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1403 | 1920 | -517 | 73 | -967 | AC

## 2330
Detailed results
Generated at: | 05/06/2026 22:00:43
Business day: | 2026-06-07
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2948.2
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1588 | 1570 | 18 | 101 | -1150 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1588 | 1570 | 18 | 101 | -1150 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1553 | 1570 | -17 | 99 | -1123 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1543 | 1570 | -27 | 98 | -1113 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1543 | 1570 | -27 | 98 | -1113 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1542 | 1570 | -28 | 98 | -1115 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1538 | 1570 | -32 | 98 | -1112 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1534 | 1570 | -36 | 98 | -1110 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1512 | 1570 | -58 | 96 | -1094 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1496 | 1570 | -74 | 95 | -1083 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1480 | 1570 | -90 | 94 | -1071 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1570 | -122 | 92 | -1048 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1438 | 1570 | -132 | 92 | -1043 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1436 | 1570 | -134 | 91 | -1036 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 885 | 999 | -114 | 89 | 333 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 868 | 999 | -131 | 87 | 330 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 850 | 999 | -149 | 85 | 323 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 841 | 999 | -158 | 84 | 321 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 720 | 999 | -279 | 72 | 267 | AC