## 0030
Detailed results
Generated at: | 06/06/2026 22:47:31
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 00:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3316.21
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Rosiori-Mukacevo/[RO-RO] [DIR] TRA 400/220 kV AT2 Iernut
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1070 | 999 | 71 | 107 | 393 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1037 | 999 | 37 | 104 | 392 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 989 | 999 | -10 | 99 | 380 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1546 | 1570 | -24 | 98 | -1110 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1546 | 1570 | -24 | 98 | -1110 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 972 | 999 | -27 | 97 | 376 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1513 | 1570 | -57 | 96 | -1082 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1513 | 1570 | -57 | 96 | -1082 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1570 | -76 | 95 | -1069 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1493 | 1570 | -77 | 95 | -1067 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1484 | 1570 | -86 | 95 | -1061 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1474 | 1570 | -96 | 94 | -1056 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1453 | 1570 | -117 | 93 | -1041 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1451 | 1570 | -119 | 92 | -1041 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1435 | 1570 | -135 | 91 | -1029 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1391 | 1570 | -179 | 89 | -995 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1570 | -202 | 87 | -982 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1570 | -205 | 87 | -977 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 847 | 999 | -152 | 85 | 310 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1185 | 1600 | -415 | 74 | -794 | AC

## 0130
Detailed results
Generated at: | 06/06/2026 22:47:32
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 01:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3295.7
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1180 | 999 | 181 | 118 | 421 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1137 | 999 | 137 | 114 | 424 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1037 | 999 | 38 | 104 | 396 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1010 | 999 | 11 | 101 | 390 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1581 | 1570 | 11 | 101 | -1132 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1581 | 1570 | 11 | 101 | -1132 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1565 | 1570 | -5 | 100 | -1116 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1565 | 1570 | -5 | 100 | -1116 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1552 | 1570 | -18 | 99 | -1104 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1543 | 1570 | -27 | 98 | -1100 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1537 | 1570 | -33 | 98 | -1095 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1524 | 1570 | -46 | 97 | -1089 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1508 | 1570 | -62 | 96 | -1076 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1497 | 1570 | -73 | 95 | -1071 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1477 | 1570 | -93 | 94 | -1056 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1438 | 1570 | -132 | 92 | -1027 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 911 | 999 | -88 | 91 | 327 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1411 | 1570 | -159 | 90 | -1012 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1395 | 1570 | -175 | 89 | -996 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1328 | 1600 | -272 | 83 | -881 | AC

## 0230
Detailed results
Generated at: | 06/06/2026 22:47:32
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 02:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3196.55
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1256 | 999 | 257 | 126 | 436 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1198 | 999 | 199 | 120 | 443 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1091 | 999 | 92 | 109 | 409 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1045 | 999 | 46 | 105 | 402 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1580 | 1570 | 10 | 101 | -1122 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1580 | 1570 | 10 | 101 | -1122 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1576 | 1570 | 6 | 100 | -1124 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1576 | 1570 | 6 | 100 | -1124 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1573 | 1570 | 3 | 100 | -1111 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1557 | 1570 | -13 | 99 | -1104 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1552 | 1570 | -18 | 99 | -1100 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1537 | 1570 | -33 | 98 | -1092 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1570 | -40 | 97 | -1084 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 967 | 999 | -32 | 97 | 337 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1504 | 1570 | -66 | 96 | -1072 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1482 | 1570 | -88 | 94 | -1055 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1450 | 1570 | -120 | 92 | -1031 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1467 | 1600 | -133 | 92 | -961 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1417 | 1570 | -153 | 90 | -1014 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1407 | 1570 | -163 | 90 | -1001 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1533 | 2000 | -467 | 77 | -990 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1156 | 1600 | -444 | 72 | -735 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1355 | 1920 | -565 | 71 | 984 | AC

## 0330
Detailed results
Generated at: | 06/06/2026 22:47:32
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 03:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3317.88
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1261 | 999 | 262 | 126 | 440 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1203 | 999 | 204 | 120 | 446 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1105 | 999 | 106 | 111 | 414 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1056 | 999 | 57 | 106 | 407 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1586 | 1570 | 16 | 101 | -1130 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1586 | 1570 | 16 | 101 | -1130 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1584 | 1570 | 14 | 101 | -1125 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1584 | 1570 | 14 | 101 | -1125 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1576 | 1570 | 6 | 100 | -1112 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1559 | 1570 | -11 | 99 | -1105 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1554 | 1570 | -16 | 99 | -1100 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1539 | 1570 | -31 | 98 | -1090 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1539 | 1570 | -31 | 98 | -1093 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 975 | 999 | -24 | 98 | 340 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1507 | 1570 | -63 | 96 | -1073 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1484 | 1570 | -86 | 95 | -1056 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1451 | 1570 | -119 | 92 | -1031 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1460 | 1600 | -140 | 91 | -958 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1417 | 1570 | -153 | 90 | -1013 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1411 | 1570 | -159 | 90 | -1003 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1522 | 2000 | -478 | 76 | -986 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1155 | 1600 | -445 | 72 | -736 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1352 | 1920 | -568 | 70 | 982 | AC

## 0430
Detailed results
Generated at: | 06/06/2026 22:47:32
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 04:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3284.89
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1231 | 999 | 232 | 123 | 460 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1215 | 999 | 216 | 122 | 459 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1064 | 999 | 65 | 106 | 406 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1042 | 999 | 43 | 104 | 400 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1583 | 1570 | 13 | 101 | -1127 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1583 | 1570 | 13 | 101 | -1127 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1577 | 1570 | 7 | 100 | -1126 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1577 | 1570 | 7 | 100 | -1126 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1563 | 1570 | -7 | 100 | -1109 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1557 | 1570 | -13 | 99 | -1107 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1553 | 1570 | -17 | 99 | -1102 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1539 | 1570 | -31 | 98 | -1095 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 974 | 999 | -25 | 98 | 352 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1539 | 1600 | -61 | 96 | -1023 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1510 | 1570 | -60 | 96 | -1074 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1505 | 1570 | -65 | 96 | -1075 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1481 | 1570 | -89 | 94 | -1057 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1455 | 1570 | -115 | 93 | -1036 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1422 | 1570 | -148 | 91 | -1017 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1419 | 1570 | -151 | 90 | -1011 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1605 | 2000 | -395 | 80 | -1058 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1192 | 1600 | -408 | 74 | -783 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1391 | 1920 | -529 | 72 | 1011 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1435 | 2000 | -565 | 72 | -935 | AC

## 0530
Detailed results
Generated at: | 06/06/2026 22:47:32
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 05:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 2393.26
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Resita-Pancevo c1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1081 | 999 | 82 | 108 | 410 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1077 | 999 | 78 | 108 | 411 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1579 | 1570 | 9 | 101 | -1133 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1530 | 1570 | -40 | 97 | -1091 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 906 | 999 | -93 | 91 | 344 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1430 | 1600 | -170 | 89 | -960 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 889 | 999 | -111 | 89 | 340 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 857 | 999 | -142 | 86 | 312 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1301 | 1570 | -269 | 83 | -918 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1299 | 1570 | -271 | 83 | -918 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1292 | 1570 | -278 | 82 | -911 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1277 | 1570 | -293 | 81 | -905 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1247 | 1570 | -323 | 79 | -886 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1243 | 1570 | -327 | 79 | -879 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1216 | 1570 | -354 | 77 | -862 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1202 | 1570 | -368 | 77 | -849 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-HU] [OPP] TIE 400 kV Nadab-Bekescsaba | RNADA_1 XBE_NA11 1 | 1493 | 2000 | -507 | 75 | -993 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1164 | 1570 | -406 | 74 | -827 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1146 | 1570 | -424 | 73 | -810 | AC

## 0630
Detailed results
Generated at: | 06/06/2026 22:47:32
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 06:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3107.89
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Rosiori-Mukacevo/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1030 | 999 | 31 | 103 | 400 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1020 | 999 | 21 | 102 | 398 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1571 | 1570 | 1 | 100 | -1129 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1557 | 1570 | -13 | 99 | -1120 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1557 | 1570 | -13 | 99 | -1120 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1549 | 1570 | -21 | 99 | -1114 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1539 | 1570 | -31 | 98 | -1107 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 973 | 999 | -26 | 97 | 376 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1518 | 1570 | -52 | 97 | -1092 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1509 | 1570 | -61 | 96 | -1085 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1509 | 1570 | -61 | 96 | -1085 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1495 | 1570 | -75 | 95 | -1076 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1488 | 1570 | -82 | 95 | -1071 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 945 | 999 | -54 | 95 | 370 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1482 | 1570 | -88 | 94 | -1066 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1480 | 1570 | -90 | 94 | -1065 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1474 | 1570 | -96 | 94 | -1061 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1426 | 1570 | -144 | 91 | -1024 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 795 | 999 | -204 | 80 | 294 | AC

## 0730
Detailed results
Generated at: | 06/06/2026 22:47:32
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 07:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3164
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Rosiori-Mukacevo/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00003 | PRA 110 kV S4 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 404 |  | 580 | 0 | TRUE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 7 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 83 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 11 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 19 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 24 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 10 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 19 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 10 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 19 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 18 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 20 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 7 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 20 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 14 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 8 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 17 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 24 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 31 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 13 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 15 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 72 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 7 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 2 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 3 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 3 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 5 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1568 | 1570 | -2 | 100 | -1125 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1557 | 1570 | -13 | 99 | -1118 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1557 | 1570 | -13 | 99 | -1118 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1546 | 1570 | -24 | 98 | -1109 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1537 | 1570 | -33 | 98 | -1103 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1516 | 1570 | -54 | 97 | -1088 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1499 | 1570 | -71 | 96 | -1076 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1499 | 1570 | -71 | 96 | -1076 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1495 | 1570 | -75 | 95 | -1073 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1486 | 1570 | -84 | 95 | -1065 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1484 | 1570 | -86 | 94 | -1065 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1481 | 1570 | -89 | 94 | -1064 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 940 | 999 | -59 | 94 | 364 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1475 | 1570 | -95 | 94 | -1059 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 935 | 999 | -64 | 94 | 362 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1387 | 1570 | -183 | 88 | -990 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1597 | 1920 | -323 | 83 | 1150 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 455 | 577 | -122 | 79 | 289 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1448 | 1920 | -472 | 75 | 1040 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 741 | 999 | -258 | 74 | 283 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 727 | 999 | -272 | 73 | 274 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 703 | 999 | -296 | 70 | 255 | AC

## 0830
Detailed results
Generated at: | 06/06/2026 22:47:33
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 08:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00007 | PRA 110 kV Resita | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 268 |  | 580 | 0 | TRUE | FALSE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 10 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 78 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 6 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 10 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 6 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 13 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 6 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 5 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 10 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 11 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 4 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 8 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 6 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 9 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 9 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 9 | 6 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 9 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 15 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 19 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 29 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 23 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 29 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 15 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 9 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 26 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 8 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2052 | 1570 | 482 | 131 | -1464 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2052 | 1570 | 482 | 131 | -1464 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2041 | 1570 | 471 | 130 | -1456 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2010 | 1570 | 440 | 128 | -1434 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1995 | 1570 | 425 | 127 | -1424 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1976 | 1570 | 406 | 126 | -1411 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1961 | 1570 | 391 | 125 | -1400 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1961 | 1570 | 391 | 125 | -1400 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1945 | 1570 | 375 | 124 | -1390 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1941 | 1570 | 371 | 124 | -1383 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1940 | 1570 | 370 | 124 | -1385 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1936 | 1570 | 366 | 123 | -1383 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1905 | 1570 | 335 | 121 | -1360 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1202 | 999 | 202 | 120 | 462 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1184 | 999 | 185 | 118 | 459 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1169 | 999 | 169 | 117 | 450 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1807 | 1570 | 237 | 115 | -1289 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1128 | 999 | 129 | 113 | 440 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1957 | 1890 | 67 | 104 | 1386 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1957 | 1890 | 67 | 104 | 1386 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1957 | 1920 | 37 | 102 | -1342 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1957 | 1920 | 37 | 102 | -1342 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 939 | 999 | -60 | 94 | 341 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1770 | 1920 | -150 | 92 | 1264 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1597 | 1920 | -323 | 83 | 1135 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1499 | 1890 | -391 | 79 | 1060 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1499 | 1890 | -391 | 79 | 1060 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RO] [DIR] TRA 400/220 kV AT3 Arad | RARA4D1 RARAD22 3 | 456 | 577 | -121 | 79 | 281 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1499 | 1920 | -421 | 78 | -1035 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1499 | 1920 | -421 | 78 | -1035 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1247 | 1600 | -353 | 78 | -846 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 733 | 960 | -227 | 76 | 299 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1522 | 2000 | -478 | 76 | -1054 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1522 | 2000 | -478 | 76 | 1071 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1511 | 2000 | -489 | 76 | 1063 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1511 | 2000 | -489 | 76 | -1043 | AC
RO_CO_00006 | N-1 OHL 400 kV Domnesti-Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 748 | 999 | -252 | 75 | 285 | AC

## 0930
Detailed results
Generated at: | 06/06/2026 22:47:33
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 09:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 273 |  | 389 | 0 | TRUE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 82 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 7 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 11 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 7 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 14 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 7 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 6 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 10 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 12 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 4 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 9 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 9 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 9 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 9 | 11 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 9 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 23 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 35 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 29 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 16 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 28 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 10 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2054 | 1570 | 484 | 131 | -1464 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2054 | 1570 | 484 | 131 | -1464 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2038 | 1570 | 468 | 130 | -1453 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2016 | 1570 | 446 | 128 | -1437 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1994 | 1570 | 424 | 127 | -1422 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1981 | 1570 | 411 | 126 | -1413 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1977 | 1570 | 407 | 126 | -1410 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1967 | 1570 | 397 | 125 | -1403 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1967 | 1570 | 397 | 125 | -1403 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1946 | 1570 | 376 | 124 | -1388 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1941 | 1570 | 371 | 124 | -1384 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1932 | 1570 | 362 | 123 | -1377 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1902 | 1570 | 332 | 121 | -1356 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1167 | 999 | 168 | 117 | 451 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1156 | 999 | 156 | 116 | 447 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1815 | 1570 | 245 | 116 | -1294 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1151 | 999 | 152 | 115 | 447 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1121 | 999 | 121 | 112 | 437 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1953 | 1890 | 63 | 103 | 1384 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1953 | 1890 | 63 | 103 | 1384 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1953 | 1920 | 33 | 102 | -1340 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1953 | 1920 | 33 | 102 | -1340 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 914 | 999 | -85 | 92 | 336 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1712 | 1920 | -208 | 89 | 1220 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 833 | 960 | -127 | 87 | 335 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1545 | 1920 | -375 | 80 | 1097 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1491 | 1890 | -399 | 79 | 1055 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1491 | 1890 | -399 | 79 | 1055 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1491 | 1920 | -429 | 78 | -1030 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1491 | 1920 | -429 | 78 | -1030 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1536 | 2000 | -464 | 77 | 1082 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1536 | 2000 | -464 | 77 | -1065 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1526 | 2000 | -474 | 76 | 1075 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1526 | 2000 | -474 | 76 | -1054 | AC
RO_CO_00014 | N-1 OHL 400 kV Lacu Sarat - Isaccea | [RO-RO] [OPP] OHL 400 kV Smardan - Isaccea c2 | RSMI2R1 RISAC41 2 | 1182 | 1600 | -418 | 74 | 836 | AC
RO_CO_00006 | N-1 OHL 400 kV Domnesti-Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 736 | 999 | -263 | 74 | 280 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1172 | 1600 | -428 | 73 | -806 | AC

## 1030
Detailed results
Generated at: | 06/06/2026 22:47:33
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 10:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Rosiori-Mukacevo/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 294 |  | 389 | 0 | TRUE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 0 | 107 |  | 114 | 0 | TRUE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 34 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 7 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 11 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 7 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 14 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 7 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 6 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 10 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 12 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 4 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 9 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 24 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 37 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 29 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 17 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 27 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 10 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2218 | 1570 | 648 | 141 | -1577 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2210 | 1570 | 640 | 141 | -1572 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2210 | 1570 | 640 | 141 | -1572 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2196 | 1570 | 626 | 140 | -1562 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2167 | 1570 | 597 | 138 | -1541 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2155 | 1570 | 585 | 137 | -1533 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2153 | 1570 | 583 | 137 | -1532 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2139 | 1570 | 569 | 136 | -1522 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2139 | 1570 | 569 | 136 | -1522 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2118 | 1570 | 548 | 135 | -1507 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2111 | 1570 | 541 | 134 | -1502 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2102 | 1570 | 532 | 134 | -1495 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2088 | 1570 | 518 | 133 | -1486 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2004 | 1570 | 434 | 128 | -1426 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1183 | 999 | 184 | 118 | 454 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1177 | 999 | 177 | 118 | 454 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1124 | 999 | 125 | 112 | 433 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1088 | 999 | 89 | 109 | 423 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1920 | 1920 | 0 | 100 | 1365 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 912 | 999 | -87 | 91 | 332 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1216 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1216 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1737 | 1920 | -183 | 90 | 1226 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1712 | 1920 | -208 | 89 | -1182 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1712 | 1920 | -208 | 89 | -1182 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 805 | 960 | -155 | 84 | 324 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1233 | 1600 | -367 | 77 | -845 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1373 | 1890 | -517 | 73 | 974 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1373 | 1890 | -517 | 73 | 974 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1390 | 1920 | -530 | 72 | 987 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1373 | 1920 | -547 | 72 | -952 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1373 | 1920 | -547 | 72 | -952 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1357 | 1920 | -563 | 71 | -917 | AC

## 1130
Detailed results
Generated at: | 06/06/2026 22:47:33
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 11:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Rosiori-Mukacevo/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 294 |  | 389 | 0 | TRUE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 0 | 107 |  | 114 | 0 | TRUE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 34 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 7 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 11 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 7 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 14 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 7 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 6 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 10 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 12 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 4 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 9 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 24 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 37 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 29 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 17 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 27 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 10 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2218 | 1570 | 648 | 141 | -1577 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2210 | 1570 | 640 | 141 | -1572 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2210 | 1570 | 640 | 141 | -1572 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2196 | 1570 | 626 | 140 | -1562 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2167 | 1570 | 597 | 138 | -1541 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2155 | 1570 | 585 | 137 | -1533 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2153 | 1570 | 583 | 137 | -1532 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2139 | 1570 | 569 | 136 | -1522 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2139 | 1570 | 569 | 136 | -1522 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2118 | 1570 | 548 | 135 | -1507 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2111 | 1570 | 541 | 134 | -1502 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2102 | 1570 | 532 | 134 | -1495 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2088 | 1570 | 518 | 133 | -1485 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2004 | 1570 | 434 | 128 | -1426 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1183 | 999 | 184 | 118 | 454 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1177 | 999 | 177 | 118 | 454 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1124 | 999 | 125 | 112 | 433 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1088 | 999 | 89 | 109 | 423 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1920 | 1920 | 0 | 100 | 1365 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 912 | 999 | -87 | 91 | 332 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1216 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1216 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1737 | 1920 | -183 | 90 | 1226 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1712 | 1920 | -208 | 89 | -1182 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1712 | 1920 | -208 | 89 | -1182 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 805 | 960 | -155 | 84 | 324 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1233 | 1600 | -367 | 77 | -845 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1373 | 1890 | -517 | 73 | 974 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1373 | 1890 | -517 | 73 | 974 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1390 | 1920 | -530 | 72 | 987 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1373 | 1920 | -547 | 72 | -952 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1373 | 1920 | -547 | 72 | -952 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1357 | 1920 | -563 | 71 | -917 | AC

## 1230
Detailed results
Generated at: | 06/06/2026 22:47:33
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 12:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Rosiori-Mukacevo/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 294 |  | 389 | 0 | TRUE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 0 | 107 |  | 114 | 0 | TRUE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 34 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 7 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 11 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 7 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 14 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 7 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 6 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 10 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 12 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 4 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 9 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 24 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 37 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 29 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 17 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 27 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 10 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2218 | 1570 | 648 | 141 | -1577 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2210 | 1570 | 640 | 141 | -1572 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2210 | 1570 | 640 | 141 | -1572 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2196 | 1570 | 626 | 140 | -1562 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2167 | 1570 | 597 | 138 | -1541 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2155 | 1570 | 585 | 137 | -1533 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2153 | 1570 | 583 | 137 | -1532 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2139 | 1570 | 569 | 136 | -1522 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2139 | 1570 | 569 | 136 | -1522 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2118 | 1570 | 548 | 135 | -1507 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2111 | 1570 | 541 | 134 | -1502 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2102 | 1570 | 532 | 134 | -1495 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2088 | 1570 | 518 | 133 | -1485 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2004 | 1570 | 434 | 128 | -1426 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1183 | 999 | 184 | 118 | 454 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1177 | 999 | 177 | 118 | 454 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1124 | 999 | 125 | 112 | 433 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1088 | 999 | 89 | 109 | 423 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1920 | 1920 | 0 | 100 | 1365 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 912 | 999 | -87 | 91 | 332 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1216 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1216 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1737 | 1920 | -183 | 90 | 1226 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1712 | 1920 | -208 | 89 | -1182 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1712 | 1920 | -208 | 89 | -1182 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 805 | 960 | -155 | 84 | 324 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1233 | 1600 | -367 | 77 | -845 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1373 | 1890 | -517 | 73 | 974 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1373 | 1890 | -517 | 73 | 974 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1390 | 1920 | -530 | 72 | 987 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1373 | 1920 | -547 | 72 | -952 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1373 | 1920 | -547 | 72 | -952 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1357 | 1920 | -563 | 71 | -917 | AC

## 1330
Detailed results
Generated at: | 06/06/2026 22:47:33
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 13:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Rosiori-Mukacevo/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 294 |  | 389 | 0 | TRUE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 0 | 107 |  | 114 | 0 | TRUE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 34 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 7 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 11 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 7 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 14 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 7 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 6 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 10 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 12 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 4 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 9 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 24 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 37 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 29 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 17 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 27 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 10 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2218 | 1570 | 648 | 141 | -1577 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2210 | 1570 | 640 | 141 | -1572 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2210 | 1570 | 640 | 141 | -1572 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2196 | 1570 | 626 | 140 | -1562 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2167 | 1570 | 597 | 138 | -1541 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2155 | 1570 | 585 | 137 | -1533 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2153 | 1570 | 583 | 137 | -1532 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2139 | 1570 | 569 | 136 | -1522 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2139 | 1570 | 569 | 136 | -1522 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2118 | 1570 | 548 | 135 | -1507 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2111 | 1570 | 541 | 134 | -1502 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2102 | 1570 | 532 | 134 | -1495 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2088 | 1570 | 518 | 133 | -1485 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2004 | 1570 | 434 | 128 | -1426 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1183 | 999 | 184 | 118 | 454 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1177 | 999 | 177 | 118 | 454 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1124 | 999 | 125 | 112 | 433 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1088 | 999 | 89 | 109 | 423 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1920 | 1920 | 0 | 100 | 1365 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 912 | 999 | -87 | 91 | 332 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1216 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1216 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1737 | 1920 | -183 | 90 | 1226 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1712 | 1920 | -208 | 89 | -1182 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1712 | 1920 | -208 | 89 | -1182 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 805 | 960 | -155 | 84 | 324 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1233 | 1600 | -367 | 77 | -845 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1373 | 1890 | -517 | 73 | 974 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1373 | 1890 | -517 | 73 | 974 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1390 | 1920 | -530 | 72 | 987 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1373 | 1920 | -547 | 72 | -952 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1373 | 1920 | -547 | 72 | -952 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1357 | 1920 | -563 | 71 | -917 | AC

## 1430
Detailed results
Generated at: | 06/06/2026 22:47:33
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 14:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV Rosiori-Mukacevo/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 294 |  | 389 | 0 | TRUE | FALSE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 0 | 107 |  | 114 | 0 | TRUE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 34 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 7 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 11 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 7 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 14 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 7 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 6 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 11 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 10 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 12 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 4 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 9 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 7 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 4 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 9 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 24 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 37 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 29 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 17 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 27 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 10 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2218 | 1570 | 648 | 141 | -1577 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2210 | 1570 | 640 | 141 | -1572 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2210 | 1570 | 640 | 141 | -1572 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2196 | 1570 | 626 | 140 | -1562 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2167 | 1570 | 597 | 138 | -1541 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2155 | 1570 | 585 | 137 | -1533 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2153 | 1570 | 583 | 137 | -1532 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2139 | 1570 | 569 | 136 | -1522 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2139 | 1570 | 569 | 136 | -1522 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2118 | 1570 | 548 | 135 | -1507 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2111 | 1570 | 541 | 134 | -1502 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2102 | 1570 | 532 | 134 | -1495 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2088 | 1570 | 518 | 133 | -1485 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 2004 | 1570 | 434 | 128 | -1426 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1183 | 999 | 184 | 118 | 454 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1177 | 999 | 177 | 118 | 454 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1124 | 999 | 125 | 112 | 433 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1088 | 999 | 89 | 109 | 423 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1920 | 1920 | 0 | 100 | 1365 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 912 | 999 | -87 | 91 | 332 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1216 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1712 | 1890 | -178 | 91 | 1216 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1737 | 1920 | -183 | 90 | 1226 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1712 | 1920 | -208 | 89 | -1182 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1712 | 1920 | -208 | 89 | -1182 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 805 | 960 | -155 | 84 | 324 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-HU] [OPP] TIE 400 kV Arad-Sandorfalva | RARA4D1 XSA_AR11 1 | 1233 | 1600 | -367 | 77 | -845 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1373 | 1890 | -517 | 73 | 974 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1373 | 1890 | -517 | 73 | 974 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1390 | 1920 | -530 | 72 | 987 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1373 | 1920 | -547 | 72 | -952 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1373 | 1920 | -547 | 72 | -952 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-UA] [OPP]TIE 400 kV Rosiori-Mukacevo | RROSI41 XRO_MU11 1 | 1357 | 1920 | -563 | 71 | -917 | AC

## 1530
Detailed results
Generated at: | 06/06/2026 22:47:34
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 15:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 23 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 53 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 9 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 14 |  | 14 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 74 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 11 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 17 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 11 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 23 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 10 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 18 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 9 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 18 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 16 | 40 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 19 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 6 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 28 | 50 |  | 50 | 0 | FALSE | FALSE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 22 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 15 | 26 |  | 26 | 0 | FALSE | FALSE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 30 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 15 | 59 |  | 59 | 0 | FALSE | FALSE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 18 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 28 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 23 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 1 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 26 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 11 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 9 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 7 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 2139 | 1890 | 249 | 113 | 1515 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 2139 | 1890 | 249 | 113 | 1515 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 2139 | 1920 | 219 | 111 | -1463 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 2139 | 1920 | 219 | 111 | -1463 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1733 | 1570 | 163 | 110 | -1247 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1733 | 1570 | 163 | 110 | -1247 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1610 | 1570 | 40 | 103 | -1158 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1608 | 1570 | 38 | 102 | -1156 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1599 | 1570 | 29 | 102 | -1150 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1592 | 1570 | 22 | 101 | -1145 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1583 | 1570 | 13 | 101 | -1138 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1582 | 1570 | 12 | 101 | -1137 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1579 | 1570 | 9 | 101 | -1130 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1516 | 1570 | -54 | 97 | -1090 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1461 | 1570 | -109 | 93 | -1049 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1445 | 1570 | -125 | 92 | -1040 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1836 | 2000 | -164 | 92 | -1256 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1836 | 2000 | -164 | 92 | 1281 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1821 | 2000 | -179 | 91 | -1242 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1821 | 2000 | -179 | 91 | 1271 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 858 | 960 | -102 | 89 | 346 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 220 kV Filesti - Barbosi | RBARB22 RFILE22 1 | 754 | 890 | -136 | 85 | 291 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1325 | 1570 | -245 | 84 | -951 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 827 | 999 | -172 | 83 | 318 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 810 | 999 | -189 | 81 | 316 | AC
RO_CO_00011 | N-1 OHL 400 kV Isaccea - Rahman | [RO-RO] [DIR] OHL 400 kV Medgidia Sud - Stupina | RMED141 RSTUP41 1 | 1583 | 2000 | -417 | 79 | 1094 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1477 | 1890 | -413 | 78 | 1045 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1477 | 1890 | -413 | 78 | 1045 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1477 | 1920 | -443 | 77 | -1020 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1477 | 1920 | -443 | 77 | -1020 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1405 | 1920 | -515 | 73 | -973 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1405 | 1920 | -515 | 73 | -973 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1338 | 1890 | -552 | 71 | 949 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1338 | 1890 | -552 | 71 | 949 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1334 | 1890 | -556 | 71 | 946 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1334 | 1890 | -556 | 71 | 946 | AC

## 1630
Detailed results
Generated at: | 06/06/2026 22:47:34
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 16:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 24 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 55 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 7 | 10 |  | 10 | 0 | FALSE | FALSE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 14 |  | 14 | 0 | FALSE | FALSE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 55 |  | 55 | 0 | FALSE | FALSE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 15 |  | 15 | 0 | FALSE | FALSE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 0 | 10 |  | 10 | 0 | TRUE | FALSE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 31 |  | 31 | 0 | FALSE | FALSE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 10 |  | 15 | 0 | FALSE | FALSE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 12 |  | 12 | 0 | FALSE | FALSE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 77 | 90 |  | 90 | 0 | FALSE | FALSE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 11 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 18 | 37 |  | 37 | 0 | FALSE | FALSE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 11 | 46 |  | 46 | 0 | FALSE | FALSE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 23 | 48 |  | 48 | 0 | FALSE | FALSE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 10 | 39 |  | 39 | 0 | FALSE | FALSE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 19 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 9 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 19 | 38 |  | 38 | 0 | FALSE | FALSE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 17 | 74 |  | 74 | 0 | FALSE | FALSE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 20 | 45 |  | 45 | 0 | FALSE | FALSE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 6 | 25 |  | 25 | 0 | FALSE | FALSE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 30 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 22 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 15 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 31 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 31 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 31 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 31 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 31 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 15 | 59 |  | 59 | 0 | FALSE | FALSE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 16 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 24 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 1 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 27 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 11 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 14 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 9 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 10 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 8 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 14 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1932 | 1890 | 42 | 102 | 1374 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1932 | 1890 | 42 | 102 | 1374 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1932 | 1920 | 12 | 101 | -1332 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1932 | 1920 | 12 | 101 | -1332 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1503 | 1570 | -67 | 96 | -1080 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1503 | 1570 | -67 | 96 | -1080 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1381 | 1570 | -189 | 88 | -992 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1365 | 1570 | -205 | 87 | -981 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1355 | 1570 | -215 | 86 | -974 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1351 | 1570 | -219 | 86 | -971 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1350 | 1570 | -220 | 86 | -970 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1350 | 1570 | -220 | 86 | -970 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1346 | 1570 | -224 | 86 | -967 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1342 | 1570 | -228 | 85 | -964 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 843 | 999 | -156 | 84 | 324 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1298 | 1570 | -272 | 83 | -932 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 818 | 999 | -181 | 82 | 322 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1262 | 1570 | -308 | 80 | -906 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1233 | 1570 | -337 | 79 | -886 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 220 kV Lacu Sarat - Filesti | RLAC222 RFILE12 1 | 695 | 890 | -195 | 78 | 275 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1539 | 2000 | -461 | 77 | 1081 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1539 | 2000 | -461 | 77 | -1063 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 220 kV Filesti - Barbosi | RBARB22 RFILE22 1 | 681 | 890 | -209 | 76 | 265 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1527 | 2000 | -473 | 76 | 1071 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1527 | 2000 | -473 | 76 | -1051 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 738 | 999 | -261 | 74 | 294 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 220 kV Focsani Vest - Frumusita | RFCSV22 RFRUM12 1 | 653 | 890 | -237 | 73 | 255 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1372 | 1890 | -518 | 73 | 975 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1372 | 1890 | -518 | 73 | 975 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 687 | 960 | -273 | 72 | 279 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1372 | 1920 | -548 | 71 | -954 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1372 | 1920 | -548 | 71 | -954 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 712 | 999 | -287 | 71 | 284 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1104 | 1570 | -466 | 70 | -793 | AC

## 1730
Detailed results
Generated at: | 06/06/2026 22:47:34
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 17:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3675
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00004 | PRA 110 kV S5 | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | close --> open
N/A | RO_RA_00005 | PRA 110 kV Pelicanu | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 580 |  | 580 | 0 | TRUE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 307 |  | 389 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 25 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 56 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 4 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 78 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 17 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 28 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 17 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 36 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 14 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 29 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 14 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 29 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 26 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 30 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 10 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 30 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 23 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 16 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 32 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 32 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 32 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 32 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 32 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 13 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 18 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 17 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 1 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 1 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 8 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 28 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 8 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 13 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 9 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 19 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 28 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00181 | RO | RRETE_5 _generator | 0 | 20 |  |  | 6 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00182 | RO | RCIRNA5 _generator | 0 | 29 |  |  | 10 | 0 |  | 29 | 0 | FALSE | TRUE
RO_RA_00183 | RO | RCIRNB5 _generator | 0 | 27 |  |  | 9 | 0 |  | 27 | 0 | FALSE | TRUE
RO_RA_00184 | RO | RHATE_5 _generator | 0 | 52 |  |  | 14 | 0 |  | 52 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | -1126 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | -1126 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 965 | 999 | -34 | 97 | 376 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 955 | 999 | -44 | 96 | 372 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1570 | -85 | 95 | -1065 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1462 | 1570 | -108 | 93 | -1049 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1448 | 1570 | -122 | 92 | -1039 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1737 | 1890 | -153 | 92 | 1236 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1737 | 1890 | -153 | 92 | 1236 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1442 | 1570 | -128 | 92 | -1035 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1438 | 1570 | -132 | 92 | -1032 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1428 | 1570 | -142 | 91 | -1023 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1428 | 1570 | -142 | 91 | -1023 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1737 | 1920 | -183 | 90 | -1202 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1737 | 1920 | -183 | 90 | -1202 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1415 | 1570 | -155 | 90 | -1016 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 885 | 999 | -114 | 89 | 336 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1380 | 1570 | -190 | 88 | -990 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 864 | 999 | -135 | 86 | 332 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1326 | 1570 | -244 | 84 | -949 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 802 | 960 | -158 | 84 | 324 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1306 | 1570 | -264 | 83 | -938 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1560 | 1920 | -360 | 81 | 1120 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1275 | 1570 | -295 | 81 | -912 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 771 | 999 | -228 | 77 | 285 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1413 | 1920 | -507 | 74 | 1012 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [DIR] OHL 220 kV Lacu Sarat - Filesti | RLAC222 RFILE12 1 | 649 | 890 | -241 | 73 | 257 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1410 | 2000 | -590 | 70 | 990 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1410 | 2000 | -590 | 70 | -975 | AC

## 1830
Detailed results
Generated at: | 06/06/2026 22:47:34
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 18:30
Border & direction: | South-Romania Importing
Remedial actions | False
Margin satisfied | True
Final step | Margin Calculation
TTC [MW]: | 3801.08
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | -1119 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | -1119 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 997 | 999 | -2 | 100 | 386 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 983 | 999 | -17 | 98 | 380 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 964 | 999 | -35 | 96 | 378 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 962 | 999 | -37 | 96 | 375 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1491 | 1570 | -79 | 95 | -1062 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1490 | 1570 | -80 | 95 | -1062 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1488 | 1570 | -82 | 95 | -1062 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1488 | 1570 | -82 | 95 | -1062 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1474 | 1570 | -96 | 94 | -1050 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1467 | 1570 | -103 | 93 | -1045 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1452 | 1570 | -118 | 92 | -1033 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1445 | 1570 | -125 | 92 | -1028 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1406 | 1570 | -164 | 90 | -1000 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1391 | 1570 | -179 | 89 | -990 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1380 | 1570 | -190 | 88 | -981 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1352 | 1570 | -218 | 86 | -962 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 818 | 999 | -181 | 82 | 309 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1499 | 1890 | -391 | 79 | 1066 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1499 | 1890 | -391 | 79 | 1066 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 754 | 960 | -206 | 79 | 305 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1499 | 1920 | -421 | 78 | -1041 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1499 | 1920 | -421 | 78 | -1041 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1495 | 2000 | -505 | 75 | 1049 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1495 | 2000 | -505 | 75 | -1032 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1480 | 2000 | -520 | 74 | -1018 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1480 | 2000 | -520 | 74 | 1037 | AC

## 1930
Detailed results
Generated at: | 06/06/2026 22:47:34
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 19:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3863
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 1/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 220 |  | 580 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 27 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 65 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 84 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 18 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 30 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 19 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 39 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 15 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 31 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 31 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 28 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 32 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 11 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 27 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 20 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 14 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 8 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 8 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 8 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 25 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00158 | RO | RSTEJ_5 _generator | 0 | 137 |  |  | 0 | 137 |  | 137 | 0 | TRUE | FALSE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 18 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 23 |  | 23 | 0 | FALSE | FALSE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 31 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 13 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 217 |  | 217 | 0 | TRUE | FALSE
RO_RA_00174 | RO | RSUGA22 _generator | 0 | 150 |  |  | 0 | 150 |  | 150 | 0 | TRUE | FALSE
RO_RA_00175 | RO | RGILC22 _generator | 0 | 150 |  |  | 0 | 121 |  | 150 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 28 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1565 | 1570 | -5 | 100 | -1118 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1565 | 1570 | -5 | 100 | -1118 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | -1055 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | -1055 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1476 | 1570 | -94 | 94 | -1054 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1472 | 1570 | -98 | 94 | -1051 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1462 | 1570 | -108 | 93 | -1044 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1453 | 1570 | -117 | 93 | -1037 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1570 | -131 | 92 | -1027 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1433 | 1570 | -137 | 91 | -1022 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1398 | 1570 | -172 | 89 | -996 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1381 | 1570 | -189 | 88 | -985 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1376 | 1570 | -194 | 88 | -982 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1344 | 1570 | -226 | 86 | -959 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1572 | 1890 | -318 | 83 | 1118 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1572 | 1890 | -318 | 83 | 1118 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1572 | 1920 | -348 | 82 | -1090 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1572 | 1920 | -348 | 82 | -1090 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1513 | 2000 | -487 | 76 | 1062 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1513 | 2000 | -487 | 76 | -1045 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1498 | 2000 | -502 | 75 | 1050 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1498 | 2000 | -502 | 75 | -1030 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 711 | 960 | -249 | 74 | 288 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 732 | 999 | -267 | 73 | 285 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 728 | 999 | -271 | 73 | 284 | AC

## 2030
Detailed results
Generated at: | 06/06/2026 22:47:34
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 20:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 484 |  | 580 | 0 | TRUE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 389 |  | 389 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 50 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 63 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 82 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 18 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 29 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 38 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 15 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 28 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 32 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 10 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 20 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 13 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 7 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 7 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 17 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 31 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 11 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 3 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 27 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1698 | 1570 | 128 | 108 | -1210 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1698 | 1570 | 128 | 108 | -1210 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 1025 | 999 | 26 | 103 | 387 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1597 | 1570 | 27 | 102 | -1138 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1597 | 1570 | 27 | 102 | -1140 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1581 | 1570 | 11 | 101 | -1127 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 1003 | 999 | 4 | 100 | 383 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1570 | 1570 | 0 | 100 | -1121 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1566 | 1570 | -4 | 100 | -1116 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1566 | 1570 | -4 | 100 | -1116 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 994 | 999 | -5 | 99 | 380 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1560 | 1570 | -10 | 99 | -1114 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 951 | 960 | -9 | 99 | 383 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1540 | 1570 | -30 | 98 | -1101 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 977 | 999 | -22 | 98 | 378 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1570 | -76 | 95 | -1069 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1480 | 1570 | -90 | 94 | -1058 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1779 | 1890 | -111 | 94 | 1263 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1779 | 1890 | -111 | 94 | 1263 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1880 | 2000 | -120 | 94 | -1294 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1880 | 2000 | -120 | 94 | 1321 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1791 | 1920 | -129 | 93 | 1282 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1862 | 2000 | -138 | 93 | 1307 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1862 | 2000 | -138 | 93 | -1277 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1779 | 1920 | -141 | 93 | -1227 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1779 | 1920 | -141 | 93 | -1227 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1439 | 1570 | -131 | 92 | -1021 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1419 | 1570 | -151 | 90 | -1009 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 831 | 999 | -168 | 83 | 306 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1574 | 1920 | -346 | 82 | 1119 | AC
RO_CO_00006 | N-1 OHL 400 kV Domnesti-Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 759 | 999 | -240 | 76 | 292 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1413 | 1920 | -507 | 74 | 1012 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 RURE212 1 | 729 | 999 | -270 | 73 | 279 | AC
RO_CO_00023 | N-1 OHL 400 kV Gutinas – Smardan | [RO-RO] [OPP] OHL 220 kV Filesti - Barbosi | RBARB22 RFILE22 1 | 637 | 890 | -253 | 72 | 248 | AC

## 2130
Detailed results
Generated at: | 06/06/2026 22:47:34
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 21:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 305 |  | 580 | 0 | TRUE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 389 |  | 389 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 50 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 59 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00120 | RO | RTOPV_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 2 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 6 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00124 | RO | RELAR_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 3 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 3 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 2 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 83 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 18 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 29 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 38 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 15 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 28 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 32 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 10 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 20 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 14 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 28 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 28 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 28 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 28 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 28 | 27 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 7 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 7 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 18 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 31 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 11 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 28 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1781 | 1570 | 211 | 113 | -1276 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1781 | 1570 | 211 | 113 | -1276 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1666 | 1570 | 96 | 106 | -1193 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1650 | 1570 | 80 | 105 | -1182 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1641 | 1570 | 71 | 105 | -1176 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1638 | 1570 | 68 | 104 | -1170 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1638 | 1570 | 68 | 104 | -1171 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1638 | 1570 | 68 | 104 | -1171 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1637 | 1570 | 67 | 104 | -1173 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1617 | 1570 | 47 | 103 | -1160 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1890 | 1890 | 0 | 100 | 1342 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1890 | 1890 | 0 | 100 | 1342 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1552 | 1570 | -18 | 99 | -1114 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1970 | 2000 | -30 | 98 | -1355 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1970 | 2000 | -30 | 98 | 1384 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1890 | 1920 | -30 | 98 | -1302 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1890 | 1920 | -30 | 98 | -1302 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1951 | 2000 | -49 | 98 | 1369 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1951 | 2000 | -49 | 98 | -1336 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1520 | 1570 | -50 | 97 | -1090 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1511 | 1570 | -59 | 96 | -1078 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1494 | 1570 | -76 | 95 | -1060 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 884 | 999 | -115 | 88 | 339 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 868 | 999 | -131 | 87 | 337 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 830 | 999 | -169 | 83 | 320 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1535 | 1920 | -385 | 80 | 1107 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 796 | 999 | -203 | 80 | 309 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1402 | 1890 | -488 | 74 | 995 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1402 | 1890 | -488 | 74 | 995 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1402 | 1920 | -518 | 73 | -973 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1402 | 1920 | -518 | 73 | -973 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [OPP] OHL 220 kV Alba Iulia-Mintia | RAIUL22 RMINT12 1 | 646 | 890 | -244 | 73 | 248 | AC

## 2230
Detailed results
Generated at: | 06/06/2026 22:47:35
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 22:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]:
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 580 |  | 580 | 0 | TRUE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 37 |  | 389 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 27 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 60 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 64 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 18 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 30 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 38 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 15 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 28 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 32 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 11 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 20 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 14 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 28 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 28 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 28 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 28 | 6 |  | 53 | 0 | FALSE | FALSE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 28 | 53 |  | 53 | 0 | FALSE | FALSE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 8 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 8 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 8 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 18 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 31 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 12 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 28 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1797 | 1570 | 227 | 114 | -1290 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1797 | 1570 | 227 | 114 | -1290 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1678 | 1570 | 108 | 107 | -1204 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1669 | 1570 | 99 | 106 | -1197 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1654 | 1570 | 84 | 105 | -1187 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1651 | 1570 | 81 | 105 | -1183 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1651 | 1570 | 81 | 105 | -1183 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1651 | 1570 | 81 | 105 | -1183 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1650 | 1570 | 80 | 105 | -1185 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1633 | 1570 | 63 | 104 | -1174 | AC
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1902 | 1890 | 12 | 101 | 1341 | AC
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1902 | 1890 | 12 | 101 | 1341 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1575 | 1570 | 5 | 100 | -1133 | AC
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1902 | 1920 | -18 | 99 | -1300 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1902 | 1920 | -18 | 99 | -1300 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 945 | 960 | -15 | 98 | 383 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1532 | 1570 | -38 | 98 | -1100 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1528 | 1570 | -42 | 97 | -1093 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1512 | 1570 | -58 | 96 | -1077 | AC
BG_RO_CO_00005 | N-1 TIE 400 kV MEDGIDIA SUD - DOBRUDJA | [BG-RO] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | XVA_MG11 VVARNA11 1 | 1896 | 2000 | -104 | 95 | 1329 | AC
RO-BG_CO_00005 | N-1 TIE 400 kV DOBRUDJA- MEDGIDIA SUD | [RO-BG] [OPP] TIE 400 kV MEDGIDIA SUD - VARNA | RMED141 XVA_MG11 1 | 1896 | 2000 | -104 | 95 | -1302 | AC
BG_RO_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [BG-RO] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | XDO_MG11 VDOBRU11 1 | 1880 | 2000 | -120 | 94 | 1317 | AC
RO-BG_CO_00004 | N-1 TIE 400 kV MEDGIDIA SUD - VARNA | [RO-BG] [OPP] TIE 400 kV DOBRUDJA- MEDGIDIA SUD | RMEDG41 XDO_MG11 1 | 1880 | 2000 | -120 | 94 | -1286 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 938 | 999 | -61 | 94 | 360 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 920 | 999 | -79 | 92 | 357 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 852 | 999 | -148 | 85 | 328 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 814 | 999 | -185 | 82 | 316 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1460 | 1920 | -460 | 76 | 1053 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12 VAECKO11 1 | 1417 | 1890 | -473 | 75 | 998 | AC
RO_RS_CO_00001 | N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [BG-RO] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11 VAECKO11 1 | 1417 | 1890 | -473 | 75 | 998 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 XKO_TI12 1 | 1417 | 1920 | -503 | 74 | -976 | AC
RO-RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap | [RO-BG] [OPP] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 XKO_TI11 1 | 1417 | 1920 | -503 | 74 | -976 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 716 | 999 | -283 | 72 | 267 | AC

## 2330
Detailed results
Generated at: | 06/06/2026 22:47:35
Business day: | 2026-06-08
Horizon: | 2DA
Timestamp | 23:30
Border & direction: | South-Romania Importing
Remedial actions | True
Margin satisfied | False
Final step | RAO
TTC [MW]: | 3121
Loading threshold | 0.7
Limiting CNEC | N-1 TIE 400 kV TINTARENI-KOZLODUI 2/[RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap
Applied RAs
Non Costly RAO
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
N/A | RO_RA_00006 | PRA 110 kV Dobrogea | preventive | topological_ra | RO | applied | open --> close
N/A | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
N/A | RO_RA_00101 | PST_ARAD 400/220_3 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(12) HigherStep(12.0)
N/A | RO_RA_00102 | PST_URECHESTI 400/220_1 | preventive | pst_ra | RO | applied | LowerStep(-12.0) CurrentStep(-12) HigherStep(12.0)
Costly RAO
RA RD ID | TSO | Generator Name | Minimum Power [MW] | Maximum Power [MW] | RDP- | RDP+ | P [MW] before RAO | P [MW] after RAO | P0 [MW] | Plimit+ [MW] | Plimit- [MW] | Started up | Shutdown
RO_RA_00114 | RO | RPDF222 _generator | 0 | 580 |  |  | 0 | 580 |  | 580 | 0 | TRUE | FALSE
RO_RA_00115 | RO | RPDF212 _generator | 0 | 389 |  |  | 0 | 174 |  | 389 | 0 | TRUE | FALSE
RO_RA_00116 | RO | RVMAR_5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00117 | RO | RGODI_5 _generator | 0 | 114 |  |  | 59 | 0 |  | 114 | 0 | FALSE | TRUE
RO_RA_00121 | RO | RFMEP_5 _generator | 0 | 14 |  |  | 1 | 0 |  | 14 | 0 | FALSE | TRUE
RO_RA_00122 | RO | RVLCE15 _generator | 0 | 55 |  |  | 3 | 0 |  | 55 | 0 | FALSE | TRUE
RO_RA_00123 | RO | RVALD_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00125 | RO | RAREF_5 _generator | 0 | 10 |  |  | 1 | 0 |  | 10 | 0 | FALSE | TRUE
RO_RA_00126 | RO | RARGS_5 _generator | 0 | 31 |  |  | 2 | 0 |  | 31 | 0 | FALSE | TRUE
RO_RA_00127 | RO | RALBE_5 _generator | 0 | 30 |  |  | 2 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00128 | RO | RCERB_5 _generator | 0 | 15 |  |  | 1 | 0 |  | 15 | 0 | FALSE | TRUE
RO_RA_00129 | RO | RVLCE25 _generator | 0 | 12 |  |  | 1 | 0 |  | 12 | 0 | FALSE | TRUE
RO_RA_00130 | RO | RCLNG_5 _generator | 0 | 90 |  |  | 64 | 0 |  | 90 | 0 | FALSE | TRUE
RO_RA_00134 | RO | RSTUP_5 _generator | 0 | 45 |  |  | 18 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00135 | RO | RDAIES5 _generator | 0 | 37 |  |  | 29 | 0 |  | 37 | 0 | FALSE | TRUE
RO_RA_00136 | RO | RVILN_5 _generator | 0 | 46 |  |  | 18 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00137 | RO | RRIUR15 _generator | 0 | 48 |  |  | 38 | 0 |  | 48 | 0 | FALSE | TRUE
RO_RA_00138 | RO | RMARC_5 _generator | 0 | 39 |  |  | 15 | 0 |  | 39 | 0 | FALSE | TRUE
RO_RA_00139 | RO | RIONE_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00140 | RO | RJIBL_5 _generator | 0 | 38 |  |  | 15 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00141 | RO | RZAVI_5 _generator | 0 | 38 |  |  | 30 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00142 | RO | RCHTU_5 _generator | 0 | 74 |  |  | 28 | 0 |  | 74 | 0 | FALSE | TRUE
RO_RA_00143 | RO | RTRAI_5 _generator | 0 | 45 |  |  | 31 | 0 |  | 45 | 0 | FALSE | TRUE
RO_RA_00144 | RO | RHGLOT5 _generator | 0 | 25 |  |  | 10 | 0 |  | 25 | 0 | FALSE | TRUE
RO_RA_00145 | RO | RCHESJ5 _generator | 0 | 50 |  |  | 26 | 0 |  | 50 | 0 | FALSE | TRUE
RO_RA_00146 | RO | RCHEAC5 _generator | 0 | 38 |  |  | 20 | 0 |  | 38 | 0 | FALSE | TRUE
RO_RA_00147 | RO | RCHEST5 _generator | 0 | 26 |  |  | 13 | 0 |  | 26 | 0 | FALSE | TRUE
RO_RA_00148 | RO | RCHEIO5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00149 | RO | RCHDO_5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00150 | RO | RFRUN_5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00151 | RO | RCIZBI5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00152 | RO | RRUSA_5 _generator | 0 | 53 |  |  | 27 | 0 |  | 53 | 0 | FALSE | TRUE
RO_RA_00153 | RO | RHCORN5 _generator | 0 | 59 |  |  | 16 | 0 |  | 59 | 0 | FALSE | TRUE
RO_RA_00154 | RO | RFAGA_5 _generator | 0 | 20 |  |  | 7 | 0 |  | 20 | 0 | FALSE | TRUE
RO_RA_00155 | RO | RUCEA25 _generator | 0 | 32 |  |  | 7 | 0 |  | 32 | 0 | FALSE | TRUE
RO_RA_00156 | RO | RUCEA15 _generator | 0 | 49 |  |  | 7 | 0 |  | 49 | 0 | FALSE | TRUE
RO_RA_00157 | RO | RCIRT_5 _generator | 0 | 54 |  |  | 24 | 0 |  | 54 | 0 | FALSE | TRUE
RO_RA_00160 | RO | RVADU_5 _generator | 0 | 67 |  |  | 17 | 0 |  | 67 | 0 | FALSE | TRUE
RO_RA_00161 | RO | RIZVO_5 _generator | 0 | 9 |  |  | 1 | 0 |  | 9 | 0 | FALSE | TRUE
RO_RA_00162 | RO | RDUMB_5 _generator | 0 | 23 |  |  | 2 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00163 | RO | RCOST_5 _generator | 0 | 24 |  |  | 2 | 0 |  | 24 | 0 | FALSE | TRUE
RO_RA_00164 | RO | RBUHU_5 _generator | 0 | 13 |  |  | 1 | 0 |  | 13 | 0 | FALSE | TRUE
RO_RA_00165 | RO | RRACO_5 _generator | 0 | 23 |  |  | 9 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00166 | RO | RGARL_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00167 | RO | RLILI_5 _generator | 0 | 23 |  |  | 4 | 0 |  | 23 | 0 | FALSE | TRUE
RO_RA_00168 | RO | RBACS_5 _generator | 0 | 98 |  |  | 31 | 0 |  | 98 | 0 | FALSE | TRUE
RO_RA_00169 | RO | RFARA_5 _generator | 0 | 30 |  |  | 9 | 0 |  | 30 | 0 | FALSE | TRUE
RO_RA_00170 | RO | RSISC_5 _generator | 0 | 44 |  |  | 12 | 0 |  | 44 | 0 | FALSE | TRUE
RO_RA_00171 | RO | RMARA_5 _generator | 0 | 46 |  |  | 11 | 0 |  | 46 | 0 | FALSE | TRUE
RO_RA_00172 | RO | RTECU_5 _generator | 0 | 34 |  |  | 10 | 0 |  | 34 | 0 | FALSE | TRUE
RO_RA_00173 | RO | RMARI22 _generator | 0 | 217 |  |  | 0 | 64 |  | 217 | 0 | TRUE | FALSE
RO_RA_00176 | RO | RSEBE_5 _generator | 0 | 55 |  |  | 27 | 0 |  | 55 | 0 | FALSE | TRUE
Non Costly Reduction
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status | Details
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PATL) | Margin (A) | Loading (%) | Flow [MW] | LF type
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1567 | 1570 | -3 | 100 | -1128 | AC
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1567 | 1570 | -3 | 100 | -1128 | AC
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1514 | 1570 | -56 | 96 | -1088 | AC
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1495 | 1570 | -75 | 95 | -1075 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1492 | 1570 | -78 | 95 | -1073 | AC
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1488 | 1570 | -82 | 95 | -1071 | AC
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1486 | 1570 | -84 | 95 | -1066 | AC
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1570 | -85 | 95 | -1064 | AC
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1485 | 1570 | -85 | 95 | -1064 | AC
Base case | Base case | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1460 | 1570 | -110 | 93 | -1051 | AC
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1452 | 1570 | -118 | 92 | -1045 | AC
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1443 | 1570 | -127 | 92 | -1039 | AC
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1382 | 1570 | -188 | 88 | -989 | AC
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [OPP] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 XPF_DJ11 1 | 1368 | 1570 | -202 | 87 | -971 | AC
RO_CO_00008 | N-1 OHL 400 kV Slatina-Portile de Fier | [RO-RO] [DIR] OHL 400 kV Portile de Fier-Urechesti | RPDF241 RUREC41 1 | 1636 | 1920 | -284 | 85 | 1189 | AC
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 808 | 999 | -192 | 81 | 307 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT2 Iernut | RIERN41 RIERN22 2 | 796 | 999 | -204 | 80 | 305 | AC
RO_CO_00009 | N-1 OHL 400 kV Iernut-Sibiu Sud | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 778 | 999 | -221 | 78 | 298 | AC
RO_CO_00031 | N-1 OHL 220 kV Resita-Timisoara c2 | [RO-RO] [DIR] OHL 220 kV Resita-Timisoara c1 | RRESI12 RTIMI12 1 | 734 | 960 | -226 | 76 | 300 | AC
Base case | Base case | [RO-RO] [DIR] TRA 400/220 kV AT Rosiori | RROS241 RROSI22 2 | 759 | 999 | -240 | 76 | 292 | AC
RO_CO_00007 | N-1 OHL 400 kV Portile de Fier-Urechesti | [RO-RO] [OPP] OHL 400 kV Slatina-Portile de Fier | RSLAT41 RPDFE41 1 | 1454 | 1920 | -466 | 76 | 1053 | AC