## 1230Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2985
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -906 | -999 | -999 | -93 | 91 | []
RO_CO_00006 | N-1 OHL 400 kV Domnesti - Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -888 | -999 | -999 | -111 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1106 | -1248 | -1248 | -142 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1105 | -1248 | -1248 | -143 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1099 | -1248 | -1248 | -149 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1095 | -1248 | -1248 | -154 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1089 | -1248 | -1248 | -160 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1085 | -1248 | -1248 | -164 | 87 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1356 | -1570 | -1570 | -214 | 86 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1356 | -1570 | -1570 | -214 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1329 | -1570 | -1570 | -241 | 85 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1290 | -1570 | -1570 | -280 | 82 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1290 | -1570 | -1570 | -280 | 82 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1290 | -1570 | -1570 | -280 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1288 | -1570 | -1570 | -282 | 82 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1287 | -1570 | -1570 | -283 | 82 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1283 | -1570 | -1570 | -287 | 82 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1277 | -1570 | -1570 | -293 | 81 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1269 | -1570 | -1570 | -301 | 81 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1206 | -1570 | -1570 | -364 | 77 | []

## 1230Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 12:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2985
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -906 |  | -999 | -93 | 91 | []
RO_CO_00006 | N-1 OHL 400 kV Domnesti - Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -888 |  | -999 | -111 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1106 |  | -1248 | -142 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1105 |  | -1248 | -143 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1099 |  | -1248 | -149 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1095 |  | -1248 | -154 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1089 |  | -1248 | -160 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1085 |  | -1248 | -164 | 87 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1356 |  | -1570 | -214 | 86 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1356 |  | -1570 | -214 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1329 |  | -1570 | -241 | 85 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1290 |  | -1570 | -280 | 82 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1290 |  | -1570 | -280 | 82 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1290 |  | -1570 | -280 | 82 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1288 |  | -1570 | -282 | 82 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1287 |  | -1570 | -283 | 82 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1283 |  | -1570 | -287 | 82 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1277 |  | -1570 | -293 | 81 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1269 |  | -1570 | -301 | 81 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1206 |  | -1570 | -364 | 77 | []

## 1330Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3067
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 | 1570 | 1570 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -902 | -999 | -999 | -97 | 90 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1112 | -1248 | -1248 | -136 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1111 | -1248 | -1248 | -137 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1105 | -1248 | -1248 | -143 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1100 | -1248 | -1248 | -148 | 88 | []
RO_CO_00006 | N-1 OHL 400 kV Domnesti - Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -879 | -999 | -999 | -120 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1378 | 1570 | 1570 | -192 | 88 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1378 | 1570 | 1570 | -192 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1095 | -1248 | -1248 | -154 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1090 | -1248 | -1248 | -158 | 87 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1346 | 1570 | 1570 | -224 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1311 | 1570 | 1570 | -259 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1307 | 1570 | 1570 | -263 | 83 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1307 | 1570 | 1570 | -263 | 83 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1305 | 1570 | 1570 | -265 | 83 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1302 | 1570 | 1570 | -268 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1300 | 1570 | 1570 | -270 | 83 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1292 | 1570 | 1570 | -278 | 82 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1287 | 1570 | 1570 | -283 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1223 | 1570 | 1570 | -347 | 78 | []

## 1330Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 13:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3067
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1567 |  | 1570 | -3 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -902 |  | -999 | -97 | 90 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1112 |  | -1248 | -136 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1111 |  | -1248 | -137 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1105 |  | -1248 | -143 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1100 |  | -1248 | -148 | 88 | []
RO_CO_00006 | N-1 OHL 400 kV Domnesti - Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -879 |  | -999 | -120 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1378 |  | 1570 | -192 | 88 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1378 |  | 1570 | -192 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1095 |  | -1248 | -154 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1090 |  | -1248 | -158 | 87 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1346 |  | 1570 | -224 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1311 |  | 1570 | -259 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1307 |  | 1570 | -263 | 83 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1307 |  | 1570 | -263 | 83 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1305 |  | 1570 | -265 | 83 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1302 |  | 1570 | -268 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1300 |  | 1570 | -270 | 83 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1292 |  | 1570 | -278 | 82 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1287 |  | 1570 | -283 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1223 |  | 1570 | -347 | 78 | []

## 1430Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3089
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1569 | 1570 | 1570 | -1 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -922 | -999 | -999 | -78 | 92 | []
RO_CO_00006 | N-1 OHL 400 kV Domnesti - Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -892 | -999 | -999 | -107 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1112 | -1248 | -1248 | -136 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1111 | -1248 | -1248 | -137 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1105 | -1248 | -1248 | -143 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1100 | -1248 | -1248 | -148 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1379 | -1570 | -1570 | -191 | 88 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1379 | -1570 | -1570 | -191 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1095 | -1248 | -1248 | -154 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1090 | -1248 | -1248 | -158 | 87 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1351 | -1570 | -1570 | -219 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1320 | -1570 | -1570 | -250 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1313 | -1570 | -1570 | -257 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1313 | -1570 | -1570 | -257 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1311 | -1570 | -1570 | -259 | 83 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1308 | -1570 | -1570 | -262 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1305 | -1570 | -1570 | -265 | 83 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1297 | -1570 | -1570 | -273 | 83 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1290 | -1570 | -1570 | -280 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1240 | -1570 | -1570 | -330 | 79 | []

## 1430Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 14:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3089
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1569 |  | 1570 | -1 | 100 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -922 |  | -999 | -78 | 92 | []
RO_CO_00006 | N-1 OHL 400 kV Domnesti - Urechesti | [RO-RO] [DIR] TRA 400/220 kV AT Urechesti | RURE241 _RURE212 _1:trf | -892 |  | -999 | -107 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1112 |  | -1248 | -136 | 89 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1111 |  | -1248 | -137 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1105 |  | -1248 | -143 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1100 |  | -1248 | -148 | 88 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1379 |  | -1570 | -191 | 88 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1379 |  | -1570 | -191 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1095 |  | -1248 | -154 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1090 |  | -1248 | -158 | 87 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1351 |  | -1570 | -219 | 86 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1320 |  | -1570 | -250 | 84 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1313 |  | -1570 | -257 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1313 |  | -1570 | -257 | 84 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1311 |  | -1570 | -259 | 83 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1308 |  | -1570 | -262 | 83 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1305 |  | -1570 | -265 | 83 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1297 |  | -1570 | -273 | 83 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1290 |  | -1570 | -280 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1240 |  | -1570 | -330 | 79 | []

## 1530Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2647
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1566 | -1570 | -1570 | -4 | 100 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1090 | -1248 | -1248 | -159 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1087 | -1248 | -1248 | -161 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1083 | -1248 | -1248 | -165 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1081 | -1248 | -1248 | -168 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1073 | -1248 | -1248 | -175 | 86 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1073 | -1248 | -1248 | -175 | 86 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1321 | -1570 | -1570 | -249 | 84 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1321 | -1570 | -1570 | -249 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1291 | -1570 | -1570 | -279 | 82 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1289 | -1570 | -1570 | -281 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1274 | -1570 | -1570 | -296 | 81 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1251 | -1570 | -1570 | -319 | 80 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1250 | -1570 | -1570 | -320 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1248 | -1570 | -1570 | -322 | 80 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1248 | -1570 | -1570 | -322 | 80 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1247 | -1570 | -1570 | -323 | 79 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1246 | -1570 | -1570 | -324 | 79 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1242 | -1570 | -1570 | -328 | 79 | []

## 1530Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 15:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2647
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1566 |  | -1570 | -4 | 100 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1090 |  | -1248 | -159 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1087 |  | -1248 | -161 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1083 |  | -1248 | -165 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1081 |  | -1248 | -168 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1073 |  | -1248 | -175 | 86 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1073 |  | -1248 | -175 | 86 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1321 |  | -1570 | -249 | 84 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1321 |  | -1570 | -249 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1291 |  | -1570 | -279 | 82 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1289 |  | -1570 | -281 | 82 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1274 |  | -1570 | -296 | 81 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1251 |  | -1570 | -319 | 80 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1250 |  | -1570 | -320 | 80 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1248 |  | -1570 | -322 | 80 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1248 |  | -1570 | -322 | 80 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1247 |  | -1570 | -323 | 79 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1246 |  | -1570 | -324 | 79 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1242 |  | -1570 | -328 | 79 | []

## 1630Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2604
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1095 | -1248 | -1248 | -153 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1093 | -1248 | -1248 | -155 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1089 | -1248 | -1248 | -160 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1086 | -1248 | -1248 | -162 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1079 | -1248 | -1248 | -169 | 86 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1079 | -1248 | -1248 | -170 | 86 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1347 | -1570 | -1570 | -223 | 86 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1347 | -1570 | -1570 | -223 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 | -1570 | -1570 | -242 | 85 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1322 | -1570 | -1570 | -248 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1322 | -1570 | -1570 | -248 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1272 | -1570 | -1570 | -298 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1272 | -1570 | -1570 | -298 | 81 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1271 | -1570 | -1570 | -299 | 81 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1269 | -1570 | -1570 | -301 | 81 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1269 | -1570 | -1570 | -301 | 81 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1266 | -1570 | -1570 | -304 | 81 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1252 | -1570 | -1570 | -318 | 80 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -900 | -1248 | -1248 | -349 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -899 | -1248 | -1248 | -349 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -892 | -1248 | -1248 | -357 | 71 | []

## 1630Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 16:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2604
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1095 |  | -1248 | -153 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1093 |  | -1248 | -155 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1089 |  | -1248 | -160 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1086 |  | -1248 | -162 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1079 |  | -1248 | -169 | 86 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1079 |  | -1248 | -170 | 86 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1347 |  | -1570 | -223 | 86 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1347 |  | -1570 | -223 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1328 |  | -1570 | -242 | 85 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1322 |  | -1570 | -248 | 84 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1322 |  | -1570 | -248 | 84 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1272 |  | -1570 | -298 | 81 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1272 |  | -1570 | -298 | 81 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1271 |  | -1570 | -299 | 81 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1269 |  | -1570 | -301 | 81 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1269 |  | -1570 | -301 | 81 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1266 |  | -1570 | -304 | 81 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | -1252 |  | -1570 | -318 | 80 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -900 |  | -1248 | -349 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -899 |  | -1248 | -349 | 72 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -892 |  | -1248 | -357 | 71 | []

## 1730Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3620
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1498 | 1570 | 1570 | -72 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1498 | 1570 | 1570 | -72 | 95 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 | 1570 | 1570 | -129 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 | 1570 | 1570 | -137 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1432 | 1570 | 1570 | -138 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1412 | 1570 | 1570 | -158 | 90 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1106 | -1248 | -1248 | -142 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1105 | -1248 | -1248 | -144 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1098 | -1248 | -1248 | -150 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1098 | -1248 | -1248 | -151 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1374 | 1570 | 1570 | -196 | 88 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1374 | 1570 | 1570 | -196 | 88 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1372 | 1570 | 1570 | -198 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1090 | -1248 | -1248 | -159 | 87 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1370 | 1570 | 1570 | -200 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1369 | 1570 | 1570 | -201 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1088 | -1248 | -1248 | -160 | 87 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 | 1570 | 1570 | -202 | 87 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1364 | 1570 | 1570 | -206 | 87 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1353 | 1570 | 1570 | -217 | 86 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | 1482 | 1890 | 1890 | -408 | 78 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | 1482 | 1890 | 1890 | -408 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1482 | 1920 | 1920 | -438 | 77 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1482 | 1920 | 1920 | -438 | 77 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -907 | -1248 | -1248 | -342 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -906 | -1248 | -1248 | -343 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -895 | -1248 | -1248 | -353 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [OPP] OHL 400 kV Tantareni-Urechesti | RTINTA1 _RURE241 _1:line | 1226 | 1740 | 1740 | -514 | 70 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1397 | 1995 | 1995 | -598 | 70 | []

## 1730Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 17:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3620
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | BG_RA_00001 | PRA 400 kV TINTARENI-KOZLODUI 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | notApplied
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | helpful
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1498 |  | 1570 | -72 | 95 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1498 |  | 1570 | -72 | 95 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1441 |  | 1570 | -129 | 92 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1433 |  | 1570 | -137 | 91 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1432 |  | 1570 | -138 | 91 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1412 |  | 1570 | -158 | 90 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1106 |  | -1248 | -142 | 89 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1105 |  | -1248 | -144 | 89 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1098 |  | -1248 | -150 | 88 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1098 |  | -1248 | -151 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1374 |  | 1570 | -196 | 88 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1374 |  | 1570 | -196 | 88 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1372 |  | 1570 | -198 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1090 |  | -1248 | -159 | 87 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1370 |  | 1570 | -200 | 87 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1369 |  | 1570 | -201 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1088 |  | -1248 | -160 | 87 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1368 |  | 1570 | -202 | 87 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1364 |  | 1570 | -206 | 87 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1353 |  | 1570 | -217 | 86 | []
BG_RO_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | XKO_TI11_VAECKO11_1:line | 1482 |  | 1890 | -408 | 78 | []
BG_RO_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [BG-RO] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | XKO_TI12_VAECKO11_1:line | 1482 |  | 1890 | -408 | 78 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 1 | RTINTB1 _XKO_TI11_1:line | -1482 |  | 1920 | -438 | 77 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-BG] [DIR] TIE 400 kV TINTARENI-KOZLODUI 2 | RTINTB1 _XKO_TI12_1:line | -1482 |  | 1920 | -438 | 77 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -907 |  | -1248 | -342 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -906 |  | -1248 | -343 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -895 |  | -1248 | -353 | 72 | []
RO-RS_CO_00001, RO_RS_CO_00001 | N-1 TIE 400 kV Portile de Fier-Djerdap, N-1 TIE 400 kV PORTILE DE FIER - DJERDAP | [RO-RO] [OPP] OHL 400 kV Tantareni-Urechesti | RTINTA1 _RURE241 _1:line | 1226 |  | 1740 | -514 | 70 | []
RO_CO_00013 | N-1 OHL 400 kV Lacu Sarat - Gura Ialomitei | [RO-RO] [OPP] OHL 400 kV Medgidia Sud- Cernavoda | RMED141 _RCERN41 _1:line | 1397 |  | 1995 | -598 | 70 | []

## 1830Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3456
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 | 1570 | 1570 | -91 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 | 1570 | 1570 | -91 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 | 1570 | 1570 | -117 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 | 1570 | 1570 | -118 | 92 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1446 | 1570 | 1570 | -124 | 92 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1421 | 1570 | 1570 | -149 | 90 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1386 | 1570 | 1570 | -184 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1381 | 1570 | 1570 | -189 | 88 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1379 | 1570 | 1570 | -191 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1095 | -1248 | -1248 | -153 | 88 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1377 | 1570 | 1570 | -193 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1093 | -1248 | -1248 | -155 | 88 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1374 | 1570 | 1570 | -196 | 87 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1373 | 1570 | 1570 | -197 | 87 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1373 | 1570 | 1570 | -197 | 87 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1371 | 1570 | 1570 | -199 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1087 | -1248 | -1248 | -161 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1087 | -1248 | -1248 | -162 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1079 | -1248 | -1248 | -170 | 86 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1078 | -1248 | -1248 | -171 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -908 | -1248 | -1248 | -340 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -907 | -1248 | -1248 | -341 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -898 | -1248 | -1248 | -350 | 72 | []

## 1830Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 18:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3456
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | notApplied
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 |  | 1570 | -91 | 94 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1479 |  | 1570 | -91 | 94 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1453 |  | 1570 | -117 | 93 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1452 |  | 1570 | -118 | 92 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1446 |  | 1570 | -124 | 92 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1421 |  | 1570 | -149 | 90 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1386 |  | 1570 | -184 | 88 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1381 |  | 1570 | -189 | 88 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1379 |  | 1570 | -191 | 88 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1095 |  | -1248 | -153 | 88 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1377 |  | 1570 | -193 | 88 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1093 |  | -1248 | -155 | 88 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1374 |  | 1570 | -196 | 87 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1373 |  | 1570 | -197 | 87 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1373 |  | 1570 | -197 | 87 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1371 |  | 1570 | -199 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1087 |  | -1248 | -161 | 87 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1087 |  | -1248 | -162 | 87 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1079 |  | -1248 | -170 | 86 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1078 |  | -1248 | -171 | 86 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -908 |  | -1248 | -340 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -907 |  | -1248 | -341 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -898 |  | -1248 | -350 | 72 | []

## 1930Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3251
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 | 1570 | 1570 | -4 | 100 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1554 | 1570 | 1570 | -16 | 99 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1554 | 1570 | 1570 | -16 | 99 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1552 | 1570 | 1570 | -18 | 99 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1545 | 1570 | 1570 | -25 | 98 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1535 | 1570 | 1570 | -35 | 98 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1502 | 1570 | 1570 | -68 | 96 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1494 | 1570 | 1570 | -76 | 95 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1486 | 1570 | 1570 | -84 | 95 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1483 | 1570 | 1570 | -87 | 94 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 | 1570 | 1570 | -98 | 94 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 | 1570 | 1570 | -102 | 94 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1466 | 1570 | 1570 | -104 | 93 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1080 | -1248 | -1248 | -168 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1078 | -1248 | -1248 | -170 | 86 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1073 | -1248 | -1248 | -175 | 86 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1071 | -1248 | -1248 | -177 | 86 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1064 | -1248 | -1248 | -184 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1064 | -1248 | -1248 | -185 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -908 | -1248 | -1248 | -340 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -908 | -1248 | -1248 | -341 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -900 | -1248 | -1248 | -349 | 72 | []

## 1930Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 19:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3251
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1566 |  | 1570 | -4 | 100 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1554 |  | 1570 | -16 | 99 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1554 |  | 1570 | -16 | 99 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1552 |  | 1570 | -18 | 99 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1545 |  | 1570 | -25 | 98 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1535 |  | 1570 | -35 | 98 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1502 |  | 1570 | -68 | 96 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1494 |  | 1570 | -76 | 95 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1486 |  | 1570 | -84 | 95 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1483 |  | 1570 | -87 | 94 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1472 |  | 1570 | -98 | 94 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 |  | 1570 | -102 | 94 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1466 |  | 1570 | -104 | 93 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1080 |  | -1248 | -168 | 87 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1078 |  | -1248 | -170 | 86 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1073 |  | -1248 | -175 | 86 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1071 |  | -1248 | -177 | 86 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1064 |  | -1248 | -184 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1064 |  | -1248 | -185 | 85 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -908 |  | -1248 | -340 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -908 |  | -1248 | -341 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -900 |  | -1248 | -349 | 72 | []

## 2030Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 2978
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 | 1570 | 1570 | -2 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1562 | 1570 | 1570 | -8 | 99 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1561 | 1570 | 1570 | -9 | 99 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1543 | 1570 | 1570 | -27 | 98 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1540 | 1570 | 1570 | -30 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1522 | 1570 | 1570 | -48 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1522 | 1570 | 1570 | -48 | 97 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1498 | 1570 | 1570 | -72 | 95 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1495 | 1570 | 1570 | -75 | 95 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1478 | 1570 | 1570 | -92 | 94 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1476 | 1570 | 1570 | -94 | 94 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 | 1570 | 1570 | -102 | 93 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1459 | 1570 | 1570 | -111 | 93 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1454 | 1570 | 1570 | -116 | 93 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1055 | -1248 | -1248 | -194 | 84 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1052 | -1248 | -1248 | -196 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1048 | -1248 | -1248 | -201 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1045 | -1248 | -1248 | -203 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1039 | -1248 | -1248 | -210 | 83 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1038 | -1248 | -1248 | -210 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -907 | -1248 | -1248 | -341 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -907 | -1248 | -1248 | -342 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -899 | -1248 | -1248 | -349 | 72 | []

## 2030Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 20:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 2978
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1568 |  | 1570 | -2 | 100 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1562 |  | 1570 | -8 | 99 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1561 |  | 1570 | -9 | 99 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1543 |  | 1570 | -27 | 98 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1540 |  | 1570 | -30 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1522 |  | 1570 | -48 | 97 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1522 |  | 1570 | -48 | 97 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1498 |  | 1570 | -72 | 95 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1495 |  | 1570 | -75 | 95 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1478 |  | 1570 | -92 | 94 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1476 |  | 1570 | -94 | 94 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1468 |  | 1570 | -102 | 93 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1459 |  | 1570 | -111 | 93 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1570 | -116 | 93 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1055 |  | -1248 | -194 | 84 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1052 |  | -1248 | -196 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1048 |  | -1248 | -201 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1045 |  | -1248 | -203 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1039 |  | -1248 | -210 | 83 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1038 |  | -1248 | -210 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -907 |  | -1248 | -341 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -907 |  | -1248 | -342 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -899 |  | -1248 | -349 | 72 | []

## 2130Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3138
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 | 1570 | 1570 | -5 | 100 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1564 | 1570 | 1570 | -6 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1553 | 1570 | 1570 | -17 | 99 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1547 | 1570 | 1570 | -23 | 99 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1544 | 1570 | 1570 | -26 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1542 | 1570 | 1570 | -28 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1542 | 1570 | 1570 | -28 | 98 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1500 | 1570 | 1570 | -70 | 96 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1494 | 1570 | 1570 | -76 | 95 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1480 | 1570 | 1570 | -90 | 94 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1478 | 1570 | 1570 | -92 | 94 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1470 | 1570 | 1570 | -100 | 94 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 | 1570 | 1570 | -109 | 93 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1457 | 1570 | 1570 | -113 | 93 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1058 | -1248 | -1248 | -190 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1055 | -1248 | -1248 | -193 | 85 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1051 | -1248 | -1248 | -197 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1049 | -1248 | -1248 | -200 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1042 | -1248 | -1248 | -206 | 83 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1042 | -1248 | -1248 | -207 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -915 | -1248 | -1248 | -334 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -914 | -1248 | -1248 | -334 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -907 | -1248 | -1248 | -342 | 73 | []

## 2130Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 21:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3138
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1565 |  | 1570 | -5 | 100 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1564 |  | 1570 | -6 | 100 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1553 |  | 1570 | -17 | 99 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1547 |  | 1570 | -23 | 99 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1544 |  | 1570 | -26 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1542 |  | 1570 | -28 | 98 | []
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1542 |  | 1570 | -28 | 98 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1500 |  | 1570 | -70 | 96 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1494 |  | 1570 | -76 | 95 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1480 |  | 1570 | -90 | 94 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1478 |  | 1570 | -92 | 94 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1470 |  | 1570 | -100 | 94 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1461 |  | 1570 | -109 | 93 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1457 |  | 1570 | -113 | 93 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1058 |  | -1248 | -190 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1055 |  | -1248 | -193 | 85 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1051 |  | -1248 | -197 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1049 |  | -1248 | -200 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1042 |  | -1248 | -206 | 83 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1042 |  | -1248 | -207 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -915 |  | -1248 | -334 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -914 |  | -1248 | -334 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -907 |  | -1248 | -342 | 73 | []

## 2230Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3430
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1532 | 1570 | 1570 | -38 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1532 | 1570 | 1570 | -38 | 98 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1529 | 1570 | 1570 | -41 | 97 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1528 | 1570 | 1570 | -42 | 97 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1527 | 1570 | 1570 | -43 | 97 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1496 | 1570 | 1570 | -74 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1482 | 1570 | 1570 | -88 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 | 1570 | 1570 | -101 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1455 | 1570 | 1570 | -115 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 | 1570 | 1570 | -119 | 92 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 | 1570 | 1570 | -119 | 92 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1443 | 1570 | 1570 | -127 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1438 | 1570 | 1570 | -132 | 92 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1438 | 1570 | 1570 | -132 | 92 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1056 | -1248 | -1248 | -193 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1053 | -1248 | -1248 | -195 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1049 | -1248 | -1248 | -200 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1047 | -1248 | -1248 | -202 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1040 | -1248 | -1248 | -209 | 83 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1039 | -1248 | -1248 | -209 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -916 | -1248 | -1248 | -332 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -915 | -1248 | -1248 | -333 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -908 | -1248 | -1248 | -341 | 73 | []

## 2230Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 22:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3430
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1532 |  | 1570 | -38 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1532 |  | 1570 | -38 | 98 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1529 |  | 1570 | -41 | 97 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1528 |  | 1570 | -42 | 97 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1527 |  | 1570 | -43 | 97 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1496 |  | 1570 | -74 | 95 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1482 |  | 1570 | -88 | 94 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1469 |  | 1570 | -101 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1455 |  | 1570 | -115 | 93 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 |  | 1570 | -119 | 92 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 |  | 1570 | -119 | 92 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1443 |  | 1570 | -127 | 92 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1438 |  | 1570 | -132 | 92 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1438 |  | 1570 | -132 | 92 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1056 |  | -1248 | -193 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1053 |  | -1248 | -195 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1049 |  | -1248 | -200 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1047 |  | -1248 | -202 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1040 |  | -1248 | -209 | 83 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1039 |  | -1248 | -209 | 83 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -916 |  | -1248 | -332 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -915 |  | -1248 | -333 | 73 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -908 |  | -1248 | -341 | 73 | []

## 2330Preventive
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | preventive
TTC [MW]: | 3471
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1543 | 1570 | 1570 | -27 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1543 | 1570 | 1570 | -27 | 98 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1543 | 1570 | 1570 | -27 | 98 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1540 | 1570 | 1570 | -30 | 98 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1539 | 1570 | 1570 | -31 | 98 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1503 | 1570 | 1570 | -67 | 96 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1495 | 1570 | 1570 | -75 | 95 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 | 1570 | 1570 | -83 | 95 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1473 | 1570 | 1570 | -97 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1471 | 1570 | 1570 | -99 | 94 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 | 1570 | 1570 | -103 | 93 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1457 | 1570 | 1570 | -113 | 93 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1454 | 1570 | 1570 | -116 | 93 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 | 1570 | 1570 | -119 | 92 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1060 | -1248 | -1248 | -189 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1057 | -1248 | -1248 | -191 | 85 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1053 | -1248 | -1248 | -196 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1050 | -1248 | -1248 | -198 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1044 | -1248 | -1248 | -205 | 84 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1043 | -1248 | -1248 | -205 | 84 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -921 | -1248 | -1248 | -328 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -920 | -1248 | -1248 | -328 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -913 | -1248 | -1248 | -336 | 73 | []

## 2330Curative
Detailed results
Generated at: | 2026-06-15 08:25
Business day: | 15.06.2026
Timestamp: | 23:30
Border & direction: | South-Romania Export
Horizon: | ID
Remedial actions: | true
Evaluation type: | curative
TTC [MW]: | 3471
Fallback applied | false
Loading threshold | 0.7
Applied RAs
CO ID | RA ID | Name of the RA | Usage | Type | Location | Status
[n/a] | RO_RA_00002 | PRA 400/220kV AT Urechesti | preventive | pst |  | helpful
[n/a] | RO_RA_00010 | PRA 400 kV Tantareni-Kozlodui 1 | preventive | topological |  | helpful
[n/a] | RO_RA_00013 | PRA 400 kV Tantareni-Kozlodui 2 | preventive | topological |  | notApplied
[n/a] | RO_RA_00014 | PRA 400 kV Resita-Pancevo c2 | preventive | topological |  | helpful
[n/a] | RO_RA_00017 | PRA 400 kV Resita-Pancevo c1 | preventive | topological |  | notApplied
Limiting CNECs
CO ID | Name of the CO | Name of the CNE | CNE UCTE branch | Calculated I (A) | I max (PRE) | I max (CUR) | Margin (A) | Loading (%) | Applicable curative RAs
RO-BG_CO_00002 | N-1 TIE 400 kV TINTARENI-KOZLODUI 2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1543 |  | 1570 | -27 | 98 | []
RO-BG_CO_00001 | N-1 TIE 400 kV TINTARENI-KOZLODUI 1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1543 |  | 1570 | -27 | 98 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1543 |  | 1570 | -27 | 98 | []
RO-RS_CO_00004 | N-1 TIE 400 kV Resita-Pancevo c1 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1540 |  | 1570 | -30 | 98 | []
RO-RS_CO_00003 | N-1 TIE 400 kV Resita-Pancevo c2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1539 |  | 1570 | -31 | 98 | []
RO_CO_00052 | N-1 OHL 400 kV Sofia Zapad -Nis | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1503 |  | 1570 | -67 | 96 | []
RO-MD_CO_00001 | N-1 TIE 400 kV Isaccea - Vulcanesti | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1495 |  | 1570 | -75 | 95 | []
RO_CO_00002 | N-1 OHL 400 kV Mintia-Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1487 |  | 1570 | -83 | 95 | []
RO-UA_CO_00001 | N-1 TIE 400 kV Rosiori-Mukacevo | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1473 |  | 1570 | -97 | 94 | []
RO-HU_CO_00002 | N-1 TIE 400 kV Nadab-Bekescsaba | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1471 |  | 1570 | -99 | 94 | []
RO-HU_CO_00001 | N-1 TIE 400 kV Arad-Sandorfalva | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1467 |  | 1570 | -103 | 93 | []
RO_CO_00029 | N-1 OHL 220 kV Resita-Timisoara 1&2 | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1457 |  | 1570 | -113 | 93 | []
RO_CO_00027 | N-1 TRA 400/220 kV AT3 Arad | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1454 |  | 1570 | -116 | 93 | []
BC | Base Case | [RO-RS] [DIR] TIE 400 kV Portile de Fier-Djerdap | RPDFE41 _XPF_DJ11_1:line | 1451 |  | 1570 | -119 | 92 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1060 |  | -1248 | -189 | 85 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -1057 |  | -1248 | -191 | 85 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1053 |  | -1248 | -196 | 84 | []
RO_CO_00028 | N-1 TRA 400/220 kV AT1 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1050 |  | -1248 | -198 | 84 | []
RO_CO_00034 | N-1 TRA 400/220 kV AT2 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -1044 |  | -1248 | -205 | 84 | []
RO_CO_00035 | N-1 TRA 400/220 kV AT3 Portile de Fier | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -1043 |  | -1248 | -205 | 84 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT3 Portile de Fier | RPDFE41 _RPDF212 _3:trf | -921 |  | -1248 | -328 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT1 Portile de Fier | RPDFE41 _RPDF222 _1:trf | -920 |  | -1248 | -328 | 74 | []
RO_CO_00001 | N-1 OHL 220 kV Portile de Fier-Resita 1&2 | [RO-RO] [OPP] TRA 400/220 kV AT2 Portile de Fier | RPDF241 _RPDF222 _2:trf | -913 |  | -1248 | -336 | 73 | []